## J. Sizemore
# | Category | Finding | Action Item | Responsible Person | Target Date | Confirm Reviewer | Completion Date | Comments
PSM
66 | Operating Procedures | Orifice plate on fuel gas run has not been pulled and inspected for several years | Assure Orifice plate for the fuel gas to the plant is inspected as per procedure and generated by MP2 or Maximo.. | Jerry Sizemore | 2001-03-31 | Rick Suderman
67 | Operating Procedures | No Measurement witness test reports on file. | Assure that meter tests are witnessed by responsible plant personnel and conditions of testing left on file at the location | Jerry Sizemore | 2001-03-31 | Rick Suderman
68 | Operating Procedures | No meter tube inspection reports on file. | Assure that meter tube inspection reports are on file, and completed as per procedure. | Jerry Sizemore | 2001-03-31 | Rick Suderman
69 | Operating Procedures | Liquid Samplers cleaning procedure on file. | Assure that procedures are in place to assure that auto. Samplers are completely cleaned as per procedure. | Jerry Sizemore | 2001-03-31 | Rick Suderman
121 | Operating Procedures | Meter tube is too short and orifice plate not removable. | Develop a plan with Enron Engineering to install the correct size and length junior meter tube at the fuel gas to the plant area. (Picture #12) | Jerry Sizemore | 2001-06-30 | Rick Suderman