## Sheet1
Rolls-Royce Energy Systems, Inc.
Project: Enron-Transwestern
Coberra 6562 DLE Expected Performance and Emissions
Site Conditions:
Pipeline Natural Gas
60% RH
2.5 inch H20 inlet loss
4 inch H20 exhaust loss
Base Load
| 59 F | [5 empty] | 95 F
Elevation | Power | GG mass flow | NOx | CO | NOx | CO | Power | GG mass flow | NOx | CO | NOx | CO
(ft. ASL) | (Hp) | (lb/s) | (vppm) | (vppm) | (Tons/ yr) | (Tons/ yr) | (Hp) | (lb/s) | (vppm) | (vppm) | (Tons/ yr) | (Tons/ yr)
5700 | 30271 | 161.1 | 25 | 5 | 100.7278 | 12.2597 | 25073 | 142.2 | 25 | 5 | 88.9105 | 10.8214
6000 | 29930 | 159.3 | 25 | 5 | 99.6023 | 12.1227 | 24811 | 140.6 | 25 | 5 | 87.9101 | 10.6997
6800 | 29034 | 154.5 | 25 | 5 | 96.6011 | 11.7575 | 24095 | 136.5 | 25 | 5 | 85.3466 | 10.3877
7400 | 28386 | 151 | 25 | 5 | 94.4128 | 11.4911 | 23525 | 133.2 | 25 | 5 | 83.2833 | 10.1365
Tons/ yr based upon 8760 hours per year and 1 ton = 2000 lb.
Mol. Wt.
NOx (NO2) | 46.01
CO | 28.01
Air | 28.964
All data is expected and not guaranteed.
2001-01-29