## Sheet1
PROJECT SUMMARY
Plant |  | AES Calgary
Capacity |  | 525 MW (nominal)
Delivery Point |  | Janet substation
Configuration |  | 2 1x1 gas-fired combined-cycle gas turbines
Structure |  | For initial discussion purposes, please propose a capacity payment ($/kW-month) under a tolling arrangement in which the toller delivers gas to and takes power from the plant with full dispatch rights, including ancillary services. As discussions proceed, AES Calgary may propose alternative structures, including financially-settled hedges (e.g., contract for differences), for the final definitive agreement.
Availability |  | Buyer can select 8 on-peak months for 98 percent availability,
so long as the 4 off-peak months occur in 2 two-month blocks,
e.g., April & May and October & November.
Off-peak average availability = 85 percent
Seller can preschedule Planned Outages anytime during off-peak months
Term |  | Term |  | Dates
|  | 15 Years |  | 1/04 - 12/18
|  | 10 Years |  | 1/04 - 12/13
|  | 5 Years |  | 1/04 - 12/08
Performance (per unit)
|  | Net Output |  | Net Heat Rate |  | Ramp Rate **
Baseload |  | (MW) |  | (kJ/kWh HHV) |  | (% per minute)
Winter: |  | 234.3277 |  | 7707.6155 |  | 5%
Summer: |  | 218.6138 |  | 7617.2036 |  | 5%
|  | Incremental |  | Incremental Heat |  | Ramp Rate **
Peaking |  | Output (MW) |  | Rate (kJ/kWh HHV) |  | (% per minute)
Winter: |  | 26.1851 |  | 9918.3595 |  | 15%
Summer: |  | 26.8641 |  | 10123.2467 |  | 15%
** Ramp rates are from min load up to full load or from full load down to min load. For base load capacity, min load is ~ 106 MW; for peaking capacity, min load = 0 MW.
| Definition: |  |  |  | Fuel |  | Net Energy
| Hours after |  | Length of |  | Consumed |  | Produced during
Starts | Last Shutdown |  | Startup (min) |  | (GJ) |  | Startup (MWh)
Cold | > 72 |  | 240 |  | 2850 |  | 216
Warm | 12 - 72 |  | 160 |  | 2200 |  | 209
Hot | < 12 |  | 80 |  | 1200 |  | 92
Variable O&M (C$/MWh) |  | 3.5
Max number of starts allowed |  | 250 | per 8,000 operating hours