## Sheet1
MW Degradation
2000-04-27 11:07 |  | Avg. Heat
| MW's | Rate (HHV)
GE Gross Output @ Sea Level | 48.5 | 9763.78
Avg. Altitude Adjustment | -0.75
Transformer Efficiency | -0.25
BOP & Auxiliary (Pumps, Fans, etc. ) | -0.75
Chillers (Adds 10 MW's) | -1.5
Gas Compression | -0.25
SCR's (Back Pressure) | -0.25
Total Plant Output | 44.75 | 10200