## Notes
NOTES
1 | The model shows only an example of the economics for a LM6000 project. Please modify the model for the specific transaction
you are trying to model (Please see the contact list below)
2 | Please double check the model/pages before sending out to clients as certain information/comment cells/notes etc. may be too detailed to be disclosed
3 | All yellow shaded cells are required input cells
4 | Turbine carrying cost are based on assumptions on the WestLB Structure, the numbers may change after 03/15/00
5 | The dispatch template is attached. Please check with Jim Simpson for the required inputs
SOURCES
Source
1 | Federal Tax, Franchise Tax, Sales & Used Tax, NOL |  |  | Patrick Maloy
calculations
2 | 15 year MACRS |  |  | Patrick Maloy
3 | Book Depreciation |  |  | Use GenCo assumption as per Jody Pierce
4 | Fin Fan Cooler |  |  | Bernstein's cost model, calculated by Bruce Golden
5 | No Capacity Degradation for LM 6000 Peaker model |  |  | Bruce Golden
6 | Spread Option Model |  |  | Jim Simpson
7 | Estimated drawdown schedule |  |  | Bruce Golden
8 | Property Tax, State Tax |  |  | Jim Curry
9 | Heat Rate Degradation |  |  | Bruce Golden
CONTACTS
| Subjects | Contacts | Extension
| Model | Clement Lau | x 3-9446
|  | Ben Rogers | x 3-7998
| Turbine/Technical Info | Doug Sewell | x 3-6337
| Engineers | Mike Coleman | x 6-6385
|  | Bruce Golden | x 6-6063
|  | Chris Booth | x 6-7089
| O&M | Scot Chambers | x 6-8371
| Spread Option Model | Jim Simpson | x 3-7202
| Accounting | Jody Pierce | x 5-7405
| Federal Tax, misc. Tax | Mike Fredell | x 3-7022
|  | Matt Gockerman | x 3-3979
|  | Patrick Maloy | x 3-6174
| State/Property Tax | Warren Schick | x 3-0689
|  | Jim Curry | x 3-6367

## Tracking Sheet
PROJECT NAME: UAE-Lowell
TRACKING SHEET
| EQUITY IRR WITH NO | DSCR
| RESIDUAL VALUE | MIN | AVG.
Current | 2.98e-07% | 1.3 | 1.3
Track Changes | 2.98e-07% | 1.3 | 1.3

## Assumptions
Unhide Sub Debt, 1999 Columns
PROJECT NAME: UAE-Lowell
UAE Cost Sceanrio
ASSUMPTIONS & SUMMARY OUTPUT
SOURCES & USES: |  |  |  | PROJECT DESCRIPTION: |  |  |  |  | OPERATING COSTS ASSUMPTIONS (FROM ENGINEERS/ASSET MANAGEMENT): |  |  |  | Fuel | Capacity $ | VOM | Residual Value | Capacity | Chillers | Compressor | Debt | New Debt | Versions
[9 empty] | (1st year Annualized) |  |  |  | Index | Base | Pass-through | EBITDA Exit Multiple | ISO | Yes | Yes | Bank LT Debt | 10-Yr. Debt | Optimal Debt
Sources of Funds | % | 000 $ | $/kW | Type of Turbine |  | LM6000 | [6 empty] | Fixed | Low | Not Pass-through | % of Project Cost | 95 degrees | No | No | Capital Market | 7-Yr. Debt | New Debt
Total Equity | -24.17% | -13291.6316 | -144.4743 | Cost Per Turbine (w Carry Cost) (000$) |  | 14260 |  |  | CPI Escalator (%) | 3% |  |  | Custom | Index |  | 000$/MW |  |  |  | Mini-perm | Lease
Debt Issuance | 124.2% | 68291.6316 | 742.3003 | Number of Turbines |  | 2 | [7 empty] | Custom |  | None
|  |  |  | Net Turbine Rating (MW) |  | 46 |  |  | Escalated Costs: |  |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1
Total Sources | 100% | 55000 | 597.8261 | Heat Rate-New and Clean (HHV) |  | 10100 |  |  |  | 000$ -year | $/kW-year | $/mWh | Index | Base | Pass-through | EBITDA Exit Multiple | 2 | 20 | Yes | Bank LT Debt | 10-Yr. Debt | 1
|  |  |  | Heat Rate-Degraded (HHV) |  | 10200 |  |  | Variable Operating Cost |  |  | 0.3
|  |  |  | No. of Construction Months |  | 7 |  |  | Major Maintenance |  |  | 1.2 |  | With Chillers | Without Chillers
Uses of Funds |  |  |  | Start of Commercial Operation |  | 2001-05-01 |  |  | Total VOM | 0 |  | 1.5 | ISO | 11 | 21
|  |  |  | No. of Months in the 1st Operating year |  | 8 | [5 empty] | ESC. | 95o | 12 | 22
EPC (From Engineers/Nepco): |  | ENA Turbines with UAE Costs |  | Project Life (Years) |  | 20 |  |  | Labor, Ann. Inspection, Fixed (Maint), Op. Fee | 200 | 2.1739
Turbine (with Carrying Cost) | 51.85% | 28520 | 310 | Location (State) |  | MA |  |  | Property & BI Insurance | 200 | 2.1739
Sprint Package Adder | 0% | 0 | 0 | [5 empty] | Water Supply Discharge | 0 | 0
BOP & Construction | 10.91% | 6000 | 65.2174 | Residual Value (at year 20) |  |  |  |  | Nox Budget/Audit Costs | 50 | 0.54348
Pipeline | 2.727% | 1500 | 16.3043 | EBITDA Exit Multiple |  | 5 |  |  | Water / Supply Discharge | 40 | 0.43478
Switchgear/MCC/Relays | 2.273% | 1250 | 13.587 | % of Initial Project Cost |  | 40% |  |  | Asset Mhmt. Cost | 40 | 0.43478
SCR, CO oxidation Catalyst, DLE Combuster Turbine | 11.18% | 6150 | 66.8478 | $/kW |  | 200 |  |  | Interconnect & Nepool Fees | 40 | 0.43478
Dual Fuel | 0% | 0 | 0 | [5 empty] | Total Fixed Escalating Cost | 570 | 6.1957
Black Start | 0% | 0 | 0 | FINANCING ASSUMPTIONS:
Gas Compression | 2.727% | 1500 | 16.3043 | DEBT |  | Construction Loan |  |  | Non-Escalated Costs:
Demineralized Water Facility | 0% | 0 | 0 | Debt Issued | 2000-10-01 |  | Debt Versions |  | Fuel | 7491.118 | 81.4252
Stacks, Noise Mitigation, Buildings | 2.727% | 1500 | 16.3043 | Treasury Rate as of: | 2000-02-15 |  |  |  | Property Tax | 300 | 3.2609 | 2%
Freight | 0.9091% | 500 | 5.4348 | [5 empty] | Franchise Tax | 0 | 0
Overhead & Fees - EE&CC | 0% | 0 | 0 | Amount ('000 $) | 68291.6316 |  | Debt Options | Lease with Prin. Pmt | Gross Receipts Tax | 0 | 0
Overhead & Fees - Nepco | 0% | 0 | 0 | Term (yrs) | 20 |  |  | No | Debt Service Reserve Fee | 0 | 0
LMP Cost Adder | 0% | 0 | 0 | Final Maturity | 2017-04-01
Chillers (Check that BOP did not already include this) | 0% | 0 | 0 | Average Life (yrs) | -83.9509 |  |  |  | DEPRECIATION ASSUMPTIONS:
Sub Total | 85.31% | 46920 | 510
|  |  |  | Treasury Rate (%) | 6.5% | 6.5% |  |  |  | Year | Method | Residual (%)
Soft Cost (From Engineers/Asset Management): |  |  |  | Spread (%) | 1.75% | 1.75% |  |  | Federal & State Tax Depreciation
Spare Parts Inventory | 0.6364% | 350 | 3.8043 | All-In Rate (%) | 8.25% | 8.25% |  |  | EPC Costs | 15 | MACRS | 0%
Owners Cost | 8.145% | 4480 | 48.6957 | [5 empty] | Start-Up Cost | 5 | SL | 0%
Others Costs | 1.364% | 750 | 8.1522 | Maximum DSR Amount (000 $) | 0 | 0 | (months/year) |  | Transaction Costs | 20 | SL | 0%
Environmental Permitting | 0% | 0 | 0 | Debt Service Reserve LOC Fee | 2%
Insurance | 0% | 0 | 0 | Interest Income Rate | 0% |  |  |  | Book Depreciation
Capitalized Salaries | 0% | 0 | 0 | [5 empty] | EPC Costs | 30 | SL | 10%
Owner's Engineer | 0% | 0 | 0 | EQUITY |  |  |  |  | Start-Up Cost | 5 | SL | 0%
Development Expenses | 0% | 0 | 0 | Equity Closed | 2000-06-01 |  |  |  | Transaction Costs | 20 | SL | 0%
Legal Expense | 0% | 0 | 0 | Equity Partner's Share | 0% | 0
Interconnect Study | 0% | 0 | 0 | Enron's Share | 100% | -13291.6316 |  |  | TAX ASSUMPTIONS (PROJECT MAY INCLUDE SPECIFIC TAXES):
IDC | 0% | 0 | 0
Land | 1.818% | 1000 | 10.8696 | PPA ASSUMPTIONS (MAKE CHANGES AS NEEDED): |  |  |  |  | Federal Income Tax Rate (%) | 35%
Sales & Used Tax | 2.727% | 1500 | 16.3043 | [5 empty] | State Income Tax Rate (average %) | 7% | (Project Specific)
Contingency | 0% | 0 | 0 | Fixed Price PPA |  |  |  |  | Franchise Tax (% on Net Asset) | 0% | (Project Specific)
Sub Total | 14.69% | 8080 | 87.8261 | No. of years |  | 20 |  |  | Gross Receipts Tax (%) | 0% | (Project Specific)
|  |  |  | Capacity Charge ($/kW-mo.) |  | 6 |  |  | Sales & Used Tax Rate on Fuel (%) | 1.5% | (Project Specific)
Financing Costs: | [8 empty] | Sales & Used Tax Rate on Hard Cost (%) | 5% | (Project Specific)
Lender's Engineer | 0% | 0 | 0 | Merchant Price Period
Lender's Counsel | 0% | 0 | 0 | No. of years |  | 0
Financing Fee (All-in Fees) | 0% | 0 | 0 | Capacity Charge ($/kW-mo.)
Sub Total | 0% | 0 | 0
|  |  |  | Variable Payment ($/mWh) |  | 1.5
Total Uses | 100% | 55000 | 597.8261
|  |  |  | Net Generation (MWh) |  | 225400
SUMMARY OUTPUT:
TECHNICAL ASSUMPTIONS:
All-in Capital Cost ($/kW) |  | 597.8261
|  |  |  | Site Condition (MW) |  | 92
|  | Avg. | Min | Evaporative Cooler (MW) |  | 0
DSCR |  | 1.3 | 1.3 | Net Output (MW) |  | 92
Enron Equity Returns |  |  |  | No. of Starts per year |  | 140
20 Yrs After-Tax Cashflow with Zero Residual Value |  | 2.98e-07% |  | Available PSIG |  | 400
20 Yrs After-Tax Cashflow with 5x EBITDA Exit Multiple Residual Value |  | #NUM! | Target | No. of Run Hours per year |  | 2450
20 Yrs After-Tax Cashflow with 40% Initial Project Cost Residual Value |  | #NUM! | 12%
20 Yrs After-Tax Cashflow with $200/kW Residual Value |  | #NUM!
Key Stats | 2001 | 2002 | 2003
EBITDA (000 $) | 3719.3333 | 5730.9 | 5708.403
Net Income (000 $) | -1180.8629 | -1722.7841 | -1805.0332
Pre-Tax Cashflow (000 $) | 1359.2755 | 24.4948 | -110.6119
Cashflow to Equity (000 $) | 1925.3296 | 1354.5702 | 1313.0093
Note on H11: clau: Calculated to include Carry Cost on a separate spreadsheet.
Note on H13: clau: This is an estimate, please check with Engineers for specific project
Note on H14: clau: This is an estimate, please check with Engineers for specific project
Note on H15: clau: This is an estimate, please check with Engineers for specific project
Note on C21: clau: $62,000/turbine as per Bruce Golden
Note on L38: clau: Assumption checked with Patrick Maloy on 2/4/00.
Note on C41: Ben Rogers: Make sure that ENA is not operating the facility, thus there will be no mobilization costs
Note on L43: clau: Assumption used for GenCo. Verified with Jody Pierce 2/3/00.
Note on N55: Ben Rogers: Need to check with Patrick Maloy the states tax rate
Note on C58: Ben Rogers: Based on company's estimate
Note on H61: clau: As per Bruce Golden for simple cycle LM6000
Note on H72: Ben Rogers: Based on company's estimates

## IS
PROJECT NAME: UAE-Lowell
INCOME STATEMENT
|  | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) |  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
|  | 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
Revenue
Capacity Revenue |  | 4416 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 6624 | 2485.5037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Revenue |  | 7835.9466 | 7802.1977 | 7888.372 | 8015.2279 | 8165.982 | 8325.9137 | 8491.1048 | 8668.4402 | 8857.9307 | 9059.5875 | 9273.4218 | 9471.4574 | 9649.7782 | 9988.1105 | 10250.7769 | 10525.6837 | 10812.8443 | 11112.273 | 11423.9842 | 11747.9929 | 12084.3144 | 5826.6669 | 5845.9114 | 5865.7332 | 5886.1497 | 5907.1787 | 5928.8385 | 5951.1481 | 5974.1271 | 5997.7954 | 6022.1737
Ancillary Services |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Revenue |  | 12251.9466 | 14426.1977 | 14512.372 | 14639.2279 | 14789.982 | 14949.9137 | 15115.1048 | 15292.4402 | 15481.9307 | 15683.5875 | 15897.4218 | 16095.4574 | 16273.7782 | 16612.1105 | 16874.7769 | 17149.6837 | 17436.8443 | 17736.273 | 18047.9842 | 18371.9929 | 14569.8181 | 5826.6669 | 5845.9114 | 5865.7332 | 5886.1497 | 5907.1787 | 5928.8385 | 5951.1481 | 5974.1271 | 5997.7954 | 6022.1737
Expense
Fuel |  | 7491.118 | 7447.0242 | 7522.5433 | 7638.4243 | 7777.8743 | 7926.1628 | 8079.3614 | 8244.3445 | 8421.1121 | 8609.6643 | 8810.001 | 8994.1339 | 9158.135 | 9481.718 | 9729.1927 | 9988.4519 | 10259.4956 | 10542.3238 | 10836.9366 | 11143.3338 | 11461.5156 | 5185.1841 | 5185.1841 | 5185.1841 | 5185.1841 | 5185.1841 | 5185.1841 | 5185.1841 | 5185.1841 | 5185.1841 | 5185.1841
Fixed Operating Expenses |  | 133.3333 | 206 | 212.18 | 218.5454 | 225.1018 | 231.8548 | 238.8105 | 245.9748 | 253.354 | 260.9546 | 268.7833 | 276.8468 | 285.1522 | 293.7067 | 302.5179 | 311.5935 | 320.9413 | 330.5695 | 340.4866 | 350.7012 | 361.2222 | 372.0589 | 383.2207 | 394.7173 | 406.5588 | 418.7556 | 431.3183 | 444.2578 | 457.5855 | 471.3131 | 485.4525
Variable Operating Expenses |  | 68.9657 | 71.0347 | 73.1657 | 75.3607 | 77.6215 | 79.9502 | 82.3487 | 84.8191 | 87.3637 | 89.9846 | 92.6842 | 95.4647 | 98.3286 | 101.2785 | 104.3168 | 107.4464 | 110.6697 | 113.9898 | 117.4095 | 120.9318 | 124.5598 | 128.2966 | 132.1455 | 136.1098 | 140.1931 | 144.3989 | 148.7309 | 153.1928 | 157.7886 | 162.5223 | 167.3979
Major Maintenance |  | 275.8629 | 284.1388 | 292.663 | 301.4428 | 310.4861 | 319.8007 | 329.3947 | 339.2766 | 349.4549 | 359.9385 | 370.7367 | 381.8588 | 393.3145 | 405.114 | 417.2674 | 429.7854 | 442.679 | 455.9594 | 469.6381 | 483.7273 | 498.2391 | 513.1863 | 528.5819 | 544.4393 | 560.7725 | 577.5957 | 594.9235 | 612.7712 | 631.1544 | 650.089 | 669.5917
Insurance |  | 133.3333 | 206 | 212.18 | 218.5454 | 225.1018 | 231.8548 | 238.8105 | 245.9748 | 253.354 | 260.9546 | 268.7833 | 276.8468 | 285.1522 | 293.7067 | 302.5179 | 311.5935 | 320.9413 | 330.5695 | 340.4866 | 350.7012 | 361.2222 | 372.0589 | 383.2207 | 394.7173 | 406.5588 | 418.7556 | 431.3183 | 444.2578 | 457.5855 | 471.3131 | 485.4525
SG&A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start Charge |  | 50 | 51.5 | 53.045 | 54.6364 | 56.2754 | 57.9637 | 59.7026 | 61.4937 | 63.3385 | 65.2387 | 67.1958 | 69.2117 | 71.288 | 73.4267 | 75.6295 | 77.8984 | 80.2353 | 82.6424 | 85.1217 | 87.6753 | 90.3056 | 93.0147 | 95.8052 | 98.6793 | 101.6397 | 104.6889 | 107.8296 | 111.0645 | 114.3964 | 117.8283 | 121.3631
Property Tax |  | 300 | 306 | 312.12 | 318.3624 | 324.7296 | 331.2242 | 337.8487 | 344.6057 | 351.4978 | 358.5278 | 365.6983 | 373.0123 | 380.4725 | 388.082 | 395.8436 | 403.7605 | 411.8357 | 420.0724 | 428.4739 | 437.0434 | 445.7842 | 454.6999 | 463.7939 | 473.0698 | 482.5312 | 492.1818 | 502.0254 | 512.0659 | 522.3073 | 532.7534 | 543.4085
Franchise Tax |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gross Receipts Tax |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Debt Service Reserve LOC Fee |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Marketing Fee |  | 26.6667 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2 | 41.2
Administrative Fee |  | 26.6667 | 41.2 | 42.436 | 43.7091 | 45.0204 | 46.371 | 47.7621 | 49.195 | 50.6708 | 52.1909 | 53.7567 | 55.3694 | 57.0304 | 58.7413 | 60.5036 | 62.3187 | 64.1883 | 66.1139 | 68.0973 | 70.1402 | 72.2444 | 74.4118 | 76.6441 | 78.9435 | 81.3118 | 83.7511 | 86.2637 | 88.8516 | 91.5171 | 94.2626 | 97.0905
O&M Fees |  | 26.6667 | 41.2 | 42.436 | 43.7091 | 45.0204 | 46.371 | 47.7621 | 49.195 | 50.6708 | 52.1909 | 53.7567 | 55.3694 | 57.0304 | 58.7413 | 60.5036 | 62.3187 | 64.1883 | 66.1139 | 68.0973 | 70.1402 | 72.2444 | 74.4118 | 76.6441 | 78.9435 | 81.3118 | 83.7511 | 86.2637 | 88.8516 | 91.5171 | 94.2626 | 97.0905
Total Expense |  | 8532.6133 | 8695.2977 | 8803.969 | 8953.9356 | 9128.4313 | 9312.7532 | 9503.0012 | 9706.0791 | 9922.0167 | 10150.845 | 10392.5958 | 10619.3136 | 10827.104 | 11195.7153 | 11489.4931 | 11796.3669 | 12116.3745 | 12449.5547 | 12795.9476 | 13155.5945 | 13528.5376 | 7308.523 | 7366.4401 | 7426.0039 | 7487.2618 | 7550.2628 | 7615.0573 | 7681.6973 | 7750.236 | 7820.7285 | 7893.2313
Total Expense w/o Energy Exp. |  | 839.1962 | 971.2388 | 996.08 | 1021.6052 | 1047.8337 | 1074.7854 | 1102.4807 | 1130.9407 | 1160.1868 | 1190.2414 | 1221.1274 | 1252.8682 | 1285.4882 | 1319.0121 | 1353.4656 | 1388.8752 | 1425.2678 | 1462.6715 | 1501.1149 | 1540.6276 | 1581.24 | 1622.9834 | 1665.8899 | 1709.9926 | 1755.3257 | 1801.9242 | 1849.8241 | 1899.0626 | 1949.6778 | 2001.709 | 2055.1968
EBITDA |  | 3719.3333 | 5730.9 | 5708.403 | 5685.2923 | 5661.5507 | 5637.1605 | 5612.1036 | 5586.3612 | 5559.914 | 5532.7424 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805 | -1481.856 | -1520.5287 | -1560.2706 | -1601.1121 | -1643.0841 | -1686.2188 | -1730.5491 | -1776.1089 | -1822.9331 | -1871.0576
Depreciation & Amortization |  | 1897.4 | 2846.1 | 2846.1 | 2846.1 | 2846.1 | 1902.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 476.7
EBIT |  | 1821.9333 | 2884.8 | 2862.303 | 2839.1923 | 2815.4507 | 3735.0605 | 4182.0036 | 4156.2612 | 4129.814 | 4102.6424 | 4074.726 | 4046.0438 | 4016.5742 | 3986.2951 | 3955.1838 | 3923.2168 | 3890.3699 | 3856.6183 | 3821.9366 | 3786.2984 | -388.8195 | -2911.956 | -2950.6287 | -2990.3706 | -3031.2121 | -3073.1841 | -3116.3188 | -3160.6491 | -3206.2089 | -3253.0331 | -2347.7576
Interest Expense |  | 3775.3873 | 5734.7323 | 5848.2966 | 5971.6631 | 6106.298 | 6254.1887 | 6416.0839 | 6593.5235 | 6786.9985 | 6998.8214 | 7230.2252 | 7483.1929 | 7758.8027 | 8059.8217 | 8388.1507 | 8746.3877 | 9136.4181 | 9561.6429 | 10024.8844 | 10529.5927 | 11178.3598 | 12078.779 | 13172.164 | 14380.1035 | 15693.206 | 17118.726 | 18667.2683 | 20348.6154 | 22175.57 | 24158.2335 | 26205.0512
Pretax Book Income |  | -1953.4539 | -2849.9323 | -2985.9936 | -3132.4708 | -3290.8474 | -2519.1282 | -2234.0804 | -2437.2624 | -2657.1844 | -2896.179 | -3155.4992 | -3437.1492 | -3742.2285 | -4073.5266 | -4432.9669 | -4823.1709 | -5246.0483 | -5705.0246 | -6202.9478 | -6743.2943 | -11567.1793 | -14990.735 | -16122.7927 | -17370.4742 | -18724.418 | -20191.9101 | -21783.5871 | -23509.2645 | -25381.7789 | -27411.2667 | -28552.8088
Book State Tax Benefit / (Expense) | 7% | 136.7418 | 199.4953 | 209.0196 | 219.273 | 230.3593 | 176.339 | 156.3856 | 170.6084 | 186.0029 | 202.7325 | 220.8849 | 240.6004 | 261.956 | 285.1469 | 310.3077 | 337.622 | 367.2234 | 399.3517 | 434.2063 | 472.0306 | 809.7025 | 1049.3514 | 1128.5955 | 1215.9332 | 1310.7093 | 1413.4337 | 1524.8511 | 1645.6485 | 1776.7245 | 1918.7887 | 1998.6966
Shareholder Fed. Tax Benefit / (Expense) | 35% | 635.8493 | 927.653 | 971.9409 | 1019.6192 | 1071.1708 | 819.9762 | 727.1932 | 793.3289 | 864.9135 | 942.7062 | 1027.115 | 1118.792 | 1218.0954 | 1325.9329 | 1442.9307 | 1569.9421 | 1707.5887 | 1856.9855 | 2019.0595 | 2194.9423 | 3765.1169 | 4879.4842 | 5247.969 | 5654.0893 | 6094.7981 | 6572.4667 | 7090.5576 | 7652.2656 | 8261.769 | 8922.3673 | 9293.9393
Net Income |  | -1180.8629 | -1722.7841 | -1805.0332 | -1893.5786 | -1989.3172 | -1522.813 | -1350.5016 | -1473.3251 | -1606.268 | -1750.7402 | -1907.4992 | -2077.7567 | -2262.1771 | -2462.4468 | -2679.7285 | -2915.6068 | -3171.2362 | -3448.6873 | -3749.682 | -4076.3214 | -6992.3599 | -9061.8993 | -9746.2282 | -10500.4516 | -11318.9107 | -12206.0097 | -13168.1784 | -14211.3504 | -15343.2854 | -16570.1107 | -17260.1729

## Capital Budget
UAE Lowell Power Expansion |  | PRELIMINARY DATA; ENGINEERING STUDY UNDERWAY TO CONFIRM ASSUMPTIONS
Capital Cost Breakdown ($ = 000's)
| 5x GE LM 6000 Base Package - Simple Cycle | DLE Combustor | 0 | (1=yes, 0=no)
Feb 23 Meeting with Enron Capital and Trade
|  | Lowell Expansion |  |  |  | GT Pro
Gas Turbine Package |  | Equipment | Installation | Total | Per Unit
| Gas Turbine Generator | 69000 | 1000 | 70000 | 14000 | 70000 | 0
| Sprint Package Adder (unavail w/DLE) | 1500 | 0 | 1500 | 300 |  | 1500
| Inlet Air Chiller | 3800 | 250 | 4050 | 810 | 4278 | -228
| Switchgear/MCC/Relays/Breaker Set | 1000 | 250 | 1250 | 250 | 770 | 480
| Stack(s)/Noise Attenuation/Buildings | 1250 | 250 | 1500 | 300 |  | 1500
| Water Tube Oil Cooler | 0 | 0 | 0 | 0 |  | 0
| Freight | 500 | 0 | 500 | 100 |  | 500
| Spare Parts Inventory | 350 | 0 | 350 | 70 | 250 | 100
Total Base Package |  | 77400 | 1750 | 79150 | 15830 | 75298 | 3852
Emissions Controls
| Vanadium-Titanium SCR (to 2 ppm NOX) | 4600 | 250 | 4850 | 970
| CO Oxidation Catalyst (to 10ppm CO) | 1000 | 100 | 1100 | 220
| Dry Low Emissions (DLE) Combustor Adder | 0 | 200 | 200 | 40
|  | 5600 | 550 | 6150 | 1230
Balance Of Plant
| Pads and Grading | 1200 | 400 | 1600 | 320
| Fuel Gas Compressors | 1000 | 250 | 1250 | 250
| Control Room (upgrade to existing unit) | 250 | 100 | 350 | 70
| Controls For Remote Operation | 50 | 50 | 100 | 20
| Demin Water Treatment (for Sprint/Water Inj) | 500 | 100 | 600 | 120
| Fire Protection | 300 | 100 | 400 | 80
| Cooling Tower for Chiller | 1200 | 350 | 1550 | 310
| Ammonia System (Tanks, Unldg./Fwdg. Pumps) | 250 | 50 | 300 | 60
| Step-Up Transformer(s) | 1500 | 300 | 1800 | 360
| Piping | 300 | 120 | 420 | 84
| Wiring | 700 | 450 | 1150 | 230
| Continuous Emissions Monitoring | 550 | 150 | 700 | 140
| Other | 0 | 0 | 0 | 0
Total Emissions and BOP |  | 13400 | 2970 | 16370 | 3274
Total EPC |  |  |  | 95520 | 19104
Owner's Cost
| Air Permitting | 500 |  |  | 100
| Air Permit Fees | 25 |  |  | 5
| Boston Gas Upgrades | 2000 |  |  | 400
| Utility Connection Cost (NEP) | 750 |  |  | 150
| Interconnect Study (NEP) | 250 |  |  | 50
| Property Purchase | 1000 |  |  | 200
| Water/Sewer Connect | 200 |  |  | 40
| Phase I/Phase II Environmental Review | 35 |  |  | 7
| Engineering Plant Specification | 50 |  |  | 10
| Engineering (Studies/Services/Conceptual) | 75 |  |  | 15
| Development/Construction Management | 600 |  |  | 120
| Interest During Construction | 3220 |  |  | 644
| Misc. Permits/Fees |  |  |  | 0
| Legal Fees | 500 |  |  | 100
| Bank Fees | 500 |  |  | 100
| Emissions Offsets | 350 |  |  | 70
| Working Capital | 2500 |  |  | 500
| Miscellaneous Consultants | 100 |  |  | 20
| Owner's Contingency (3% of EPC) | 2865.6 |  |  | 573.12
Total Owner's |  | 15520.6 |  |  | 3104.12
Commissioning
| Site Infrastructure (roads, landscape, neighbors) | 250 |  |  | 50
| Start Up | 500 |  |  | 100
Total Commissioning |  | 750 |  |  | 150
Total
| Base Package | 79150 |  |  | 15830
| BOP | 16370 |  |  | 3274
| Sales Tax (5.0%) | 4540 |  |  | 908
| Owner's Cost | 15520.6 |  |  | 3104.12
| Other Costs | 750 |  |  | 150
Total Capital Cost |  | 116330.6 |  |  | 23266.12
ISO Output (MW) |  | 227.5 |  |  | 45.5
$/kW |  | 511.3433 |  |  | 511.3433
| DLE Estimated Output at 90 deg F | 221.6
| Sprint/Water Inj Estimated Output at 90 deg F | 227.5

## Gas Curve
Total Price to
| Tenn Zone 6 | Annual | Year | Price
2001-01-01 | 4.0555 |  | 2001 | 3.1784
2001-02-01 | 3.8955 |  | 2002 | 3.1597
2001-03-01 | 3.343 |  | 2003 | 3.1917 | 1.0101
2001-04-01 | 2.863 |  | 2004 | 3.2409 | 1.0154
2001-05-01 | 2.781 |  | 2005 | 3.3 | 1.0183
2001-06-01 | 2.793 |  | 2006 | 3.363 | 1.0191
2001-07-01 | 2.816 |  | 2007 | 3.428 | 1.0193
2001-08-01 | 2.8155 |  | 2008 | 3.498 | 1.0204
2001-09-01 | 2.796 |  | 2009 | 3.573 | 1.0214
2001-10-01 | 2.8405 |  | 2010 | 3.653 | 1.0224
2001-11-01 | 3.2795 |  | 2011 | 3.738 | 1.0233
2001-12-01 | 3.862 | 3.1784 | 2012 | 3.8161 | 1.0209
2002-01-01 | 4.0725 |  | 2013 | 3.8857 | 1.0182
2002-02-01 | 3.925 |  | 2014 | 4.023 | 1.0353
2002-03-01 | 3.3155 |  | 2015 | 4.128 | 1.0261
2002-04-01 | 2.829 |  | 2016 | 4.238 | 1.0266
2002-05-01 | 2.77 |  | 2017 | 4.353 | 1.0271
2002-06-01 | 2.782 |  | 2018 | 4.473 | 1.0276
2002-07-01 | 2.799 |  | 2019 | 4.598 | 1.0279
2002-08-01 | 2.8025 |  | 2020 | 4.728 | 1.0283
2002-09-01 | 2.782 |  | 2021 | 4.863 | 1.0286
2002-10-01 | 2.8255
2002-11-01 | 3.2965
2002-12-01 | 3.7165 | 3.1597
2003-01-01 | 4.0725
2003-02-01 | 3.937
2003-03-01 | 3.358
2003-04-01 | 2.864
2003-05-01 | 2.805
2003-06-01 | 2.817
2003-07-01 | 2.834
2003-08-01 | 2.8375
2003-09-01 | 2.817
2003-10-01 | 2.8605
2003-11-01 | 3.3365
2003-12-01 | 3.7615 | 3.1917
2004-01-01 | 4.1325
2004-02-01 | 3.997
2004-03-01 | 3.408
2004-04-01 | 2.909
2004-05-01 | 2.85
2004-06-01 | 2.862
2004-07-01 | 2.879
2004-08-01 | 2.8825
2004-09-01 | 2.862
2004-10-01 | 2.9055
2004-11-01 | 3.3865
2004-12-01 | 3.8165 | 3.2409
2005-01-01 | 4.2025
2005-02-01 | 4.067
2005-03-01 | 3.468
2005-04-01 | 2.964
2005-05-01 | 2.905
2005-06-01 | 2.917
2005-07-01 | 2.934
2005-08-01 | 2.9375
2005-09-01 | 2.917
2005-10-01 | 2.9605
2005-11-01 | 3.4465
2005-12-01 | 3.8815 | 3.3
2006-01-01 | 4.2775
2006-02-01 | 4.142
2006-03-01 | 3.533
2006-04-01 | 3.024
2006-05-01 | 2.965
2006-06-01 | 2.977
2006-07-01 | 2.994
2006-08-01 | 2.9975
2006-09-01 | 2.977
2006-10-01 | 3.0205
2006-11-01 | 3.5065
2006-12-01 | 3.9415 | 3.363
2007-01-01 | 4.3425
2007-02-01 | 4.207
2007-03-01 | 3.598
2007-04-01 | 3.089
2007-05-01 | 3.03
2007-06-01 | 3.042
2007-07-01 | 3.059
2007-08-01 | 3.0625
2007-09-01 | 3.042
2007-10-01 | 3.0855
2007-11-01 | 3.5715
2007-12-01 | 4.0065 | 3.428
2008-01-01 | 4.4125
2008-02-01 | 4.277
2008-03-01 | 3.668
2008-04-01 | 3.159
2008-05-01 | 3.1
2008-06-01 | 3.112
2008-07-01 | 3.129
2008-08-01 | 3.1325
2008-09-01 | 3.112
2008-10-01 | 3.1555
2008-11-01 | 3.6415
2008-12-01 | 4.0765 | 3.498
2009-01-01 | 4.4875
2009-02-01 | 4.352
2009-03-01 | 3.743
2009-04-01 | 3.234
2009-05-01 | 3.175
2009-06-01 | 3.187
2009-07-01 | 3.204
2009-08-01 | 3.2075
2009-09-01 | 3.187
2009-10-01 | 3.2305
2009-11-01 | 3.7165
2009-12-01 | 4.1515 | 3.573
2010-01-01 | 4.5675
2010-02-01 | 4.432
2010-03-01 | 3.823
2010-04-01 | 3.314
2010-05-01 | 3.255
2010-06-01 | 3.267
2010-07-01 | 3.284
2010-08-01 | 3.2875
2010-09-01 | 3.267
2010-10-01 | 3.3105
2010-11-01 | 3.7965
2010-12-01 | 4.2315 | 3.653
2011-01-01 | 4.6525
2011-02-01 | 4.517
2011-03-01 | 3.908
2011-04-01 | 3.399
2011-05-01 | 3.34
2011-06-01 | 3.352
2011-07-01 | 3.369
2011-08-01 | 3.3725
2011-09-01 | 3.352
2011-10-01 | 3.3955
2011-11-01 | 3.8815
2011-12-01 | 4.3165 | 3.738
2012-01-01 | 4.7425
2012-02-01 | 4.607
2012-03-01 | 3.998
2012-04-01 | 3.489
2012-05-01 | 3.43
2012-06-01 | 3.442
2012-07-01 | 3.459
2012-08-01 | 3.4625
2012-09-01 | 3.442
2012-10-01 | 3.4855
2012-11-01 | 3.9715
2012-12-01 | 4.264 | 3.8161
2013-01-01 | 4.39
2013-02-01 | 4.702
2013-03-01 | 4.093
2013-04-01 | 3.584
2013-05-01 | 3.525
2013-06-01 | 3.537
2013-07-01 | 3.554
2013-08-01 | 3.5575
2013-09-01 | 3.537
2013-10-01 | 3.5805
2013-11-01 | 4.0665
2013-12-01 | 4.5015 | 3.8857
2014-01-01 | 4.9375
2014-02-01 | 4.802
2014-03-01 | 4.193
2014-04-01 | 3.684
2014-05-01 | 3.625
2014-06-01 | 3.637
2014-07-01 | 3.654
2014-08-01 | 3.6575
2014-09-01 | 3.637
2014-10-01 | 3.6805
2014-11-01 | 4.1665
2014-12-01 | 4.6015 | 4.023
2015-01-01 | 5.0425
2015-02-01 | 4.907
2015-03-01 | 4.298
2015-04-01 | 3.789
2015-05-01 | 3.73
2015-06-01 | 3.742
2015-07-01 | 3.759
2015-08-01 | 3.7625
2015-09-01 | 3.742
2015-10-01 | 3.7855
2015-11-01 | 4.2715
2015-12-01 | 4.7065 | 4.128
2016-01-01 | 5.1525
2016-02-01 | 5.017
2016-03-01 | 4.408
2016-04-01 | 3.899
2016-05-01 | 3.84
2016-06-01 | 3.852
2016-07-01 | 3.869
2016-08-01 | 3.8725
2016-09-01 | 3.852
2016-10-01 | 3.8955
2016-11-01 | 4.3815
2016-12-01 | 4.8165 | 4.238
2017-01-01 | 5.2675
2017-02-01 | 5.132
2017-03-01 | 4.523
2017-04-01 | 4.014
2017-05-01 | 3.955
2017-06-01 | 3.967
2017-07-01 | 3.984
2017-08-01 | 3.9875
2017-09-01 | 3.967
2017-10-01 | 4.0105
2017-11-01 | 4.4965
2017-12-01 | 4.9315 | 4.353
2018-01-01 | 5.3875
2018-02-01 | 5.252
2018-03-01 | 4.643
2018-04-01 | 4.134
2018-05-01 | 4.075
2018-06-01 | 4.087
2018-07-01 | 4.104
2018-08-01 | 4.1075
2018-09-01 | 4.087
2018-10-01 | 4.1305
2018-11-01 | 4.6165
2018-12-01 | 5.0515 | 4.473
2019-01-01 | 5.5125
2019-02-01 | 5.377
2019-03-01 | 4.768
2019-04-01 | 4.259
2019-05-01 | 4.2
2019-06-01 | 4.212
2019-07-01 | 4.229
2019-08-01 | 4.2325
2019-09-01 | 4.212
2019-10-01 | 4.2555
2019-11-01 | 4.7415
2019-12-01 | 5.1765 | 4.598
2020-01-01 | 5.6425
2020-02-01 | 5.507
2020-03-01 | 4.898
2020-04-01 | 4.389
2020-05-01 | 4.33
2020-06-01 | 4.342
2020-07-01 | 4.359
2020-08-01 | 4.3625
2020-09-01 | 4.342
2020-10-01 | 4.3855
2020-11-01 | 4.8715
2020-12-01 | 5.3065 | 4.728
2021-01-01 | 5.7775
2021-02-01 | 5.642
2021-03-01 | 5.033
2021-04-01 | 4.524
2021-05-01 | 4.465
2021-06-01 | 4.477
2021-07-01 | 4.494
2021-08-01 | 4.4975
2021-09-01 | 4.477
2021-10-01 | 4.5205
2021-11-01 | 5.0065
2021-12-01 | 5.4415 | 4.863

## Fixed and Variable Costs
United American Energy | PRELIMINARY ECONOMIC ANALYSIS
Lowell Power Expansion
Feb 23 Meeting with Enron Capital and Trade
Operations Summary
FIXED COSTS
Labor |  | 100 | add one+ maintenance
Annual Inspection of Gas Turbines |  | 100
Fixed - maint & consum |  | 193.75 | per S&S
Operator Fee |  | 100
G&A
Property & BI Insurance |  | 400
Replacement Power Insurance |  | discuss
Real Property Taxes |  | 500 | same as existing PILOT
Water Supply/Discharge |  | 100 | cooling tower
Interconnect and NEPOOL Fees |  | 150
Audit/Miscellaneous |  | 50
NOx Budget |  | 75
Asset Mgt. Cost |  | 100
1868.75
VARIABLE COSTS | $/mwhr | Cost | Energy | hrs/yr | Capacity
LM6000 | 2.3187 | 1258.9348 | 542942.5855 | 2450.1019 | 221.6
Consumables | 0.15418 | 83.7091 | 542942.5855

## Returns Analysis
PROJECT NAME: UAE-Lowell
RETURNS ANALYSIS
| 0 | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) | Close | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| 2000-06-01 | 2001-12-30 12:00 | 2002-12-30 18:00 | 2003-12-31 | 2004-12-30 06:00 | 2005-12-30 12:00 | 2006-12-30 18:00 | 2007-12-31 | 2008-12-30 06:00 | 2009-12-30 12:00 | 2010-12-30 18:00 | 2011-12-31 | 2012-12-30 06:00 | 2013-12-30 12:00 | 2014-12-30 18:00 | 2015-12-31 | 2016-12-30 06:00 | 2017-12-30 12:00 | 2018-12-30 18:00 | 2019-12-31 | 2020-12-30 06:00 | 2021-12-30 12:00 | 2022-12-30 18:00 | 2023-12-31 | 2024-12-30 06:00 | 2025-12-30 12:00 | 2026-12-30 18:00 | 2027-12-31 | 2028-12-30 06:00 | 2029-12-30 12:00 | 2030-12-30 18:00 | 2031-12-31
EBITDA | 0 | 3719.3333 | 5730.9 | 5708.403 | 5685.2923 | 5661.5507 | 5637.1605 | 5612.1036 | 5586.3612 | 5559.914 | 5532.7424 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805 | -1481.856 | -1520.5287 | -1560.2706 | -1601.1121 | -1643.0841 | -1686.2188 | -1730.5491 | -1776.1089 | -1822.9331 | -1871.0576
Less Interest Payments | 0 | -2360.0578 | -5706.4052 | -5819.0149 | -5943.6285 | -6067.0056 | -6215.6295 | -6373.876 | -6551.8656 | -6731.9889 | -6943.6468 | -7169.957 | -7422.5265 | -7681.8442 | -7981.472 | -8302.7048 | -8659.2503 | -9028.8729 | -9451.0286 | -9904.3999 | -10405.6486 | -10978.091 | -11822.1228 | -12883.2695 | -14076.2596 | -15342.2542 | -16748.4054 | -18265.0742 | -19926.0088 | -21687.1295 | -23643.2695 | -14729.5983
Pre-Tax Cashflow | 0 | 1359.2755 | 24.4948 | -110.6119 | -258.3362 | -405.4549 | -578.469 | -761.7724 | -965.5044 | -1172.0749 | -1410.9044 | -1665.131 | -1946.3827 | -2235.17 | -2565.0769 | -2917.421 | -3305.9336 | -3708.403 | -4164.3103 | -4652.3633 | -5189.2502 | -9936.8105 | -13303.9788 | -14403.7982 | -15636.5302 | -16943.3662 | -18391.4895 | -19951.293 | -21656.558 | -23463.2384 | -25466.2026 | -16600.6559
Less Cash Taxes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Principal Payments | 0 | 566.054 | 1330.0755 | 1423.6212 | 1562.9155 | 1710.3925 | 1874.6746 | 2052.0678 | 2246.8006 | 2452.9871 | 2682.4801 | 2930.1216 | 3201.7381 | 3489.3126 | 3809.2073 | 4154.2123 | 4532.3786 | 4932.7094 | 5377.8493 | 5857.7205 | 6383.4664 | 9379.1318 | 12478.1228 | 14045.4902 | 15269.6636 | 16565.2287 | 18004.2668 | 19553.8932 | 21249.6056 | 23043.7228 | 25036.5458 | 16518.4769
Less Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cashflow to Equity | 0 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | -557.6787 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -82.1789
Distribution to Equity | 2000-06-01: 100%
| 0 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | -557.6787 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -82.1789
Equity RROR | 2000-06-01: 14%
Beginning Balance | 13291.6316 | 13291.6316 | 17077.7895 | 20823.2503 | 25051.5146 | 29863.306 | 35349.1064 | 41594.1869 | 48707.6684 | 56808.0381 | 66042.0757 | 76559.5421 | 88542.8686 | 102194.2255 | 117755.5596 | 135485.4684 | 155690.2252 | 178713.3018 | 204957.4704 | 234865.0553 | 268951.5202 | 307798.9493 | 350333.1235 | 398553.9048 | 453993.1435 | 517185.317 | 589213.1238 | 671315.7384 | 764902.542 | 871581.9455 | 993183.9023 | 1131799.9917
RROR Target Coupon | 0 | -1860.8284 | -2390.8905 | -2915.255 | -3507.212 | -4180.8628 | -4948.8749 | -5823.1862 | -6819.0736 | -7953.1253 | -9245.8906 | -10718.3359 | -12396.0016 | -14307.1916 | -16485.7783 | -18967.9656 | -21796.6315 | -25019.8622 | -28694.0459 | -32881.1077 | -37653.2128 | -43091.8529 | -49046.6373 | -55797.5467 | -63559.0401 | -72405.9444 | -82489.8373 | -93984.2034 | -107086.3559 | -122021.4724 | -139045.7463 | -158451.9988
Actual Cash Flow | 0 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | -557.6787 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -82.1789
Equity Paydown | 0 | 3786.158 | 3745.4608 | 4228.2643 | 4811.7913 | 5485.8004 | 6245.0805 | 7113.4815 | 8100.3697 | 9234.0376 | 10517.4663 | 11983.3265 | 13651.3569 | 15561.3341 | 17729.9087 | 20204.7568 | 23023.0766 | 26244.1687 | 29907.5849 | 34086.4649 | 38847.429 | 42534.1742 | 48220.7813 | 55439.2387 | 63192.1735 | 72027.8068 | 82102.6146 | 93586.8036 | 106679.4035 | 121601.9568 | 138616.0895 | 158369.8199
Ending Balance | 13291.6316 | 17077.7895 | 20823.2503 | 25051.5146 | 29863.306 | 35349.1064 | 41594.1869 | 48707.6684 | 56808.0381 | 66042.0757 | 76559.5421 | 88542.8686 | 102194.2255 | 117755.5596 | 135485.4684 | 155690.2252 | 178713.3018 | 204957.4704 | 234865.0553 | 268951.5202 | 307798.9493 | 350333.1235 | 398553.9048 | 453993.1435 | 517185.317 | 589213.1238 | 671315.7384 | 764902.542 | 871581.9455 | 993183.9023 | 1131799.9917 | 1290169.8116
ENRON'S RETURNS ANALYSIS
Zero Residual Value
Equity Return | 2000-06-01: 13291.6316
Actual Cash Flow | 0 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | -557.6787 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -82.1789
Total Cash Flow | 13291.6316 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | -557.6787 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -82.1789
| IRR | 2.98e-07%
With 5x EBITDA Exit Multiple
Equity Return | 2000-06-01: 13291.6316
Actual Cash Flow | 0 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | -557.6787 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -82.1789
Residual Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5206.4026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9114.6656
Total Cash Flow | 13291.6316 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | 4648.7239 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -9196.8445
| IRR | #NUM!
With 40% Initial Project Cost
Equity Return | 2000-06-01: 13291.6316
Actual Cash Flow | 0 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | -557.6787 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -82.1789
Residual Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22000
Total Cash Flow | 13291.6316 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | 21442.3213 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | 21917.8211
| IRR | #NUM!
With $200/kW
Equity Return | 2000-06-01: 13291.6316
Actual Cash Flow | 0 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | -557.6787 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | -82.1789
Residual Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18400
Total Cash Flow | 13291.6316 | 1925.3296 | 1354.5702 | 1313.0093 | 1304.5793 | 1304.9376 | 1296.2056 | 1290.2954 | 1281.2962 | 1280.9122 | 1271.5757 | 1264.9906 | 1255.3553 | 1254.1426 | 1244.1304 | 1236.7912 | 1226.445 | 1224.3064 | 1213.539 | 1205.3572 | 1194.2162 | 17842.3213 | -825.856 | -358.3079 | -366.8666 | -378.1376 | -387.2227 | -397.3998 | -406.9524 | -419.5156 | -429.6569 | 18317.8211
| IRR | #NUM!

## Price_Technical Assumption
PROJECT NAME: UAE-Lowell
PRICE/TECHNICAL ASSUMPTIONS
|  | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
|  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
CAPACITY PRICE $/kW-MONTH
| Fixed Price | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Merchant Price
1 | Base | 5.4933 | 5.6581 | 5.6458 | 5.7213 | 5.6998 | 5.7713 | 5.8419 | 5.9116 | 6.0889 | 6.1596 | 6.3444 | 6.4159 | 6.6084 | 6.6806 | 6.7512 | 6.82 | 6.8869 | 6.9516 | 7.014 | 7.0739 | 7.1311 | 7.1854 | 7.2396 | 7.2939 | 7.3482 | 7.4024 | 7.4567 | 7.5109 | 7.5652 | 7.6195 | 7.6737
2 | Low | 4.3775 | 4.5088 | 4.7352 | 4.8772 | 5.0235 | 5.1742 | 5.3295 | 5.2782 | 5.2191 | 5.0397 | 4.9602 | 4.8713 | 4.8951 | 4.9159 | 4.8037 | 4.8141 | 4.8208 | 4.9654 | 5.1144 | 5.1173 | 5.2708 | 5.429 | 5.5871 | 5.7452 | 5.9033 | 6.0615 | 6.2196 | 6.3777 | 6.5358 | 6.694 | 6.8521
3 | Index | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Custom | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Market Price Scenario | 5.4933 | 5.6581 | 5.6458 | 5.7213 | 5.6998 | 5.7713 | 5.8419 | 5.9116 | 6.0889 | 6.1596 | 6.3444 | 6.4159 | 6.6084 | 6.6806 | 6.7512 | 6.82 | 6.8869 | 6.9516 | 7.014 | 7.0739 | 7.1311 | 7.1854 | 7.2396 | 7.2939 | 7.3482 | 7.4024 | 7.4567 | 7.5109 | 7.5652 | 7.6195 | 7.6737
| Blended Capacity Price | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.7541 | 7.1854 | 7.2396 | 7.2939 | 7.3482 | 7.4024 | 7.4567 | 7.5109 | 7.5652 | 7.6195 | 7.6737
GAS PRICE $/MMBTU
1 | Index (Tenn Zone 6) | 3.1784 | 3.1597 | 3.1917 | 3.2409 | 3.3 | 3.363 | 3.428 | 3.498 | 3.573 | 3.653 | 3.738 | 3.8161 | 3.8857 | 4.023 | 4.128 | 4.238 | 4.353 | 4.473 | 4.598 | 4.728 | 4.863 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
2 | Fixed | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
3 | Custom | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Sales Tax Rate | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
1 | Gas Price Assumption | 3.2261 | 3.2071 | 3.2396 | 3.2895 | 3.3495 | 3.4134 | 3.4794 | 3.5504 | 3.6266 | 3.7078 | 3.794 | 3.8733 | 3.944 | 4.0833 | 4.1899 | 4.3015 | 4.4183 | 4.5401 | 4.6669 | 4.7989 | 4.9359 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233
ENERGY PRICE $/MWH
| Fuel | 33.2348 | 33.0391 | 33.3742 | 33.8883 | 34.507 | 35.1649 | 35.8445 | 36.5765 | 37.3607 | 38.1973 | 39.0861 | 39.903 | 40.6306 | 42.0662 | 43.1641 | 44.3143 | 45.5168 | 46.7716 | 48.0787 | 49.438 | 50.8497 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044 | 23.0044
| Variable O&M | 1.5299 | 1.5757 | 1.623 | 1.6717 | 1.7219 | 1.7735 | 1.8267 | 1.8815 | 1.938 | 1.9961 | 2.056 | 2.1177 | 2.1812 | 2.2466 | 2.314 | 2.3835 | 2.455 | 2.5286 | 2.6045 | 2.6826 | 2.7631 | 2.846 | 2.9314 | 3.0193 | 3.1099 | 3.2032 | 3.2993 | 3.3982 | 3.5002 | 3.6052 | 3.7134
| Marginal Cost of Generation | 34.7646 | 34.6149 | 34.9972 | 35.56 | 36.2288 | 36.9384 | 37.6713 | 38.458 | 39.2987 | 40.1934 | 41.1421 | 42.0207 | 42.8118 | 44.3128 | 45.4782 | 46.6978 | 47.9718 | 49.3002 | 50.6832 | 52.1206 | 53.6128 | 25.8503 | 25.9357 | 26.0237 | 26.1142 | 26.2075 | 26.3036 | 26.4026 | 26.5046 | 26.6096 | 26.7177
Pass-through | Energy Price Assumption | 34.7646 | 34.6149 | 34.9972 | 35.56 | 36.2288 | 36.9384 | 37.6713 | 38.458 | 39.2987 | 40.1934 | 41.1421 | 42.0207 | 42.8118 | 44.3128 | 45.4782 | 46.6978 | 47.9718 | 49.3002 | 50.6832 | 52.1206 | 53.6128 | 25.8503 | 25.9357 | 26.0237 | 26.1142 | 26.2075 | 26.3036 | 26.4026 | 26.5046 | 26.6096 | 26.7177
HEAT RATE (HHV)
| New and Clean | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100 | 10100
Degradation (%) | bar: 2001 to 2031
| Net Heat Rate | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302 | 10302

## Cash Flows
PROJECT NAME: UAE-Lowell
Cash Flows
| 0 | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667
('000 $) | Close | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
| 2000-06-01 | 2001-12-30 12:00 | 2002-12-30 18:00 | 2003-12-31 | 2004-12-30 06:00 | 2005-12-30 12:00 | 2006-12-30 18:00 | 2007-12-31 | 2008-12-30 06:00 | 2009-12-30 12:00 | 2010-12-30 18:00 | 2011-12-31 | 2012-12-30 06:00 | 2013-12-30 12:00 | 2014-12-30 18:00 | 2015-12-31 | 2016-12-30 06:00 | 2017-12-30 12:00 | 2018-12-30 18:00 | 2019-12-31 | 2020-12-30 06:00 | 2021-12-30 12:00
EBITDA | 0 | 3719.3333 | 5730.9 | 5708.403 | 5685.2923 | 5661.5507 | 5637.1605 | 5612.1036 | 5586.3612 | 5559.914 | 5532.7424 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
Less Interest Payments (Debt Years 1-7) | 2000-06-01: 0; 2001-12-30 12:00: -2695; 2002-12-30 18:00: -2499.9426; 2003-12-31: -2291.2312; 2004-12-30 06:00: -2067.9101; 2005-12-30 12:00: -1828.9564; 2006-12-30 18:00: -1573.276; 2007-12-31: -1299.6979; 2008-12-30 06:00: -1006.9694; 2009-12-30 12:00: -693.7499; 2010-12-30 18:00: -358.605
Less Interest Payments (Lease) & (Int. Years 6-20) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Interest Payments (Debt Years 8-20) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pre-Tax Cashflow | 0 | 1024.3333 | 3230.9574 | 3417.1718 | 3617.3822 | 3832.5943 | 4063.8845 | 4312.4056 | 4579.3917 | 4866.1641 | 5174.1374 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
Less Cash Taxes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Principal Payments (Debt Years 1-7) | 2000-06-01: 0; 2001-12-30 12:00: -2786.5339; 2002-12-30 18:00: -2981.5912; 2003-12-31: -3190.3026; 2004-12-30 06:00: -3413.6238; 2005-12-30 12:00: -3652.5775; 2006-12-30 18:00: -3908.2579; 2007-12-31: -4181.8359; 2008-12-30 06:00: -4474.5644; 2009-12-30 12:00: -4787.784; 2010-12-30 18:00: -5122.9288
Less Principal Payments (Lease Years 6-20) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Principal Payments (Debt Years 8-20) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Lease Principal Payments | 2000-06-01: 0; 2001-12-30 12:00: 0; 2002-12-30 18:00: 0; 2003-12-31: 0; 2004-12-30 06:00: 0; 2005-12-30 12:00: 0
Add Depreciation (Lease) | 2000-06-01: 0; 2001-12-30 12:00: 0; 2002-12-30 18:00: 0; 2003-12-31: 0; 2004-12-30 06:00: 0; 2005-12-30 12:00: 0; 2006-12-30 18:00: 0; 2007-12-31: 0; 2008-12-30 06:00: 0; 2009-12-30 12:00: 0; 2010-12-30 18:00: 0
Less Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cashflow to Equity | 0 | -1762.2005 | 249.3661 | 226.8691 | 203.7584 | 180.0168 | 155.6266 | 130.5697 | 104.8273 | 78.3802 | 51.2086 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
Equity Distribution Percentage | 2000-06-01: 100%
Distribution to ENA | 0 | -1762.2005 | 249.3661 | 226.8691 | 203.7584 | 180.0168 | 155.6266 | 130.5697 | 104.8273 | 78.3802 | 51.2086 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
Distribution to UAE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Option
Capacity Price | 2000-06-01: 6
ENRON'S RETURN ANALYSIS |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Equity Return | -5500
Actual Cash Flow | 0 | -1762.2005 | 249.3661 | 226.8691 | 203.7584 | 180.0168 | 155.6266 | 130.5697 | 104.8273 | 78.3802 | 51.2086 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
Debt Repayment - No Bullet | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cash In Flow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Cash Flow - 5 Year Term | -5500 | 1: -1762.2005; 2: 249.3661; 3: 226.8691; 4: 203.7584; 5: 180.0168
Total Cash Flow - 20 Year Term | -5500 | -1762.2005 | 249.3661 | 226.8691 | 203.7584 | 180.0168 | 155.6266 | 130.5697 | 104.8273 | 78.3802 | 51.2086 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
5 Year Term | IRR | 1: #NUM!
| NPV | 1: -5642.2798
20 Year Term | IRR | 1: 14.98%
| NPV | 1: 393.9357
UAE's RETURN ANALYSIS
Equity Return | 0
Actual Cash Flow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Debt Repayment - No Bullet | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cash In Flow (Trapped Cash) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Cash Flow - 5 Year Term | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0
Total Cash Flow - 20 Year Term | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 Year Term | IRR | 1: #NUM!
| NPV | 1: 0
20 Year Term | IRR | 1: #NUM!
| NPV | 1: 0
10-Yr. Debt Option w/ 10 Yr. Amort
Equity Distribution Percentage | 100%
Capacity Price | 6
ENRON'S RETURN ANALYSIS |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Equity Return | -16500
Actual Cash Flow | 0 | -1762.2005 | 249.3661 | 226.8691 | 203.7584 | 180.0168 | 155.6266 | 130.5697 | 104.8273 | 78.3802 | 51.2086 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
Resid Value |  | 10: 22000
Debt Repayment - Bullet | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0
Total Cash Flow - 10 Year Term | -16500 | 1: -1762.2005; 2: 249.3661; 3: 226.8691; 4: 203.7584; 5: 180.0168; 6: 155.6266; 7: 130.5697; 8: 104.8273; 9: 78.3802; 10: 22051.2086
Total Cash Flow - 20 Year Term | -16500 | -1762.2005 | 249.3661 | 226.8691 | 203.7584 | 180.0168 | 155.6266 | 130.5697 | 104.8273 | 78.3802 | 22051.2086 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
10 Year Term | IRR | 1: 2.473%
| NPV | 1: -10317.3772
20 Year Term | IRR | 1: 11.29%
| NPV | 1: -4490.6385
UAE's RETURN ANALYSIS
Equity Return | 0
Actual Cash Flow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Debt Repayment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cash In Flow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Cash Flow - 7 Year Term | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0
Total Cash Flow - 20 Year Term | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10-Yr. Debt Option
With 20% of Initial Project Costs
Equity Return | -16500 | 11: New Debt
Actual Cash Flow | 0 | -1762.2005 | 249.3661 | 226.8691 | 203.7584 | 180.0168 | 155.6266 | 130.5697 | 104.8273 | 78.3802 | 51.2086 | 5504.826 | 5476.1438 | 5446.6742 | 5416.3951 | 5385.2838 | 5353.3168 | 5320.4699 | 5286.7183 | 5252.0366 | 5216.3984 | 1041.2805
Debt Repayment - First Level | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0
Debt Repayment - Second Level | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0
Total Cash Flow | -16500 | 1: -1762.2005; 2: 249.3661; 3: 226.8691; 4: 203.7584; 5: 180.0168; 6: 155.6266; 7: 130.5697; 8: 104.8273; 9: 78.3802; 10: 51.2086
| IRR | 1: -32.93%
| NPV | 1: -15046.1281
7 Year Term | IRR | 1: #NUM!
| NPV | 1: 0
20 Year Term | IRR | 1: #NUM!
| NPV | 1: 0

## Summary
Enron Return Analysis
2000-04-21 11:42
| Capacity Price | NPV @ 15% (000's) | IRR
5 Year Lease Structure | 4.5 | 5920.9086 | 50.94%
| 5 | 7738.3171 | 60.76%
| 5.5 | 9555.7256 | 70.26%
| 6 | 11373.134 | 79.53%
| 6.5 | 13190.5425 | 88.6%
20 Year Lease Structure With Debt | 4.5 | 6754.9595 | 41.52%
Refinancing in Year 6 - 20 | 5 | 9596.2895 | 49.29%
| 5.5 | 12114.4601 | 56.04%
| 6 | 14436.0288 | 62.1%
| 6.5 | 16643.3456 | 67.61%
7 Year Debt Structure | 4.5 | -17330.527 | N/A
| 5 | -15033.431 | -31.26%
| 5.5 | -12736.335 | -17.73%
| 6 | -10449.6171 | -9.575%
| 6.5 | -8906.3561 | -6.739%
20 Year Debt Structure With Debt | 4.5 | -13521.3664 | 2.466%
Refinancing in Year 8-20 | 5 | -10682.1542 | 4.377%
| 5.5 | -8166.1016 | 6.438%
| 6 | -5846.6507 | 8.502%
| 6.5 | -3641.4518 | 10.52%
Notes: Lease Structure
Years 1-5: 8.0% Rate; 90/10 D/E: Capacity @ $4.50
Years 6-20: 8.75% Rate;
Notes: Debt Structure
Years 1-7: 70/30 D/E; 9.5% Rate; 12 year amort.

## Amortization
Amortization
Schedules
|  |  | Lease | Debt (7 Yr.) | Debt (13 Yr.) | Debt (15 Yr.)
|  | Plant Turnkey Price | 55000 | 55000 | 55000 | 55000
|  | Debt Term (yrs) | 5 | 10 | 13 | 15
|  | Rate (%) | 8% | 9.5% | 8.75% | 8.75%
|  | Princ Amort Sched (yrs) | 0 | 10 | 13 | 15
|  | Equity (%) | 10% | 30% | 30% | 30%
|  | Equity ($) | 5500 | 16500 | 16500 | 16500
|  | Posted LC | 30000 | 0 | 0 | 0
Lease Years 1 -5 | 2001 | 2002 | 2003 | 2004 | 2005
Principal Balance | 49500 | 49500 | 49500 | 49500 | 49500
Payment | 3960 | 3960 | 3960 | 3960 | 3960
Interest Payment | 3960 | 3960 | 3960 | 3960 | 3960
Principal Payment | 0 | 0 | 0 | 0 | 0
7 Year Debt w/ 12 yr. Amort | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007
Principal Balance | 38500 | 35713.4661 | 32731.8749 | 29541.5723 | 26127.9485 | 22475.3711 | 18567.1132
Payment | 6444.0339 | 6374.3705 | 6299.8307 | 6220.0732 | 6134.7326 | 6043.4181 | 5945.7117
Interest Payment | 3657.5 | 3392.7793 | 3109.5281 | 2806.4494 | 2482.1551 | 2135.1603 | 1763.8758
Principal Payment | 2786.5339 | 2981.5912 | 3190.3026 | 3413.6238 | 3652.5775 | 3908.2579 | 4181.8359
13 Year Debt | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Principal Balance | 38500 | 36877.1458 | 35100.1204 | 33154.2777 | 31023.5798 | 28690.4657 | 26135.7057 | 23338.2435 | 20275.0225 | 16920.7954 | 13247.9167 | 9226.1146 | 4822.2413
Payment | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542 | 5280.3542
Interest Payment | 3657.5 | 3503.3288 | 3334.5114 | 3149.6564 | 2947.2401 | 2725.5942 | 2482.892 | 2217.1331 | 1926.1271 | 1607.4756 | 1258.5521 | 876.4809 | 458.1129
Principal Payment | 1622.8542 | 1777.0254 | 1945.8428 | 2130.6978 | 2333.1141 | 2554.76 | 2797.4622 | 3063.2211 | 3354.2271 | 3672.8787 | 4021.8021 | 4403.8733 | 4822.2413
15 Year Debt | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Principal Balance | 19500 | 18210.4051 | 16807.9707 | 15282.8233 | 13624.2255 | 11820.5004 | 9858.9493 | 7725.7625 | 5405.9218 | 2883.0951 | 139.5211 | -2844.1157 | -6088.8207 | -9617.4373 | -13454.808
Payment | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904 | 4538.2904
Interest Payment | 3248.6955 | 3135.8559 | 3013.1429 | 2879.6925 | 2734.5652 | 2576.7393 | 2405.1036 | 2218.4497 | 2015.4637 | 1794.7163 | 1554.6536 | 1293.5854 | 1009.6737 | 700.9197 | 365.1498
Principal Payment | 1289.5949 | 1402.4344 | 1525.1474 | 1658.5978 | 1803.7251 | 1961.5511 | 2133.1868 | 2319.8406 | 2522.8267 | 2743.574 | 2983.6368 | 3244.705 | 3528.6167 | 3837.3706 | 4173.1406

## Debt Structs
|  |  | Debt | Lease
|  | Plant Turnkey Price | 55000 | 55000
|  | Debt Term (yrs) | 10 | 5
|  | Rate (%) | 7% | 8%
|  | Princ Amort Sched (yrs) | 10 | 0
|  | Equity (%) | 30% | 10%
|  | Equity ($) | 16500 | 5500
|  | Posted LC | 0 | 0
|  | Turbines (#) | 2 | 2
|  | Capacity (MW) | 92 | 92
|  | Capacity Pmt ($/kw-mo) | 6.5 | 4.25
[15 empty] | Total $ | $/kw/mo
| 12 yr Amort |  |  |  |  | 7 yr Term with 12 yr. Amort. |  |  |  |  | 100% Lease |  |  |  | Pmt Diff | Pmt Diff
| Prin Bal | Pmt | Int Pmt | Prin Pmt |  | Prin Bal | Pmt | Int Pmt | Prin Pmt |  | Prin Bal | Pmt | Int Pmt | Prin Pmt
1 | 38500 | 5481.5339 | 2695 | 2786.5339 | 1 | 38500 | 5481.5339 | 2695 | 2786.5339 | 1 | 49500 | 3960 | 3960 | 0 | 1521.5339 | 1.3782
2 | 35713.4661 | 5481.5339 | 2499.9426 | 2981.5912 | 2 | 35713.4661 | 5481.5339 | 2499.9426 | 2981.5912 | 2 | 49500 | 3960 | 3960 | 0
3 | 32731.8749 | 5481.5339 | 2291.2312 | 3190.3026 | 3 | 32731.8749 | 5481.5339 | 2291.2312 | 3190.3026 | 3 | 49500 | 3960 | 3960 | 0 | 42000
4 | 29541.5723 | 5481.5339 | 2067.9101 | 3413.6238 | 4 | 29541.5723 | 5481.5339 | 2067.9101 | 3413.6238 | 4 | 49500 | 3960 | 3960 | 0 | 0.15
5 | 26127.9485 | 5481.5339 | 1828.9564 | 3652.5775 | 5 | 26127.9485 | 5481.5339 | 1828.9564 | 3652.5775 | 5 | 49500 | 3960 | 3960 | 0 | 6300 | 5.7065
6 | 22475.3711 | 5481.5339 | 1573.276 | 3908.2579 | 6 | 22475.3711 | 5481.5339 | 1573.276 | 3908.2579
7 | 18567.1132 | 5481.5339 | 1299.6979 | 4181.8359 | 7 | 18567.1132 | 5481.5339 | 1299.6979 | 4181.8359 | [6 empty] | 7.0847
8 | 14385.2772 | 5481.5339 | 1006.9694 | 4474.5644
9 | 9910.7128 | 5481.5339 | 693.7499 | 4787.784
10 | 5122.9288 | 5481.5339 | 358.605 | 5122.9288 | [5 empty] | 100% Lease with Principal Payment (12 yr. Amort.)
11 | 2.6375e-11 | 5481.5339 | 1.8463e-12 | 5481.5339 | [6 empty] | Prin Bal | Pmt | Int Pmt | Prin Pmt
12 | -5481.5339 | 5481.5339 | -383.7074 | 5865.2412 | [5 empty] | 1 | 49500 | 6746.5339 | 3960 | 2786.5339
[10 empty] | 2 | 46713.4661 | 6718.6685 | 3737.0773 | 2981.5912
[10 empty] | 3 | 43731.8749 | 6688.8526 | 3498.55 | 3190.3026
[10 empty] | 4 | 40541.5723 | 6656.9496 | 3243.3258 | 3413.6238
[10 empty] | 5 | 37127.9485 | 6622.8133 | 2970.2359 | 3652.5775
10 yr Amort
| Prin Bal | Pmt | Int Pmt | Prin Pmt
1 | 38500 | 5481.5339 | 2695 | 2786.5339
2 | 35713.4661 | 5481.5339 | 2499.9426 | 2981.5912
3 | 32731.8749 | 5481.5339 | 2291.2312 | 3190.3026
4 | 29541.5723 | 5481.5339 | 2067.9101 | 3413.6238
5 | 26127.9485 | 5481.5339 | 1828.9564 | 3652.5775
6 | 22475.3711 | 5481.5339 | 1573.276 | 3908.2579
7 | 18567.1132 | 5481.5339 | 1299.6979 | 4181.8359
8 | 14385.2772 | 5481.5339 | 1006.9694 | 4474.5644
9 | 9910.7128 | 5481.5339 | 693.7499 | 4787.784
10 | 5122.9288 | 5481.5339 | 358.605 | 5122.9288
|  |  | Debt | Lease
|  | Plant Turnkey Price | 55000 | 55000
|  | Debt Term (yrs) | 7 | 5
|  | Rate (%) | 9.5% | 8.75%
|  | Princ Amort Sched (yrs) | 15 | 0
|  | Equity (%) | 30% | 10%
|  | Equity ($) | 16500 | 5500
|  | Posted LC | 0 | 0
Payment to Equal Lease
|  | Turbines (#) | 5 | 5
|  | Capacity (MW) | 230 | 230
|  | Capacity Pmt ($/kw-mo) | 6.5 | 4.25
| 15 yr Amort on Lease Structure | [5 empty] | 13 yr Amort Debt Structure
Year | Prin Bal | Pmt | Int Pmt | Prin Pmt |  | Year | Prin Bal | Pmt | Int Pmt | Prin Pmt
2006 | 37127.9485 | 4538.2904 | 3248.6955 | 1289.5949 |  | 2008 | 38500 | 5280.3542 | 3657.5 | 1622.8542
2007 | 35838.3537 | 4538.2904 | 3135.8559 | 1402.4344 |  | 2009 | 36877.1458 | 5280.3542 | 3503.3288 | 1777.0254
2008 | 34435.9192 | 4538.2904 | 3013.1429 | 1525.1474 |  | 2010 | 35100.1204 | 5280.3542 | 3334.5114 | 1945.8428
2009 | 32910.7718 | 4538.2904 | 2879.6925 | 1658.5978 |  | 2011 | 33154.2777 | 5280.3542 | 3149.6564 | 2130.6978
2010 | 31252.174 | 4538.2904 | 2734.5652 | 1803.7251 |  | 2012 | 31023.5798 | 5280.3542 | 2947.2401 | 2333.1141
2011 | 29448.4489 | 4538.2904 | 2576.7393 | 1961.5511 |  | 2013 | 28690.4657 | 5280.3542 | 2725.5942 | 2554.76
2012 | 27486.8978 | 4538.2904 | 2405.1036 | 2133.1868 |  | 2014 | 26135.7057 | 5280.3542 | 2482.892 | 2797.4622
2013 | 25353.711 | 4538.2904 | 2218.4497 | 2319.8406 |  | 2015 | 23338.2435 | 5280.3542 | 2217.1331 | 3063.2211
2014 | 23033.8703 | 4538.2904 | 2015.4637 | 2522.8267 |  | 2016 | 20275.0225 | 5280.3542 | 1926.1271 | 3354.2271
2015 | 20511.0436 | 4538.2904 | 1794.7163 | 2743.574 |  | 2017 | 16920.7954 | 5280.3542 | 1607.4756 | 3672.8787
2016 | 17767.4696 | 4538.2904 | 1554.6536 | 2983.6368 |  | 2018 | 13247.9167 | 5280.3542 | 1258.5521 | 4021.8021
2017 | 14783.8328 | 4538.2904 | 1293.5854 | 3244.705 |  | 2019 | 9226.1146 | 5280.3542 | 876.4809 | 4403.8733
2018 | 11539.1279 | 4538.2904 | 1009.6737 | 3528.6167 |  | 2020 | 4822.2413 | 5280.3542 | 458.1129 | 4822.2413
2019 | 8010.5112 | 4538.2904 | 700.9197 | 3837.3706
2020 | 4173.1406 | 4538.2904 | 365.1498 | 4173.1406

## Performance
UAE Lowell Power Expansion |  | Single LM6000 Unit
Equipment Performance |  | Ambient vs. Front End Simple Cycle Technology
5 - GE/S&S LM6000 Units
|  | 0 oF |  |  | 60 oF |  |  | 90 oF
|  | DLE | Spr. w/ WI | Spr. w/ SI | DLE | Spr. w/ WI | Spr. w/ SI | DLE | Spr. w/ WI | Spr. w/ SI
General Plant Performance Data
Generator Power, MW |  | S | 48.76 | 48.76 | 44.28 | 46.13 | 47.35 | 44.32 | 46.04 | 47.25
Gross Heat Rate, Btu/kWh (LHV) |  | & | 8338 | 8338 | 8261 | 8557 | 7934 | 8260 | 8555 | 7938
Gross Heat Rate, Btu/kWh (HHV) (3) |  | S | 9264.4352 | 9264.4352 | 9178.8797 | 9507.7683 | 8815.5467 | 9177.7686 | 9505.5461 | 8819.9912
Gross Heat Rate Adjusted for Steam Use, Btu/kWh (HHV) |  |  | na | 10132.1649 | na | na | 9665.9845 | na | na | 9664.0761
Fuel Flow, mmBtu/hr (LHV) |  |  | 406.5609 | 406.5609 | 365.7971 | 394.7344 | 375.6749 | 366.0832 | 393.8722 | 375.0705
Fuel Flow, mmBtu/hr (HHV) |  |  | 451.2826 | 451.2826 | 406.0348 | 438.1552 | 416.9991 | 406.3524 | 437.1981 | 416.3283
Chilling Requirements, tons |  | R | 0 | 0 | 210 | 208 | 212 | 1892 | 1590 | 1905
Water Injection Flow, pph |  | u | 20548 | 0 | 0 | 20835 | 0 | 0 | 20593 | 0
Steam Injection Flow, pph |  | n | 0 | 33500 | 0 | 0 | 31883 | 0 | 0 | 31578
Sprint Water Injection Flow, pph |  | s | 0 | 0 | 0 | 2445 | 2445 | 0 | 2445 | 2445
Aux Load (kW) (2) |  |  | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200
Chiller Aux. Load (kW) |  |  | 0 | 0 | 272 | 270.6 | 273.4 | 1449.4 | 1238 | 1458.5
Net Power Output, MW |  | @ | 47.56 | 47.56 | 42.808 | 44.6594 | 45.8766 | 41.6706 | 43.602 | 44.5915
NOx, ppm |  | 2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
NOx, pph |  | 0 | 41 | 41 | 37 | 40 | 38 | 37 | 40 | 38
CO, ppm |  | oF | 80 | 80 | 25 | 29 | 23 | 25 | 28 | 23
CO, pph |  |  | 80 | 80 | 22 | 28 | 22 | 22 | 27 | 21
Expected DEP NOx Emission Rate, ppm |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Reduction Required |  |  | 92% | 92% | 92% | 92% | 92% | 92% | 92% | 92%
Expected DEP NOx Emission Rate, lb/mmBtu |  |  | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729 | 0.0073729
Expected DEP NOx Emission Rate, lb/hr |  |  | 2.9937 | 2.996 | 3.3273 | 3.2305 | 3.2234 | 3.3273 | 3.0745 | 3.0696
Expected DEP CO Reduction Rate, % |  |  | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
Expected DEP CO Emission Rate, ppm |  |  | 8 | 8 | 2.5 | 2.9 | 2.3 | 2.5 | 2.8 | 2.3
Notes:
1 | Spray Intercooling (Sprint) is not currently available with DLE combustors.
2 | Auxiliary load includes fuel compression, misc. GT auxiliaries, and transformer losses
3 | Gross heat rate as a function of the HHV of the fuel plus degradation

## Perf.
UAE Lowell Power Expansion
Technology Comparison
5 - GE/S&S LM6000 Units | Yearly Revenue/Cost Variances per Unit
| DLE Combustor | Sprint w/ Water Injection | Sprint w/ Steam Injection (3)
| w/ Inlet Chilling | w/ Inlet Chilling | w/ Inlet Chilling
DLE Capital Recovery ($1.1m over 15 yr. @ 11%) (1) | 121000.0008 | 0 | 0
Chiller Cost (90 oF, electric @ $0.03/kw-hr, 2500 hrs) | 108705 | 92850 | 109387.5
Sprint Water Injection (@100 oF & $1.40/100 cu. ft.) | 0 | 1377.7575 | 1377.7575
Water Injection (@100 oF & $1.40/100 cu. ft.) | 0 | 11740.5225 | 0
Steam Injection (550 psig, 75 oF sprht, 1263 Btu/lb) | 0 | 0 | 358947.126
Major Maintenance | 264650 | 224871.0977 | 231000
Water Treatment Capital Recovery ($200,000 over 15 yr. @ 11%) | 0 | 22000.0002 | 22000.0002
Water Treatment Variable Cost ($0.0025/gal for chemical, 2500 hrs.) | 0 | 15432.4041 | 23664.5683
Fuel Cost ($3/mmBtu & 2500 hrs.) | 3047642.64 | 3278986.065 | 3122461.9125
Capacity Payment ($6/kw-mo w/ DLE Unit as datum) | 0 | -133300.8 | -220939.2
Total First Year Cost | 3541997.6408 | 3513957.0469 | 3647899.6645
Operating Hours | 2500
(1) Price differential between machines equipped with a DLE Combustor and those with the Sprint Technology is $1.1 m ($1.4 m for DLE, $0.3 for Sprint)
(2) General assumption of 2500 hrs. operating
(3) Steam injection rates of over 30,000 lbs/hr can not be handled by existing systems

## BS (hidden)
PROJECT NAME: UAE-Lowell
BALANCE SHEET
| 0 | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) | Close | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
|  | 2001-12-30 12:00 | 2002-12-30 18:00 | 2003-12-31 | 2004-12-30 06:00 | 2005-12-30 12:00 | 2006-12-30 18:00 | 2007-12-31 | 2008-12-30 06:00 | 2009-12-30 12:00 | 2010-12-30 18:00 | 2011-12-31 | 2012-12-30 06:00 | 2013-12-30 12:00 | 2014-12-30 18:00 | 2015-12-31 | 2016-12-30 06:00 | 2017-12-30 12:00 | 2018-12-30 18:00 | 2019-12-31 | 2020-12-30 06:00 | 2021-12-30 12:00 | 2022-12-30 18:00 | 2023-12-31 | 2024-12-30 06:00 | 2025-12-30 12:00 | 2026-12-30 18:00 | 2027-12-31 | 2028-12-30 06:00 | 2029-12-30 12:00 | 2030-12-30 18:00 | 2031-12-31
Assets
Cash | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accounts Receivable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inventories | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other Current Assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Debt Service Reserve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current Assets |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gross PP&E | 55000 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750 | 54750
Accumulated Depreciation | 0 | 1897.4 | 4743.5 | 7589.6 | 10435.7 | 13281.8 | 15183.9 | 16614 | 18044.1 | 19474.2 | 20904.3 | 22334.4 | 23764.5 | 25194.6 | 26624.7 | 28054.8 | 29484.9 | 30915 | 32345.1 | 33775.2 | 35205.3 | 36635.4 | 38065.5 | 39495.6 | 40925.7 | 42355.8 | 43785.9 | 45216 | 46646.1 | 48076.2 | 49506.3 | 49983
Net PP&E | 55000 | 52852.6 | 50006.5 | 47160.4 | 44314.3 | 41468.2 | 39566.1 | 38136 | 36705.9 | 35275.8 | 33845.7 | 32415.6 | 30985.5 | 29555.4 | 28125.3 | 26695.2 | 25265.1 | 23835 | 22404.9 | 20974.8 | 19544.7 | 18114.6 | 16684.5 | 15254.4 | 13824.3 | 12394.2 | 10964.1 | 9534 | 8103.9 | 6673.8 | 5243.7 | 4767
Land | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Other Assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Assets | 56000 | 53852.6 | 51006.5 | 48160.4 | 45314.3 | 42468.2 | 40566.1 | 39136 | 37705.9 | 36275.8 | 34845.7 | 33415.6 | 31985.5 | 30555.4 | 29125.3 | 27695.2 | 26265.1 | 24835 | 23404.9 | 21974.8 | 20544.7 | 19114.6 | 17684.5 | 16254.4 | 14824.3 | 13394.2 | 11964.1 | 10534 | 9103.9 | 7673.8 | 6243.7 | 5767
Liabilities
Accounts Payable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accrued Expenses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Deferred Tax Liability | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Working Capital Revolver | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Long Term Debt | 68291.6316 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Other Non-Current Liabilities | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Long-term Liabilities | 68291.6316 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Stockholders' Equity
Paid-In-Capital | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316 | -13291.6316
Retained earnings | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total stockholders' equity | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Liabilities & Equity | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Proof | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Debt
PROJECT NAME: UAE-Lowell
DEBT ISSUANCE | (This page is set up to solve for Debt Principal given DSCR, by using the Goal Seek Button)
('000 $) | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
EBITDA by Debt Fiscal Year | 2332.2049 | 5689.2287 | 5714.0118 | 5694.9269 | 5663.5971 | 5643.2413 | 5618.3506 | 5596.5845 | 5562.7023 | 5539.5167 | 5511.786 | 5487.025 | 5450.2911 | 5423.9442 | 5393.0403 | 5364.9333 | 5325.0125 | 5295.1331 | 5260.6833 | 5228.8369 | 2078.647 | -852.8001 | -1510.887 | -1551.4252 | -1589.8668 | -1632.6198 | -1675.4647 | -1720.6757 | -1763.5714 | -1811.2591 | -2325.5423 |  | 1
DSCR | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 |  | 6
Target DS | 1794.0038 | 4376.3298 | 4395.3937 | 4380.713 | 4356.6131 | 4340.9549 | 4321.8082 | 4305.065 | 4279.0018 | 4261.1667 | 4239.8354 | 4220.7884 | 4192.5316 | 4172.2647 | 4148.4926 | 4126.8717 | 4096.1634 | 4073.1793 | 4046.6794 | 4022.1822 | 1598.9592 | -656 | -1162.2208 | -1193.404 | -1222.9745 | -1255.8614 | -1288.819 | -1323.5967 | -1356.5933 | -1393.2763 | -1788.8787
Debt Principal | 2001-12-31: 68291.6316
Ending Balance at Maturity | 2001-12-31: 110712.0769
| 2001-04-01 | 2002-04-01 | 2003-04-01 | 2004-04-01 | 2005-04-01 | 2006-04-01 | 2007-04-01 | 2008-04-01 | 2009-04-01 | 2010-04-01 | 2011-04-01 | 2012-04-01 | 2013-04-01 | 2014-04-01 | 2015-04-01 | 2016-04-01 | 2017-04-01 | 2018-04-01 | 2019-04-01 | 2020-04-01 | 2021-04-01 | 2022-04-01 | 2023-04-01 | 2024-04-01 | 2025-04-01 | 2026-04-01 | 2027-04-01 | 2028-04-01 | 2029-04-01 | 2030-04-01 | 2031-04-01 | 2031-05-01
Beginning Balance |  | 68857.6856 | 70187.7611 | 71611.3823 | 73174.2978 | 74884.6902 | 76759.3648 | 78811.4326 | 81058.2332 | 83511.2203 | 86193.7004 | 89123.822 | 92325.5601 | 95814.8727 | 99624.08 | 103778.2922 | 108310.6709 | 113243.3803 | 118621.2296 | 124478.9501 | 130862.4165 | 140241.5483 | 152719.6711 | 166765.1613 | 182034.8249 | 198600.0536 | 216604.3204 | 236158.2135 | 257407.8191 | 280451.5419 | 305488.0877
Addition |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Principal Payment |  | -643.4634 | -689.6161 | -767.6374 | -827.7513 | -910.053 | -996.7449 | -1102.8682 | -1190.4352 | -1304.8166 | -1425.8314 | -1570.972 | -1696.541 | -1855.4027 | -2023.9881 | -2223.2508 | -2401.406 | -2621.9017 | -2856.3802 | -3130.661 | -4576.4516 | -6097.1147 | -6863.5374 | -7485.1368 | -8089.6213 | -8797.7384 | -9554.8584 | -10416.5963 | -11252.8128 | -12233.5694 | -13461.2986
Interest Payment |  | 1416.2988 | 1443.6565 | 1485.0557 | 1505.085 | 1540.2652 | 1578.8245 | 1634.3682 | 1667.2457 | 1717.7 | 1772.8745 | 1848.2235 | 1898.9976 | 1970.7676 | 2049.1172 | 2152.1236 | 2227.7873 | 2329.2457 | 2439.8599 | 2581.4077 | 2691.6427 | 2884.5573 | 3141.2135 | 3458.3267 | 3744.182 | 4084.9038 | 4455.2245 | 4897.3793 | 5294.491 | 5768.4656 | 6283.4296
Ending Balance |  | 69501.149 | 70877.3772 | 72379.0197 | 74002.049 | 75794.7433 | 77756.1097 | 79914.3008 | 82248.6684 | 84816.0369 | 87619.5318 | 90694.794 | 94022.101 | 97670.2754 | 101648.0681 | 106001.5431 | 110712.0769 | 115865.282 | 121477.6098 | 127609.6112 | 135438.8681 | 146338.6629 | 159583.2085 | 174250.2981 | 190124.4462 | 207397.7919 | 226159.1788 | 246574.8098 | 268660.6319 | 292685.1113 | 318949.3863
Pro-rata EBITDA |  | 2815.9281 | 2851.9906 | 2852.2808 | 2825.0662 | 2816.939 | 2804.611 | 2803.4039 | 2775.129 | 2765.5664 | 2751.8321 | 2748.9531 | 2719.4928 | 2708.3269 | 2693.0213 | 2688.2749 | 2657.4892 | 2644.5319 | 2627.4704 | 2620.6377 | 1556.5803 | -109.8421 | -748.5398 | -771.2899 | -787.1175 | -808.827 | -830.0454 | -855.4012 | -873.0839 | -897.2954 | -1861.6437
DSCR |  | 1.2869 | 1.2977 | 1.3022 | 1.2969 | 1.2978 | 1.2979 | 1.3024 | 1.2971 | 1.298 | 1.2981 | 1.3026 | 1.2973 | 1.2983 | 1.2983 | 1.3028 | 1.2976 | 1.2985 | 1.2986 | 1.3031 | 1.947 | 0.33488 | 1.2881 | 1.2926 | 1.2872 | 1.2881 | 1.2881 | 1.2925 | 1.2872 | 1.288 | 2.0814
(Debt Anniversary) | 2001-10-01 | 2002-10-01 | 2003-10-01 | 2004-10-01 | 2005-10-01 | 2006-10-01 | 2007-10-01 | 2008-10-01 | 2009-10-01 | 2010-10-01 | 2011-10-01 | 2012-10-01 | 2013-10-01 | 2014-10-01 | 2015-10-01 | 2016-10-01 | 2017-10-01 | 2018-10-01 | 2019-10-01 | 2020-10-01 | 2021-10-01 | 2022-10-01 | 2023-10-01 | 2024-10-01 | 2025-10-01 | 2026-10-01 | 2027-10-01 | 2028-10-01 | 2029-10-01 | 2030-10-01 | 2031-05-01
Beginning Balance | 68291.6316 | 69501.149 | 70877.3772 | 72379.0197 | 74002.049 | 75794.7433 | 77756.1097 | 79914.3008 | 82248.6684 | 84816.0369 | 87619.5318 | 90694.794 | 94022.101 | 97670.2754 | 101648.0681 | 106001.5431 | 110712.0769 | 115865.282 | 121477.6098 | 127609.6112 | 135438.8681 | 146338.6629 | 159583.2085 | 174250.2981 | 190124.4462 | 207397.7919 | 226159.1788 | 246574.8098 | 268660.6319 | 292685.1113 | 318949.3863
Addition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Principal Payment | -566.054 | -686.6121 | -734.0051 | -795.2781 | -882.6412 | -964.6216 | -1055.3229 | -1143.9324 | -1262.5519 | -1377.6635 | -1504.2902 | -1630.766 | -1792.7716 | -1953.8046 | -2130.2241 | -2309.1278 | -2531.3034 | -2755.9476 | -3001.3403 | -3252.8053 | -4802.6801 | -6381.0081 | -7181.9528 | -7784.5268 | -8475.6073 | -9206.5284 | -9999.0347 | -10833.0093 | -11790.9101 | -12802.9764 | -3057.1783
Interest Payment | 2360.0578 | 2874.777 | 2931.7019 | 2985.6346 | 3060.9478 | 3135.099 | 3216.227 | 3296.4649 | 3402.0528 | 3508.2469 | 3624.2079 | 3741.1603 | 3889.0375 | 4039.9369 | 4204.4704 | 4372.5637 | 4579.3852 | 4792.5372 | 5024.68 | 5263.8965 | 5602.1598 | 6053.0081 | 6600.8424 | 7187.8248 | 7864.1201 | 8578.5977 | 9354.6252 | 10171.2109 | 11112.6134 | 12106.3383 | 2162.739
Ending Balance | 68857.6856 | 70187.7611 | 71611.3823 | 73174.2978 | 74884.6902 | 76759.3648 | 78811.4326 | 81058.2332 | 83511.2203 | 86193.7004 | 89123.822 | 92325.5601 | 95814.8727 | 99624.08 | 103778.2922 | 108310.6709 | 113243.3803 | 118621.2296 | 124478.9501 | 130862.4165 | 140241.5483 | 152719.6711 | 166765.1613 | 182034.8249 | 198600.0536 | 216604.3204 | 236158.2135 | 257407.8191 | 280451.5419 | 305488.0877 | 322006.5646
Pro-rata EBITDA | 2332.2049 | 2873.3005 | 2862.0212 | 2842.6461 | 2838.5309 | 2826.3024 | 2813.7396 | 2793.1806 | 2787.5733 | 2773.9503 | 2759.9539 | 2738.0719 | 2730.7983 | 2715.6173 | 2700.019 | 2676.6584 | 2667.5233 | 2650.6012 | 2633.2129 | 2608.1992 | 522.0667 | -742.958 | -762.3473 | -780.1353 | -802.7493 | -823.7929 | -845.4193 | -865.2746 | -890.4875 | -913.9637 | -463.8986
DSCR | 1.3 | 1.3131 | 1.3023 | 1.2978 | 1.3031 | 1.3022 | 1.3021 | 1.2976 | 1.3029 | 1.302 | 1.3019 | 1.2974 | 1.3027 | 1.3017 | 1.3017 | 1.2972 | 1.3024 | 1.3015 | 1.3014 | 1.2969 | 0.65301 | 2.2651 | 1.3119 | 1.3074 | 1.3128 | 1.3119 | 1.3119 | 1.3075 | 1.3128 | 1.312 | 0.51865
| 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
Beginning Balance | 68857.6856 | 70187.7611 | 71611.3823 | 73174.2978 | 74884.6902 | 76759.3648 | 78811.4326 | 81058.2332 | 83511.2203 | 86193.7004 | 89123.822 | 92325.5601 | 95814.8727 | 99624.08 | 103778.2922 | 108310.6709 | 113243.3803 | 118621.2296 | 124478.9501 | 130862.4165 | 140241.5483 | 152719.6711 | 166765.1613 | 182034.8249 | 198600.0536 | 216604.3204 | 236158.2135 | 257407.8191 | 280451.5419 | 305488.0877 | 322006.5646
Addition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest Payment | 1415.3294 | 1443.6565 | 1472.9382 | 1500.9728 | 1540.2652 | 1578.8245 | 1621.0324 | 1662.6904 | 1717.7 | 1772.8745 | 1833.1427 | 1893.8091 | 1970.7676 | 2049.1172 | 2134.5631 | 2221.7004 | 2329.2457 | 2439.8599 | 2560.3444 | 2684.2885 | 2884.5573 | 3141.2135 | 3430.1081 | 3733.952 | 4084.9038 | 4455.2245 | 4857.4186 | 5280.0251 | 5768.4656 | 6283.4296 | 17758.8826
Ending Balance | 68857.6856 | 70187.7611 | 71611.3823 | 73174.2978 | 74884.6902 | 76759.3648 | 78811.4326 | 81058.2332 | 83511.2203 | 86193.7004 | 89123.822 | 92325.5601 | 95814.8727 | 99624.08 | 103778.2922 | 108310.6709 | 113243.3803 | 118621.2296 | 124478.9501 | 130862.4165 | 140241.5483 | 152719.6711 | 166765.1613 | 182034.8249 | 198600.0536 | 216604.3204 | 236158.2135 | 257407.8191 | 280451.5419 | 305488.0877 | 322006.5646
Debt Service
Principal Payments | -566.054 | -1330.0755 | -1423.6212 | -1562.9155 | -1710.3925 | -1874.6746 | -2052.0678 | -2246.8006 | -2452.9871 | -2682.4801 | -2930.1216 | -3201.7381 | -3489.3126 | -3809.2073 | -4154.2123 | -4532.3786 | -4932.7094 | -5377.8493 | -5857.7205 | -6383.4664 | -9379.1318 | -12478.1228 | -14045.4902 | -15269.6636 | -16565.2287 | -18004.2668 | -19553.8932 | -21249.6056 | -23043.7228 | -25036.5458 | -16518.4769
Interest Expense | 2360.0578 | 5706.4052 | 5819.0149 | 5943.6285 | 6067.0056 | 6215.6295 | 6373.876 | 6551.8656 | 6731.9889 | 6943.6468 | 7169.957 | 7422.5265 | 7681.8442 | 7981.472 | 8302.7048 | 8659.2503 | 9028.8729 | 9451.0286 | 9904.3999 | 10405.6486 | 10978.091 | 11822.1228 | 12883.2695 | 14076.2596 | 15342.2542 | 16748.4054 | 18265.0742 | 19926.0088 | 21687.1295 | 23643.2695 | 14729.5983
Net Debt Service | 1794.0038 | 4376.3298 | 4395.3937 | 4380.713 | 4356.6131 | 4340.9549 | 4321.8082 | 4305.065 | 4279.0018 | 4261.1667 | 4239.8354 | 4220.7884 | 4192.5316 | 4172.2647 | 4148.4926 | 4126.8717 | 4096.1634 | 4073.1793 | 4046.6794 | 4022.1822 | 1598.9592 | -656 | -1162.2208 | -1193.404 | -1222.9745 | -1255.8614 | -1288.819 | -1323.5967 | -1356.5933 | -1393.2763 | -1788.8787
ACTUAL DSCR | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Accrued Debt Service
Principal Payments | -566.054 | -1330.0755 | -1423.6212 | -1562.9155 | -1710.3925 | -1874.6746 | -2052.0678 | -2246.8006 | -2452.9871 | -2682.4801 | -2930.1216 | -3201.7381 | -3489.3126 | -3809.2073 | -4154.2123 | -4532.3786 | -4932.7094 | -5377.8493 | -5857.7205 | -6383.4664 | -9379.1318 | -12478.1228 | -14045.4902 | -15269.6636 | -16565.2287 | -18004.2668 | -19553.8932 | -21249.6056 | -23043.7228 | -25036.5458 | -16518.4769
Interest Expense | 3775.3873 | 5734.7323 | 5848.2966 | 5971.6631 | 6106.298 | 6254.1887 | 6416.0839 | 6593.5235 | 6786.9985 | 6998.8214 | 7230.2252 | 7483.1929 | 7758.8027 | 8059.8217 | 8388.1507 | 8746.3877 | 9136.4181 | 9561.6429 | 10024.8844 | 10529.5927 | 11178.3598 | 12078.779 | 13172.164 | 14380.1035 | 15693.206 | 17118.726 | 18667.2683 | 20348.6154 | 22175.57 | 24158.2335 | 26205.0512
Net Debt Service | 3209.3332 | 4404.6568 | 4424.6755 | 4408.7476 | 4395.9056 | 4379.5141 | 4364.0161 | 4346.723 | 4334.0114 | 4316.3413 | 4300.1036 | 4281.4548 | 4269.49 | 4250.6144 | 4233.9385 | 4214.0091 | 4203.7087 | 4183.7936 | 4167.1639 | 4146.1263 | 1799.228 | -399.3439 | -873.3262 | -889.56 | -872.0227 | -885.5408 | -886.6249 | -900.9902 | -868.1529 | -878.3122 | 9686.5743
Debt Summary
| Treasury (%) |  |  | 6.5%
| Spread (%) |  |  | 1.75%
| All In Coupon Rate (%) |  |  | 8.25%
| Term (years) |  |  | 20
| Average Life (years) |  |  | -83.9509
| Total amount ($ '000) |  |  | 68291.6316
| DSCR |  | Average | 1.3
|  |  | Minimum | 1.3
Time Factor | 0 | 0.99932 | 1.9986 | 3.0007 | 4 | 4.9993 | 5.9986 | 7.0007 | 8 | 8.9993 | 9.9986 | 11.0007 | 12 | 12.9993 | 13.9986 | 15.0007 | 16 | 16.9993 | 17.9986 | 19.0007 | 20 | 20.9993 | 21.9986 | 23.0007 | 24 | 24.9993 | 25.9986 | 27.0007 | 28 | 28.9993 | 29.5797
| 0.49829 | 1.4976 | 2.4997 | 3.499 | 4.4983 | 5.4976 | 6.4997 | 7.499 | 8.4983 | 9.4976 | 10.4997 | 11.499 | 12.4983 | 13.4976 | 14.4997 | 15.499 | 16.4983 | 17.4976 | 18.4997 | 19.499 | 20.4983 | 21.4976 | 22.4997 | 23.499 | 24.4983 | 25.4976 | 26.4997 | 27.499 | 28.4983 | 29.4976 | 29.5797
Average Life | 2001-12-31: -83.9509
Goal Seek Debt

## Depreciation
PROJECT NAME: UAE-Lowell
DEPRECIATION SCHEDULE
|  |  | 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) |  |  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
|  |  | 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
US FEDERAL TAX DEPRECIATION & AMORTIZATION
Years
Plant & Equipment - MACRS | 15 |  | 5% | 9.5% | 8.55% | 7.7% | 6.93% | 6.23% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 2.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Start-Up Costs - SL | 5 |  | 13.33% | 20% | 20% | 20% | 20% | 6.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Transaction Costs - SL | 20 |  | 3.333% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 1.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Plant & Equipment - MACRS | 47670 |  | 2383.5 | 4528.65 | 4075.785 | 3670.59 | 3303.531 | 2969.841 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 1406.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start-Up Costs - SL | 7080 |  | 944 | 1416 | 1416 | 1416 | 1416 | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transaction Costs - SL | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Beginning Book Value | 54750 |  | 3327.5 | 5944.65 | 5491.785 | 5086.59 | 4719.531 | 3441.841 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 1406.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending Value of Assets | 54750 |  | 51422.5 | 45477.85 | 39986.065 | 34899.475 | 30179.944 | 26738.103 | 23925.573 | 21108.276 | 18295.746 | 15478.449 | 12665.919 | 9848.622 | 7036.092 | 4218.795 | 1406.265 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12
STATE TAX DEPRECIATION & AMORTIZATION
Years
Plant & Equipment - MACRS | 15 |  | 5% | 9.5% | 8.55% | 7.7% | 6.93% | 6.23% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 2.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Start-Up Costs - SL | 5 |  | 13.33% | 20% | 20% | 20% | 20% | 6.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Transaction Costs - SL | 20 |  | 3.333% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 1.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Plant & Equipment - MACRS | 47670 |  | 2383.5 | 4528.65 | 4075.785 | 3670.59 | 3303.531 | 2969.841 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 1406.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start-Up Costs - SL | 7080 |  | 944 | 1416 | 1416 | 1416 | 1416 | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transaction Costs - SL | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Beginning Book Value | 54750 |  | 3327.5 | 5944.65 | 5491.785 | 5086.59 | 4719.531 | 3441.841 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 2817.297 | 2812.53 | 1406.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending Value of Assets | 54750 |  | 51422.5 | 45477.85 | 39986.065 | 34899.475 | 30179.944 | 26738.103 | 23925.573 | 21108.276 | 18295.746 | 15478.449 | 12665.919 | 9848.622 | 7036.092 | 4218.795 | 1406.265 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12 | 9.5497e-12
BOOK DEPRECIATION & AMORTIZATION
| Years | Residual
Plant & Equipment - SL | 30 | 10% | 2% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 1%
Start-Up Costs - SL | 5 |  | 13.33% | 20% | 20% | 20% | 20% | 6.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Transaction Costs - SL | 20 |  | 3.333% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 1.667% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Plant & Equipment - MACRS | 47670 |  | 953.4 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 476.7
Start-Up Costs - SL | 7080 |  | 944 | 1416 | 1416 | 1416 | 1416 | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transaction Costs - SL | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Beginning Book Value | 54750 |  | 1897.4 | 2846.1 | 2846.1 | 2846.1 | 2846.1 | 1902.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 476.7
Ending Book Value of Assets | 54750 |  | 52852.6 | 50006.5 | 47160.4 | 44314.3 | 41468.2 | 39566.1 | 38136 | 36705.9 | 35275.8 | 33845.7 | 32415.6 | 30985.5 | 29555.4 | 28125.3 | 26695.2 | 25265.1 | 23835 | 22404.9 | 20974.8 | 19544.7 | 18114.6 | 16684.5 | 15254.4 | 13824.3 | 12394.2 | 10964.1 | 9534 | 8103.9 | 6673.8 | 5243.7 | 4767

## Taxes
PROJECT NAME: UAE-Lowell
TAXES
| 0.66667 | 1.6667 | 2.6667 | 3.6667 | 4.6667 | 5.6667 | 6.6667 | 7.6667 | 8.6667 | 9.6667 | 10.6667 | 11.6667 | 12.6667 | 13.6667 | 14.6667 | 15.6667 | 16.6667 | 17.6667 | 18.6667 | 19.6667 | 20.6667 | 21.6667 | 22.6667 | 23.6667 | 24.6667 | 25.6667 | 26.6667 | 27.6667 | 28.6667 | 29.6667 | 30.6667
('000 $) | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| 2001-12-31 | 2002-12-31 | 2003-12-31 | 2004-12-31 | 2005-12-31 | 2006-12-31 | 2007-12-31 | 2008-12-31 | 2009-12-31 | 2010-12-31 | 2011-12-31 | 2012-12-31 | 2013-12-31 | 2014-12-31 | 2015-12-31 | 2016-12-31 | 2017-12-31 | 2018-12-31 | 2019-12-31 | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-12-31 | 2026-12-31 | 2027-12-31 | 2028-12-31 | 2029-12-31 | 2030-12-31 | 2031-12-31
STATE TAXES
Adjusted Pretax Book Income | -1953.4539 | -2849.9323 | -2985.9936 | -3132.4708 | -3290.8474 | -2519.1282 | -2234.0804 | -2437.2624 | -2657.1844 | -2896.179 | -3155.4992 | -3437.1492 | -3742.2285 | -4073.5266 | -4432.9669 | -4823.1709 | -5246.0483 | -5705.0246 | -6202.9478 | -6743.2943 | -11567.1793 | -14990.735 | -16122.7927 | -17370.4742 | -18724.418 | -20191.9101 | -21783.5871 | -23509.2645 | -25381.7789 | -27411.2667 | -28552.8088
Plus Book Depreciation & Amortization | 1897.4 | 2846.1 | 2846.1 | 2846.1 | 2846.1 | 1902.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 1430.1 | 476.7
Less State Tax Depreciation | -3327.5 | -5944.65 | -5491.785 | -5086.59 | -4719.531 | -3441.841 | -2812.53 | -2817.297 | -2812.53 | -2817.297 | -2812.53 | -2817.297 | -2812.53 | -2817.297 | -2812.53 | -1406.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
State Taxable Income | -3383.5539 | -5948.4823 | -5631.6786 | -5372.9608 | -5164.2784 | -4058.8692 | -3616.5104 | -3824.4594 | -4039.6144 | -4283.376 | -4537.9292 | -4824.3462 | -5124.6585 | -5460.7236 | -5815.3969 | -4799.3359 | -3815.9483 | -4274.9246 | -4772.8478 | -5313.1943 | -10137.0793 | -13560.635 | -14692.6927 | -15940.3742 | -17294.318 | -18761.8101 | -20353.4871 | -22079.1645 | -23951.6789 | -25981.1667 | -28076.1088
State Income Tax Rate | bar: 2001-12-31 to 2031-12-31
Current State Income Tax Expense (Benefit) | -236.8488 | -416.3938 | -394.2175 | -376.1073 | -361.4995 | -284.1208 | -253.1557 | -267.7122 | -282.773 | -299.8363 | -317.655 | -337.7042 | -358.7261 | -382.2506 | -407.0778 | -335.9535 | -267.1164 | -299.2447 | -334.0993 | -371.9236 | -709.5955 | -949.2444 | -1028.4885 | -1115.8262 | -1210.6023 | -1313.3267 | -1424.7441 | -1545.5415 | -1676.6175 | -1818.6817 | -1965.3276
Beginning NOL's | 0 | 236.8488 | 653.2425 | 1047.46 | 1423.5673 | 1785.0668 | 2069.1876 | 2322.3433 | 2590.0555 | 2635.9797 | 2756.2711 | 3073.9261 | 3411.6303 | 3770.3564 | 4152.6071 | 4559.6849 | 4895.6384 | 5162.7548 | 0 | 136.7356 | 488.61 | 1177.1837 | 2102.9036 | 3106.565 | 4222.3912 | 5432.9934 | 6746.3201 | 8123.7513 | 9434.1049 | 10753.0013 | 12311.0122
New NOL's | 236.8488 | 416.3938 | 394.2175 | 376.1073 | 361.4995 | 284.1208 | 253.1557 | 267.7122 | 282.773 | 299.8363 | 317.655 | 337.7042 | 358.7261 | 382.2506 | 407.0778 | 335.9535 | 267.1164 | 299.2447 | 334.0993 | 371.9236 | 709.5955 | 949.2444 | 1028.4885 | 1115.8262 | 1210.6023 | 1313.3267 | 1424.7441 | 1545.5415 | 1676.6175 | 1818.6817 | 1965.3276
Expired NOLs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -236.8488 | -179.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -120.2913 | -197.3637 | -20.0492 | -21.0219 | -23.5246 | -24.8271 | 0 | 0 | 0 | -47.3129 | -235.188 | -357.7211 | -260.6708 | -102.7686
NOL Utilization (8 years) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending NOL's | 236.8488 | 653.2425 | 1047.46 | 1423.5673 | 1785.0668 | 2069.1876 | 2322.3433 | 2590.0555 | 2635.9797 | 2756.2711 | 3073.9261 | 3411.6303 | 3770.3564 | 4152.6071 | 4559.6849 | 4895.6384 | 5162.7548 | 5341.7082 | 136.7356 | 488.61 | 1177.1837 | 2102.9036 | 3106.565 | 4222.3912 | 5432.9934 | 6746.3201 | 8123.7513 | 9434.1049 | 10753.0013 | 12311.0122 | 14173.5712
TOTAL STATE TAXES UTILIZING NOLs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FEDERAL TAXES
State Taxable Income | -3383.5539 | -5948.4823 | -5631.6786 | -5372.9608 | -5164.2784 | -4058.8692 | -3616.5104 | -3824.4594 | -4039.6144 | -4283.376 | -4537.9292 | -4824.3462 | -5124.6585 | -5460.7236 | -5815.3969 | -4799.3359 | -3815.9483 | -4274.9246 | -4772.8478 | -5313.1943 | -10137.0793 | -13560.635 | -14692.6927 | -15940.3742 | -17294.318 | -18761.8101 | -20353.4871 | -22079.1645 | -23951.6789 | -25981.1667 | -28076.1088
Less: State Taxes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Federal Taxable Income | -3383.5539 | -5948.4823 | -5631.6786 | -5372.9608 | -5164.2784 | -4058.8692 | -3616.5104 | -3824.4594 | -4039.6144 | -4283.376 | -4537.9292 | -4824.3462 | -5124.6585 | -5460.7236 | -5815.3969 | -4799.3359 | -3815.9483 | -4274.9246 | -4772.8478 | -5313.1943 | -10137.0793 | -13560.635 | -14692.6927 | -15940.3742 | -17294.318 | -18761.8101 | -20353.4871 | -22079.1645 | -23951.6789 | -25981.1667 | -28076.1088
Federal Tax Rate | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35%
Federal Tax Expense/ (Benefit) | -1184.2439 | -2081.9688 | -1971.0875 | -1880.5363 | -1807.4974 | -1420.6042 | -1265.7786 | -1338.5608 | -1413.8651 | -1499.1816 | -1588.2752 | -1688.5212 | -1793.6305 | -1911.2532 | -2035.3889 | -1679.7676 | -1335.5819 | -1496.2236 | -1670.4967 | -1859.618 | -3547.9777 | -4746.2222 | -5142.4425 | -5579.131 | -6053.0113 | -6566.6335 | -7123.7205 | -7727.7076 | -8383.0876 | -9093.4083 | -9826.6381
Beginning NOL's | 0 | 1184.2439 | 3266.2127 | 5237.3002 | 7117.8365 | 8925.3339 | 10345.9381 | 11611.7167 | 12950.2775 | 14364.1426 | 15863.3242 | 17451.5994 | 19140.1205 | 20933.751 | 22845.0042 | 24880.3931 | 25375.9169 | 25813.7738 | 0 | 1670.4967 | 3530.1147 | 7078.0925 | 11824.3147 | 16966.7572 | 22545.8881 | 28598.8994 | 35165.533 | 42289.2535 | 50016.961 | 58400.0487 | 67493.457
New NOL's | 1184.2439 | 2081.9688 | 1971.0875 | 1880.5363 | 1807.4974 | 1420.6042 | 1265.7786 | 1338.5608 | 1413.8651 | 1499.1816 | 1588.2752 | 1688.5212 | 1793.6305 | 1911.2532 | 2035.3889 | 1679.7676 | 1335.5819 | 1496.2236 | 1670.4967 | 1859.618 | 3547.9777 | 4746.2222 | 5142.4425 | 5579.131 | 6053.0113 | 6566.6335 | 7123.7205 | 7727.7076 | 8383.0876 | 9093.4083 | 9826.6381
Expired NOLs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1184.2439 | -897.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NOL Utilization (15 years) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ending NOL's | 1184.2439 | 3266.2127 | 5237.3002 | 7117.8365 | 8925.3339 | 10345.9381 | 11611.7167 | 12950.2775 | 14364.1426 | 15863.3242 | 17451.5994 | 19140.1205 | 20933.751 | 22845.0042 | 24880.3931 | 25375.9169 | 25813.7738 | 27309.9974 | 1670.4967 | 3530.1147 | 7078.0925 | 11824.3147 | 16966.7572 | 22545.8881 | 28598.8994 | 35165.533 | 42289.2535 | 50016.961 | 58400.0487 | 67493.457 | 77320.0951
TOTAL STATE TAXES UTILIZING NOLs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## IDC
PROJECT NAME: UAE-Lowell
IDC CALCULATIONS
Total Construction & Other Costs (000$): |  | 6000
No. of Construction Months: |  | 7
Interest During Construction: |  | 8.25% | 0.02292%
|  | Annual | Daily (360-Day)
|  |  | Turbine Cost | Construction &
IDC Calculations |  |  | including Carry | Other Cost | Principal | Balance | Interest | Cum. Interest
Month | Date | % Drawn | (000$) | (000$) | (000$) | (000$) | (000$) | (000$)
1 | 2000-04-01 | 17% | 28520.8992 | 1020 | 29540.8992 | 29540.8992 | 0 | 0
2 | 2000-05-01 | 16% | 0 | 960 | 960 | 30703.9929 | 203.0937 | 203.0937
3 | 2000-06-01 | 16% | 0 | 960 | 960 | 31882.1192 | 218.1263 | 421.22
4 | 2000-07-01 | 16% | 0 | 960 | 960 | 33061.3087 | 219.1896 | 640.4095
5 | 2000-08-01 | 17% | 0 | 1020 | 1020 | 34316.1818 | 234.873 | 875.2826
6 | 2000-09-01 | 18% | 0 | 1080 | 1080 | 35639.9697 | 243.7879 | 1119.0705
7 | 2000-10-01 | 0% | 0 | 0 | 0 | 35884.9945 | 245.0248 | 1364.0952
8 | 2000-11-01 | 0% | 0 | 0 | 0 | 36139.9274 | 254.933 | 1619.0282
9 | 2000-12-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
10 | 2001-01-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
11 | 2001-02-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
12 | 2001-03-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
13 | 2001-04-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
14 | 2001-05-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
15 | 2001-06-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
16 | 2001-07-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
17 | 2001-08-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
18 | 2001-09-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
19 | 2001-10-01 | 0% | 0 | 0 | 0 | 36139.9274 | 0 | 1619.0282
|  | 100% | 28520.8992 | 6000 | 34520.8992 |  | 1619.0282
TURBINE DELIVERY SCHEDULE
*Rough Estimate by Bruce Golden. Please double-check for deal specific
[6 empty] | Turbine No. | 1 | 2 | 3 | 4 | 5 | 6
Unit | Turbines | Delivery | LD'S |  | Month | No. of Months | 5.5 | 6 | 6.5 | 7 | 7.5 | 8
Number | Delivered | Schedule | Enforced On |  | 1 |  | 17% | 17% | 17% | 17% | 17% | 17%
1-3 | 3 | 2000-07-30 | 2000-10-30 |  | 2 |  | 16% | 16% | 16% | 12% | 12% | 12%
4-6 | 3 | 2000-08-30 | 2000-10-30 |  | 3 |  | 16% | 16% | 13% | 12% | 12% | 12%
7-8 | 2 | 2000-09-30 | 2000-10-30 |  | 4 |  | 16% | 16% | 16% | 14% | 14% | 14%
9-11 | 3 | 2000-10-30 | 2000-10-30 |  | 5 |  | 17% | 17% | 16% | 18% | 13% | 13%
12-13 | 2 | 2000-11-30 | 2000-11-30 |  | 6 |  | 18% | 18% | 12% | 12% | 12% | 12%
14-15 | 2 | 2000-12-30 | 2000-12-30 |  | 7 |  | 0% | 0% | 10% | 15% | 10% | 10%
16-18 | 3 | 2000-01-30 | 2000-01-30 |  | 8 |  | 0% | 0% | 0% | 0% | 10% | 10%
19-20 | 2 | 2001-02-28 | 2001-02-28 |  | 9 | bar: 1 to 6
21-22 | 2 | 2001-03-30 | 2001-03-30 |  | 10 | bar: 1 to 6
23-24 | 2 | 2001-04-30 | 2001-04-30 |  | 11 | bar: 1 to 6
12 | bar: 1 to 6
13 | bar: 1 to 6
Summary (000$): |  |  |  |  | 14 | bar: 1 to 6
Basis Per Turbine |  |  | 13950 |  | 15 | bar: 1 to 6
Carry Cost Per Turbine |  |  | 289.6163 |  | Sum |  | 100% | 100% | 100% | 100% | 100% | 100%
WestLB Structuring, Restructuring & Legal Fees |  |  | 20.8333
Total Price |  |  | 14260.4496