## Table of Contents
St Peter, Illinois (Ameren) Power Project, Rev 0
Operations & Maintenance Cost Estimate
Table of Contents
Table of Contents |  | 1
Scope
| Project Scope Description | 2
| List of Assumptions | 3
| Map (not included) | 4
Summary - Operations & Maintenance Cost Estimate |  | 4
| Comparison vs. Other Plants | 6
O&M Staff Organization Chart |  | 7
O&M Pre-Mobilization / Mobilization Cost Estimate |  | 5
| O&M Staff Mobilization Schedule | 7
| O&M Staff Mobilization Plan | 6
| Training Program | 7
| Assumed Turnkey/Operator/Owner Scope Split | 8
| Pre-Mob / Mobilization Drawdown Schedule | 14
| Owners' Engineer | 16
| Pre-Mob / Mobilization Estimate Backup/Detail (Proprietary) | 10
Commercial Operations O&M Estimate |  | 15
| Staffing Plan | 16
| Contract & Opns Support Staffing Plan | 24
| Commercial Office Cost Estimate & Staffing Plan | 25
| Foreign vs. Local Costs | 26
| Personnel Benefits (Confidential) | 17
| O&M Estimate Backup/Detail (Proprietary) | 18
| Chemical Cost Estimate Backup | 23
Major Maintenance Cost Estimate
| Initial Operating Spares | 35
| GT Scheduled Major Maint. Program (20 Year term) | 25

## Scope
St Peter, Illinois (Ameren) Power Project, Rev 0
Project Scope Description
Scope of Work: | Full Operations and Maintenance services during the Operating Period
for one gas-fired LM6000 simple cycle peaking facility
Location: | St Peter, Illinois
approx 70 miles East of St Louis
Ownership: | Ameren to fully own and operate
Capacity: | 93.4 | MW
Equipment: | 2 | GE LM6000 PC SPRINT Gas Turbine packages with standard combustor (non-DLE)
SPRINT water injection assumed at a rate of 7.5 gpm
Water injection for NOX control assumed at a rate of 44 gpm
Water source:
Ground water for supply to reverse osmosis/demin process
Ground water for cooling tower makeup
| Demin system: Reverse Osmosis and mixed bed equipment |  |  |  |  | Installed
(1) induced draft Cooling Tower with circ. water pumps
| Chillers with condenser and chilled water pumps: |  |  |  | Yes
Distributed Control System provided at site
No Remote monitoring or control
| 0 | Selective Catalytic Reduction units
Continuous Emissions Monitoring units
| Gas compressors?: |  | Yes
No gas or electric distribution
Facilities: | Administrative Office space
Central control room and small lab area
Maintenance shop with bay
Warehouse
Sanitary facilities, to include lockers & showers
Fuel: | Primary: | Pipeline Quality Natural Gas
Backup: None
Operations Mode: | Fired Hours per year: |  | 1600
May - September dispatch season
No Winter season dispatch anticipated
PPA: | TBD
Average of 3 and 20 year terms modeled
Schedule: | Notice To Proceed: |  |  | 2000-09-01
| Commercial Operations Date: |  |  | 2001-06-01
Commercial Office: | Costs not included
Other Facilities: | Barge dock on river for fuel deliveries.
Owners Engineer: | Costs not included

## Assumptions
St Peter, Illinois (Ameren) Power Project, Rev 0
List of O&M Assumptions
1) Base year for all costs and prices herein: current 2000 US $ (no escalation or inflation included).
2) O&M personnel salaries and benefits per Enron experience at Wilton Center, no assumed union labor force in the project area.
3) Primary fuel to be Pipline Quality Natural Gas below required operating pressures, with no backup fuel.
4) Water injection for Nox control at an assumed rate of 44 gpm; SPRINT at 7.5 gpm.
5) Plant to be considered available year round with the exception of scheduled maintenance outages (Mar-April;Oct-Nov).
6) Gas turbine run hours/year: |  | 1600
7) Gas turbine starts/year: assumed to be less than 150 per year with the above indicated dispatch schedule.
7A) Type of combustion system to be Standard, non-DLE combustor, with water injection.
8) Assume any major schedule maintenance will be performed during off-peak season.
9) Gas turbine major scheduled maintenance pricing per GE Pricing catalog (George Graham e-mail dated 3/00).
10) Major scheduled maintenance intervals per OEM (GE): Hot Gas Path - 25,000 hrs; Major - 50,000 hours.
11) Water Source: Ground water. TDS is assumed to be 1000 ppm. Owner/Originator to provide sample analysis when available.
12) Water treatment chemicals costs per inhouse estimating model and performance dept tabulations (no Water Balance available).
13) Chemical costs and 25% of annual maintnenace are assumed variable with dispatch; all other costs are fixed.
14) Variable costs are based on an annual plant capacity factor of: |  |  | 18.26%
15) EPC Contract assumed to provide an allowance for GT, MK VI, DCS, BOP familiarization and operations training to O&M staff.
16) Spare Parts estimate per GE recommended spares for stand alone domestic project, with some assumed adjustments.
17) O&M Staffing plan assumes a seasonal requirement for seven people during the peak season and a "core" staff of four people during the off season. Dispatch is anticipated for 5 summer and shoulder months out of the 12 months. No winter dispatch is anticipated.
18) Assumed Scope Split between Turnkey/Startup Contractor and Owner/Operator per enclosed.
19) Turnkey Contractor: Assumed to be Ameren.
20) Owners Engineer: Owner's responsibility (estimate not included).
21) Sustaining capital expenses intended to cover only replacement of initial procurement items at end of their useful life.
22) Necessary Admin staff and support are provided by Operator from existing home office resources and other sites.
23) Along with O&M Services, Owner to provide Commercial Office function.
Revenue and Property Book Accounting including customer and fuel supplier billing
Tax Accounting including preparing Local and US tax returns
Annual financial audits by outside auditors.
Maintaining Bank accounts and treasury functions
Commercial contracts and interface with Power Purchasers and Fuel Suppliers
Fuel purchasing & supply, logistics and scheduling
Government and Public Relations
Legal and contractual requirements
Project Human resources (compensation and benefits plans)
Interface with Lenders and Partners regarding funding and information requests
Budgeting, Operating and Capital planning (Operator to provide plans per contract)
24) This O&M Estimate does not include the cost of the following items:
Fuel
Water rights and water usage costs
Purchased (backfeed) power and other purchased utilities
Owner's Insurance
Buildings: Administration, Warehouse and Shop facilities
Operating or Environmental Permits
Communications facilities (internal & external)
Taxes
Escalation
Emissions fees, discharge fees or waste water charges
Security (At Owner's discretion)
Lease Engine Membership fees (At Owner's discretion)
25) | No SCR units are assumed for this project.
26) GT Major Maintenance Program cost per fired hour for the 20 year term is estimated to be: |  |  |  | 44.1562
| NOTE: A GT Major Maintenance Program accrual figure in cost per fired hour would need to be: |  |  |  | 56.52
27) Cooling Tower chemicals cost estimate assumes 3 cycles, 17,000 gpm flow rate and 10 deg F range. No water balance available for project
28) Estimate makes standard assumptions for labor practices (i.e. O/T after 40hrs/wk). Local labor practices may differ.
30) GT Major Maintenance not accrued for in the estimate.

## Map (hidden)
St Peter, Illinois (Ameren) Power Project, Rev 0
Map

## Summary
St Peter, Illinois (Ameren) Power Project, Rev 0
Summary - Operations & Maintenance Cost Estimate
(US $)
Expenses before Commercial Operation:
|  | US $ |  | $/kW
O&M Pre-Mobilization / Mobilization Expenses
| Pre-Mobilization Expenses | 19744.2671
| Mobilization Payroll and Burden | 148618.7825
| Mobilization Operating Expenses | 242695.6634
| Mobilization Procurement Expenses | 224790.25
| Total O&M Pre-Mobilization / Mobilization Expenses | 635848.963 |  | 6.8078
| Housing Colony Mobilization Expenses | NA
| Commercial Office Mobilization Expenses | NA
| Owners' Engineer Expenses | NA
| Initial Operating Spares | 913275 |  | 9.7781
| O&M Mobilization Period Fee | 125000 |  | 1.3383
Operator Overhead Charge (G&A)
| TOTAL | 1674123.963 |  | 17.9242
Expenses during Commercial Operation:
|  |  |  | 3 YEAR | 20 YEAR | 3 YEAR |  | 20 YEAR
|  | Year 1 | Years 2+ | AVERAGE | AVERAGE | FOM ($/kW-yr) | VOM ($/mWh) | FOM ($/kW-yr) | VOM ($/mWh)
O&M Expenses
| Payroll and Burden | 519842.8862 | 519842.8862 | 519842.8862 | 519842.8862 | 5.5658 |  | 5.5658
| Administration & Operations Expenses | 213069.6447 | 197819.6447 | 202902.978 | 198582.1447 | 2.1724 |  | 2.1261
| Water | 0 | 0 | 0 | 0 |  | 0 |  | 0
| Chemicals | 29716.6 | 29716.6 | 29716.6 | 29716.6 |  | 0.19885 |  | 0.19885
| Waste Water Costs | 0 | 0 | 0 | 0 |  | 0 |  | 0
| Maintenance Expenses (excl. GT Scheduled Maint. Program) | 193748.3349 | 337885.5877 | 289839.8367 | 330678.7251 | 2.3274 | 0.48488 | 2.6553 | 0.5532
| Sustaining Capital Expenses | 22479.025 | 22479.025 | 22479.025 | 22479.025 | 0.24067 |  | 0.24067
| Contingency | 0 | 0 | 0 | 0 | 0 |  | 0
| Total O&M Expenses (ex GT Scheduled Maint.) | 978856.4907 | 1107743.7436 | 1064781.3259 | 1101299.3809 | 10.3063 | 0.68373 | 10.5879 | 0.75205
O&M Annual Operating Fee |  | 175000 | 175000 | 175000 | 175000 | 1.8737 |  | 0.625
GT Scheduled Major Maintenance ($/fired hour for 20 Yr term) |  |  |  |  | 44.1562
SCR Catalyst Replacement Accrual ($/fired hour) |  |  |  |  | 0
GT Lease Program Annual Membership (1 unit) |  | 0 | 0 | 0 | 0
Housing Colony Operating Expenses |  | NA | NA
Commercial Office Expenses |  | NA | NA | NA | NA
Operator Overhead Charge (G&A) |  | #REF! | #REF! | #REF! | #REF!

## Mob_Estimate
St Peter, Illinois (Ameren) Power Project, Rev 0
O&M Pre-Mobilization / Mobilization Cost Estimate
US $
O&M Pre-Mobilization Expenses |  | 19744.2671
Mobilization Payroll & Burden |  | 148618.7825
Mobilization Operating Expenses
| Employee Expenses | 12200
| Recruiting Expenses | 14500
| Relocation Expenses | 27456
| Outside Services | 49240
| Other Supplies & Expenses | 8635.7143
| Communications | 4780
| Temporary Offices/Facilities | 4800
| Training | 41732
| Manuals & Procedures | 61550
| Permits | 0
| Operator's Insurance | 2551.9491
| Operations Support Personnel | 15250
| Total Mobilization Operating Expenses | 242695.6634
Mobilization Procurement Expenses
| Office Furnishings & Equipment | 85522.5
| Safety & Environmental Equipment | 21420
| Vehicles & Mobile Equipment | 12160
| Warehouse Furnishings & Equipment | 12075
| Laboratory Equipment | 6300
| Shop Tools & Equipment | 76812.75
| Chemicals, Lubricants, Hydraulic Fluids | 10500
| Total Mobilization Procurement Expenses | 224790.25
Total O&M Pre-Mobilization / Mobilization Expenses |  | 635848.963
Housing Colony Mobilization Expenses |  | NA
Commercial Office Mobilization Expenses |  | NA
Owners' Engineer Expenses |  | NA
Initial Operating Spares |  | 913275
O&M Mobilization Period Fee |  | 125000
Operator Overhead Charge (G&A) |  | 0

## Mob_Schedule (hidden)
St Peter, Illinois (Ameren) Power Project, Rev 0
Staff Mobilization Schedule
MOB. MONTHS | 6 | 5 | 4 | 3 | 2 | 1 | COD
SCHEDULE | Recruiting/Procedures/Setup------------------------------------------------------------------------------------------> |  |  | Training/Early Commissioning----------------------------------------------> |  | Commissioning/Startup--------->
PLANT MANAGER
CLERK
O&M SUPERVISOR
O&M TECHNICIAN III
SEASONAL O&M TECHNICIAN II
FACILITY NEEDS
ADMINISTRATION FACILITIES
OFFICE EQUIPMENT
WAREHOUSE/SHOP
VEHICLES
TRAINING FACILITIES
TOOLS AND O&M EQUIPMENT

## Mob_Staffing
St Peter, Illinois (Ameren) Power Project, Rev 0
O&M Staff Mobilization Plan
|  | Staff | Number | Salary & | Total Salary
| No. | Area | of | Benefits | & Benefits
| Personnel | A,O or M | Months | US$/Month | US $
PLANT MANAGER | 1 | A | 6 | 9744.2671 | 58465.6025
MAINTENANCE MANAGER | 0 | M | 0 |  | 0
PURCHASING / WAREHOUSE | 0 | A | 0 |  | 0
CLERK | 1 | A | 5 | 3386.7569 | 16933.7844
O&M SUPERVISOR | 0 | O,M | 5 | 205.974 | 0
O&M TECHNICIAN III | 2 | O & M | 3 | 15304.8862 | 45914.6585
SEASONAL O&M TECHNICIAN II | 3 | O & M | 1 | 27304.7372 | 27304.7372
TOTALS | 7 |  |  |  | 148618.7825

## Training
St Peter, Illinois (Ameren) Power Project, Rev 0
Training Program
Class
|  | Weeks | Weeks | $M
Basic Plant Training (All New Hires) (1session at site)
| New Employee Orientation (1 day) * | 0.2 | 0.2 | 0
| Plant Safety/Environmental/Firefighting (3 days) * | 0.6 | 0.6 | 0
| Power Plant Basic O&M (2 days)* | 0.4 | 0.4 | 0
| Introduction to Plant & Systems (3 days)* | 0.6 | 0.6 | 0
|  | 1.8 | 1.8 | 0
Major Systems Training (All O&M Personnel) (1 session at site)
| GT&G Operation & Familiarization (equip vendor)3 | 0.6 | 0.6 | 15
| Boiler Familiarization & Operation (general vendor) | 0 | 0 | 0
| Balance of Plant (general vendor)4 | 2 | 2 | 16
|  | 2.6 | 2.6 | 31
Specialized Operator Training (All Operators) (1 session at site)
| Water Systems & Chemistry (general vendor)4,5 | 0.4 | 0.4 | 0
|  | 0.4 | 0.4 | 0
Control Room Training (All Operators) (1 session at site/other plants)
| GTG controls MK VI (equip vendor)3 | 0.6 | 0.6 | 15
| Boiler controls (general vendor) | 0 | 0 | 0
| DCS Operation & Familiarization (equip. vendor)3 | 0.6 | 0.6 | 15
|  | 1.2 | 1.2 | 30
Basic Maintenance Training (2 x Mechanics) (At Cincinnati)
| Level 1 Maintenance (equip. vendor) | 1 | 1 | 3.848
| Level 2 Maintenance (equip. vendor) | 0 | 0 | 0
| Boroscope Maintenance (equip. vendor) | 0.6 | 0.6 | 3.534
|  | 1.6 | 1.6 | 7.382
Electrical/Controls Maintenance Training (2 x I/C/E Technicians) (at OEM sites)
| GTG controls MK VI (equip vendor) | 2 | 2 | 10
| Generator/Excitation Maintenance (equip. vendor) | 0.6 | 0.6 | 4
| Electrical System Maintenance (general vendor) | 0 | 0 | 0 | Familiarization | No Charge
| DCS Maint. (equip. vendor) | 0.4 | 0.4 | 8
|  | 3 | 3 | 22
Total Class Training Cost |  |  | 10.6 | 90.382
Travel, lodging, facilities, misc.
| Maint Techs' Per diem: # techs x # class weeks at OEM site x 5d/wk x $150/day |  |  | 14.25
| Instructor Per diem: # class weeks at site for OEM x 5d/wk x $150/day (1 instructor/class week) |  |  | 1.35
| Travel: maintenance techs 8 trips x $1M/trip |  |  | 8
| Travel: Instructors (3 Vendors) x $1M/trip ea |  |  | 3
| On site Training Coordinator/Instructor (4 wks x $2600/wk incl per diem + $1M travel) * |  |  | 0
12.35
Total Training Cost Estimate |  |  |  | 102.732
| Less Training provided by Equipment supplier (incl in Purchase PO) |  |  | 61
Net Training Cost Estimate ($M) for Operator/Owner |  |  |  | 41.732
Notes:
1. Assumed cost of training (instructor, training materials, aids, manuals, etc.):
Equip. Vendor Training - $25M/wk
Basic Plant Training (developed in-house) - no added cost
General Vendor Training - $8M/wk
2. The asterisk (*) denotes training and expenses provided by Operator
3. LM6000 and MK VI Familiarization training assumed provided for by EPC Contractor/Equipment Supplier (in Equipment PO).
4. Balance of Plant (gas compressors, chillers, water plant, etc) O&M familiarization training assumed to be included in the EPC contract.
5. Assume that Operator will receive training as part of a service contract entered into with Betz, Nalco, etc.

## ScopeSplit
St Peter, Illinois (Ameren) Power Project, Rev 0
Assumed Turnkey/O&M/Owner Scope Split
Turnkey/
| Startup | O&M | Owner | Remarks/Comments
OPERATING EXPENSES (pre-COD):
Payroll and Benefits
for Owner Personnel |  |  | x
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Employee Expenses/Recruiting/Relocation
for Owner Personnel |  |  | x
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Outside Services
Technical Direction of Installation (TD of I) | x
Vendor reps & startup services | x
Security before COD | x
Security after COD |  |  | x | At Owner's discretion
O&M related services |  | x
Reliability Availability Maintainability (RAM) Study |  |  | x | At Owner's discretion
Process Hazards Analysis (HAZOP) |  |  | x | At Owner's discretion
Other Supplies & Expenses
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Communications (phone bills, etc.)
for O&M Personnel |  | x
for Startup Personnel | x
Offices/Buildings/Facilities (temporary)
for O&M Personnel (admin, training, etc.) |  | x
for Startup/Commissioning Personnel | x
Training for O&M Personnel *
Vendor Familiarization Training (Maj. Equip & Controls) |  |  | x | Assumed in equipment supply
Add'l Major Equip. Vendor |  | x
OJT during startup/commissioning | x
Basic Power Plant Training (& all other training) |  | x
Permits/Insurance
Construction & Startup Contractor's name | x |  |  | need permit matrix
Operator's name |  | x |  | "
Owner's name |  |  | x | "
Manuals, Procedures and Plans
Startup/Commissioning Plans & Procedures | x
Job Data books | x
Engineering drawings (incl. "as builts") | x |  |  | AutoCad 14 (or apprvd substitute)
Systems Descriptions | x
Test procedures & report | x
O&M Procedures | x | x
Admin and all other Plant procedures |  | x
Punchlist resolution | x |  |  | with O&M walkdown
Purchase and transportation of fuel to plant (startup) | x
Schedule fuel deliveries from supplier |  | x
Purchase of turbine generator startup power (backfeed) |  |  | x
Purchase of construction power (from fence line) | x
Purchase and delivery of Process water (hydrotests, etc) | x
Steam Blows |  |  |  | na
Chemical Cleaning (including disposal) | x
Oil Flushes | x
* O&M has overall responsibility for training O&M personnel, but Major Equip. Vendor training (for CT, Chillers, Water
Treatment/Desal, and DCS) will be provided under the major equip. purchase orders (with O&M participation in scoping).
Turnkey/
| Startup | O&M | Owner | Remarks/Comments
Warranty Implementation | x |  |  | O&M/Owner participate
Pre-Mobilization expenses
O&M engineering review/comments |  | x
Operating plans/budgets/estimates |  | x
Other Owner directed O&M services |  | x
Fuel/water quality checking (pre-COD) | x
Procurement Expenses:
Office Furnishings & Equipment
Stationary items (built-ins) | x
PABX (internal) telephone system & wiring | x
LAN wiring
External communications (satellite dish) |  |  |  | na
Office/Building furniture |  | x
Office equipment (copiers, fax, etc.) |  | x
Computer hardware/software |  | x
CMMS computer system (incl training) |  | x
Safety & Environmental equipment
Permanent Fire protection | x
Portable fire extinguishers (for offices & buildings) | x
Portable fire extinguishers (exterior) | x
Safety showers/eye washes | x
Permanent Environmental testing equip. | x
Portable Environmental testing equip. |  | x
O&M Personnel Safety/First Aid equip. |  | x
Vehicles & Mobile Equipment
Construction/Startup Contractor requirements | x
O&M requirements |  | x
Warehouse/Shop Furnishings & Equipment
Stationary items incl hoists (built-ins) | x
Non-stationary items (bins, furniture, etc.) |  | x
Process Monitoring & Laboratory Equipment
Installed analyzers/instruments | x
Stationary lab items (vent hoods, lab benches, etc.) | x
Analytical equipment, glassware, etc. |  | x
Shop Tools and Equipment
Machine shop/Instrument shop tools |  | x
Maint. (incl I/C&E) test equipment |  | x
Work benches, storage bins |  | x
Hand tools for O&M personnel |  | x
Hand tools for Startup personnel | x
Special Tools
Startup, Std Vendor supply | x
Optional vendor supply |  | x | x | Incl with Vendor PO
Chemicals, Lubricants, Fluids
Initial equipment/vessel fill | x
Consumption (pre-COD) | x
Consumption (post-COD) |  | x
Warehouse stock |  | x
Spare parts*
Consumption (pre-COD) | x
Consumption (post-COD) |  | x
Capital (Overhaul) Spares for major equip. |  |  | x | In Owner's scope to accrue
Operating (Initial) Spares for major equip. |  | x
Warehouse stock & BOP spare parts |  | x
Installed Cranes |  |  |  | na
* Turbine spare parts will be purchased based on competitive bids as part of and prior to Turbine vendors selection;
actual parts purchased will be approved by Owner.

## Mob_Backup
| EstimateSummary | Group Item | Budget Item | Line Item | Detail/Basis |  | Total (US $) | LOCAL | FOREIGN | Calculation and Note Area
St Peter, Illinois (Ameren) Power Project, Rev 0
O&M Pre-Mobilization / Mobilization Estimate Backup/Detail
O&M Mobilization BudgetOperating ExpensesPublic Relations Title | O&M Mobilization Budget | Operating Expenses | Public Relations | Pre-Mobilization Expenses
O&M Mobilization BudgetOperating ExpensesPublic Relations | O&M Mobilization Budget | Operating Expenses | Public Relations | recruiting;advertising | Recruiting PM |  | 2500 | 2500 | 0
|  |  |  | payroll | Plant Manager - 1 month pay/benefits |  | 9744.2671 | 9744.2671 | 0
|  |  |  | Travel Expenses in to/fro Houston;living | 2 trips x $1000/trip+ $150/day x 30 days |  | 6500 | 6500 | 0
|  |  |  | miscellaneous comms, postage,etc |  |  | 1000 | 1000 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
O&M Mobilization BudgetOperating ExpensesPublic Relations Total | O&M Mobilization Budget | Operating Expenses | Public Relations | (Assumes Mob period begins COD less 6 months) |  | Sub-Total | 19744.2671 | 19744.2671 | 0
O&M Mobilization BudgetOperating ExpensesPayroll with burden Title | O&M Mobilization Budget | Operating Expenses | Payroll with burden | Payroll with burden
|  |  |  | Total Company Payroll with benefits and 20% overtime on Opns/Maint. |  |  | 148618.7825 | 148618.7825 | 0
|  |  |  | (See detailed PltMobStaff schedule) |  |  |  | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
O&M Mobilization BudgetOperating ExpensesPayroll with burden Total | O&M Mobilization Budget | Operating Expenses | Payroll with burden |  |  | Sub-Total | 148618.7825 | 148618.7825 | 0
O&M Mobilization BudgetOperating ExpensesEmployee Expenses Title | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Employee Expenses
O&M Mobilization BudgetOperating ExpensesEmployee Expenses | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Travel related to Plant Mobilization | 6 trips x $1500/trip |  | 9000 | 9000
|  |  |  | Misc. (OT meals, Conferences,etc.) | $200/month x 6 months |  | 1200 | 1200 |  |  | Where is Ameren HQ?
|  |  |  | Dues, Misc |  |  | 1000 | 1000
|  |  |  | Employee Expenses | $250/month x 4 months |  | 1000
O&M Mobilization BudgetOperating ExpensesEmployee Expenses Total | O&M Mobilization Budget | Operating Expenses | Employee Expenses |  |  | Sub-Total | 12200 | 11200 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses Title | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Recruiting Expenses
|  |  |  | Candidate travel, expenses | 2 trips x $1000/trip+ $150/day x 4 days |  | 2600
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | HR/Home office support | 2 trips x $1500/trip + perdiem @ $150/day x 10 days |  | 4500 | 4500 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Advertisements | Local, Chicago or St Louis |  | 5000 | 5000 | 0
|  |  |  | Screening Tests | $200/employee |  | 1400 | 1400 | 0
|  |  |  | Misc expenses | reproduction, postage, etc |  | 1000 | 1000 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses Total | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses |  |  | Sub-Total | 14500 | 7400 | 0
O&M Mobilization BudgetOperating ExpensesRelocation Expenses Title | O&M Mobilization Budget | Operating Expenses | Relocation Expenses | Relocation Expenses
|  |  |  | Plant Mgr (assume non-Enron) | 20% of base |  | 17056
|  |  |  | Technician III (assume 1 needed) | cover HHG shipment, misc |  | 5000 | 5000 | 0
|  |  |  | Technician II (assume 0 needed) | cover HHG shipment, misc |  | 0 | 0 | 0
|  |  |  | Seasonal O&M Technicians | Private auto to site & temp living = ($300/trip + 30days*$50/day)x3 |  | 5400
O&M Mobilization BudgetOperating ExpensesRelocation Expenses Total | O&M Mobilization Budget | Operating Expenses | Relocation Expenses | Rest of staff assumed obtained locally |  | Sub-Total | 27456 | 5000 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services Title | O&M Mobilization Budget | Operating Expenses | Outside Services | Outside Services
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Guards | Turnkey responsibility |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Groundskeepers | Turnkey responsibility |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Janitors | $800/month x 5 months |  | 4000 | 4000 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Legal | Covered in fee |  | 0 | 0 | 0
|  |  |  | Tax | Covered in fee |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Accounting | 1 trips x $1000/trip + 4 days per diem x $150/day |  | 1600 | 1600 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Safety | 2 trips x $1000/trip + 8 days per diem x $150/day |  | 3200 | 3200 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Environmental | 2 trips x $1000/trip + 8 days per diem x $150/day |  | 3200 | 3200 | 0
|  |  |  | Management | 2 trips x $1000/trip + 8 days per diem x $150/day |  | 3200
|  |  |  | Technical/Professional | 15 days x 8hrs/day x $60/hr |  | 7200
|  |  |  | Trash/Waste Disposal | Turnkey responsibility |  |  | 0 | 0
|  |  |  | Electrical Testing/Calibration | Turnkey responsibility |  |  | 0 | 0
|  |  |  | Buyer support from other projects | 480 hrs x $43/hr |  | 20640 | 20640 | 0
|  |  |  | Uniform services |  |  | 3000
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Office Equipment Maintenance |  |  | 0 | 0 | 0
|  |  |  | Warehouse temporaries | $20/hr x 160 hrs |  | 3200
O&M Mobilization BudgetOperating ExpensesOutside Services Total | O&M Mobilization Budget | Operating Expenses | Outside Services | Labor for all OEC staff assumed covered in Operator's Fee and O/H allocation |  | Sub-Total | 49240 | 32640 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses Title | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Other Supplies & Expenses
|  |  |  | Postage & Freight | $100/month x 6 months |  | 600 | 600
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Office & Misc. Supplies (usage) | $500/month x 5 months |  | 2500 | 2500
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Vehicle fuel and maint | 1 vehicles x 5 months x 1000miles/month x $1.5/14 miles + $500 |  | 1035.7143 | 1035.7143
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Janitorial Supplies (usage) |  |  | 2000 | 2000
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Bldg. Utilities (water, power, gas) | 5 months x $500/month |  | 2500 | 2500
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses Total | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses |  |  | Sub-Total | 8635.7143 | 8635.7143 | 0
O&M Mobilization BudgetOperating ExpensesCommunications Title | O&M Mobilization Budget | Operating Expenses | Communications | Communications
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Phone Service | 5 months x $500/month (excludes cellular service) |  | 2500 | 2500
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Cellular Phones | 1ea. x 6 months x $300/month |  | 1800 | 1800
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Pagers | pagers 6 x $20/month x 4 months |  | 480 | 480
O&M Mobilization BudgetOperating ExpensesCommunications Total | O&M Mobilization Budget | Operating Expenses | Communications |  |  | Sub-Total | 4780 | 4780 | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses Title | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Temporary Offices/Facilities
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Office Bldgs. | Use existing plant buildings/offices when necessary |  |  | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Trailers (admin only, ex training) | 1 x $1000/months x 4 months |  | 4000 | 4000
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Sanitary facilities |  |  | 800 | 800
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Misc. Furnishings |  |  |  | 0
|  |  |  | Temporary Living Quarters |  |  |  | 0
Assume admin facilties complete COD minus 2 months
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses Total | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses |  |  | Sub-Total | 4800 | 4800 | 0
O&M Mobilization BudgetOperating ExpensesTraining Title | O&M Mobilization Budget | Operating Expenses | Training | Training
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Basic Plant Training | See Training sheet |  | 41732 | 41732 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Major Systems Training |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Plant Chemistry |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Control Room Training |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Basic Maintenance |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Electrical/Controls Maintenance |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Additional Vendor Training |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Per diem for instructors |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Facilities (trailer rental, hall) |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Travel |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Training Coordinator |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Additional Manuals/Documents |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Miscellaneous |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Translation |  |  |  | 0 | 0
[8 empty] | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining Total | O&M Mobilization Budget | Operating Expenses | Training |  |  | Sub-Total | 41732 | 41732 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures Title | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Manuals/Operating Procedures
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Administration | 5 mandays @$400/manday |  | 2000 | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Operations check lists | 10 P&Ids x 2 mandays each x $400/day |  | 8000 | 8000 | 0
|  |  |  | Maintenance | 1/2 of operating procedures |  | 4000 | 4000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Maintenance/CMMS (excluding data) | 5 mandays @$400/manday |  | 2000 | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Warehouse/Inventory | 5 mandays @$400/manday |  | 2000 | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Emergency Plans | 40 mandays @$400/manday |  | 16000 | 16000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Safety and Health | 5 mandays @$400/manday |  | 2000 | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Environmental Compliance | 20 mandays @$400/manday |  | 8000 | 8000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Utility dispatch | 10 mandays @$400/manday |  | 4000 | 4000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Government Reporting | 10 mandays @$400/manday |  | 4000 | 4000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Owner Reports | 5 mandays @$400/manday |  | 2000 | 2000 | 0
|  |  |  | Accounting | 1 mandays @$400/manday |  | 400 | 400 | 0
|  |  |  | Training Program | 10 mandays @$400/manday |  | 4000 | 4000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures |  |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Reproduction/Printing |  |  | 3000 | 3000 | 0
|  |  |  | Freight | 5% of Reproduction cost |  | 150 | 150 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures Total | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures |  |  | Sub-Total | 61550 | 61550 | 0
O&M Mobilization BudgetOperating ExpensesPermits Title | O&M Mobilization Budget | Operating Expenses | Permits | Permits
O&M Mobilization BudgetOperating ExpensesPermits | O&M Mobilization Budget | Operating Expenses | Permits | Owner's Scope of Supply |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesPermits Total | O&M Mobilization Budget | Operating Expenses | Permits |  |  | Sub-Total | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesInsurance Title | O&M Mobilization Budget | Operating Expenses | Insurance | Operator's Insurance
O&M Mobilization BudgetOperating ExpensesInsurance | O&M Mobilization Budget | Operating Expenses | Insurance | Worker's Compensation | $200/employee/yr |  | 700 | 700 |  |  | Insurance costs per Paul Clayton
|  |  |  | Auto Liability | $400/yr/licensed vehicle |  | 200
O&M Mobilization BudgetOperating ExpensesInsurance | O&M Mobilization Budget | Operating Expenses | Insurance | 3rd Party/General Liability | 0.15% of Total Expenses |  | 1651.9491 |  |  | 0.0015
O&M Mobilization BudgetOperating ExpensesInsurance Total | O&M Mobilization Budget | Operating Expenses | Insurance |  |  | Sub-Total | 2551.9491 | 700 | 0
Operations Support Personnel
|  |  |  | Operations Support Personnel | 1ea.x$350/dayx30days (includes benefits) |  | 10500 | 10500 | 0
|  |  |  | Per diem | 1ea.x$125/dayx30days |  | 3750 | 3750 | 0
|  |  |  | Home leave, travel | 1ea.x$1000 tripx1trips (coach class) |  | 1000 | 1000 | 0
[8 empty] | 0 | 0
|  |  |  | Basis: 1 Operating Engineer as operations support 1 months prior to COD |  | Sub-Total | 15250 | 15250 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies Title | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Office Furnishings, Equipment, Supplies
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Offices (desk, chair, table, misc) | 4ea @ $800/set |  | 3200 | 3200 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Chairs - misc. | 10ea @ $150 |  | 1500 | 1500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Bookshelves | 10ea @ $75 |  | 750 | 750 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | File Cabinets | 4ea @ $200 |  | 800 | 800 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Storage Shelves/Cabinets | 10ea @ $50 |  | 500 | 500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Conference Room (table & chairs) | 6ea @ $150 + $1000 |  | 1900 | 1900 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Tables | 1ea @ $150 |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Chairs | 6ea @ $75 |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Microwave | 1 ea @ $150 |  | 150 | 150 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Coffee Pot | 1 ea. @ $150 |  | 150 | 150 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Refrig. | 1 ea @ $750 |  | 750 | 750 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Misc |  |  | 500 | 500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Computer Tables | 5ea @ $200 |  | 1000 | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Computers w printers | 5ea @ $3000 |  | 15000 | 15000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Systems Software | 5ea @ $500 |  | 2500 | 2500 | 0
|  |  |  | CMMS software/installation | $10M License + $10M installation/training |  | 20000 | 20000 | 0
|  |  |  | CMMS hardware, equipment | 1 PC's ($2500), printer |  | 0 | 0 | 0
|  |  |  | SAP Acctg System | Software & License |  | 0 | 0 | 0
|  |  |  | SAP Acctg System | Training & Implementation |  | 10000 | 10000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Copiers | 1ea @ $8000 |  | 8000 | 8000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Typewriters | 1ea @ $250 |  | 250 | 250 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Local Area Network | LAN $2M + Installation $1,000 |  | 3000 | 3000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Calculators | 5ea @ $20 |  | 100 | 100 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Projectors (overhead) | 1ea @ $400 |  | 400 | 400 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | TV/VCR/Camcorders | 1ea @ $750/$500/$750 |  | 2000 | 2000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies |  |  |  |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | White Boards | 5ea @ $80 |  | 400 | 400 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | FAX machine | 1ea @ $400 |  | 400 | 400 | 0
|  |  |  | Misc Supplies | pens, paper, staplers, envelopes, etc. |  | 1000 | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Phones | 6ea @ $200 |  | 1200 | 1200 | 0
|  |  |  | Office Misc, pictures, plants, rugs, boards |  |  | 5000 | 5000 | 0
|  |  |  | Janitorial supplies |  |  | 1000 | 1000 | 0
|  |  |  | Freight | 5% of cost |  | 4072.5 | 4072.5 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies Total | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies |  |  | Sub-Total | 85522.5 | 85522.5 | 0
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies Title | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Safety & Environmental Equipment & Supplies
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Personnel Safety equipment | Safety glasses, Hard hats, goggles, face shields, gloves, |  |  | 0 | 0
[5 empty] | locks, acid suits, SCBA respirators, safety shoes, etc. |  | 3000 | 3000 | 0
|  |  |  | Portable Fire Extinguishers | 10ea. @ $120 |  | 1200 | 1200 | 0
|  |  |  | Firehose Cabinet Accessories |  |  | 7700 | 7700 | 0
|  |  |  | First Aid equipment | First Aid kit, stretcher, water jell blanket |  | 6000 | 6000 | 0
|  |  |  | Safety test Equipment | Biosystem unit, LEL & O2 meter |  | 2500 | 2500 | 0
|  |  |  | Environmental Test Equipment | Noise level meter |  |  | 0 | 0
|  |  |  | 6" and 12" containment booms |  | 44700 |  | 0 | 0
|  |  |  | 30 ton/hr skimmer |  | 21000 |  | 0 | 0
|  |  |  | Misc. anchors, tow bridles, buoys, etc. |  | 17600 |  | 0 | 0
|  |  |  | Freight | 5% of cost |  | 1020 | 1020 | 0
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies Total | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies |  |  | Sub-Total | 21420 | 21420 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment Title | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Vehicles & Mobile Equipment
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Cars 4 WD w AC |  | $26M |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 1/2 ton Pickup Trucks | 1ea leased $2000 down & lease | 700/mnth | 6200 | 6200 | 0
|  |  |  | 2 1/2 ton flat bed truck w winch |  | $32M |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 6 ton Forklift (outside) |  | $38M |  | 0 | 0
|  |  |  | 3 ton Forklift (warehouse) | 1ea leased $1000 down & lease | 500/mnth | 2000 | 2000 | 0
|  |  |  | 12 passenger Van w/o AC |  | $24M |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 18 passenger Van w/o AC |  | $30M | 0 | 0 | 0
|  |  |  | Firefighting equipment | 1ea. extinguisher cart | $1M per | 1000 | 1000 | 0
|  |  |  | Backhoe/heavy equipment |  |  | 0 | 0 | 0
|  |  |  | Compressor water wash cart |  | $10M |  | 0 | 0
|  |  |  | 250 cfm Air Compressor (trailer mtd) |  | $16M |  | 0 | 0
|  |  |  | 400 amp welder(diesel drvr, trailer) |  | $11M |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 8 ton Crane |  | $30M (used) |  | 0 | 0
|  |  |  | Crew Boats |  | $60M (used) | 0 | 0 | 0
|  |  |  | Switch engine |  | $300M | 0 | 0 | 0
|  |  |  | Maintenance cart |  |  | 2500
|  |  |  | Freight | 5% of cost |  | 460 | 460 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment Total | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Basis: Purchasing Dept. |  | Sub-Total | 12160 | 9660 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment Title | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Warehouse Furnishings & Equipment
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Bins/Racks/shelves | includes Lumber, nails, materials (to construct) |  | 9000 | 9000 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Equipment/Tools | dollies, scales, carpenter tools, banding & labeling machines |  | 1500 | 1500 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Furniture | tables, desks, chairs, file cabinets |  |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Miscellaneous Supplies |  |  | 1000 | 1000 | 0
|  |  |  | Freight | 5% of cost |  | 575 | 575 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment Total | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment |  |  | Sub-Total | 12075 | 12075 | 0
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment Title | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Laboratory Equipment
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Laboratory Analyzers (pH, conductivity, spectrophotometer) |  |  | 3000 | 3000 | 0
|  |  |  | Glassware/Misc. Equipment (centrifuge, vacuum pump, PC,scale,oven) |  |  | 2000 | 2000 | 0
|  |  |  | Furniture, cabinets, benches, tables, refrigerator |  |  | 1000 | 1000 | 0
|  |  |  | Fuel Testing equipment | Gas Chromatogragh/Atomic Absorption |  |  | 0 | 0
|  |  |  | Freight | 5% of cost |  | 300 | 300 | 0
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment Total | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Basis: Rino Manzano ccMail dtd 8/8/96 |  | Sub-Total | 6300 | 6300 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment Title | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Shop Tools & Equipment
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Mechanic Hand Tools | tool boxes | $1200 each | 1200 | 1200 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | I/E Tech Hand Tools | tool boxes | $1500 each | 1500 | 1500 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Consumables (Cleaning, Mech. supplies, compounds, I&E supplies, hoses) |  | 8000 | 8000 | 8000 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Radios (Basis: Houston 2-way Radio - Motorola HC1000, 2 channels) |  | $1000 each | 4000 | 4000 | 0
|  |  |  | Radio Base |  | $1000 each | 1000 | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Mechanical Shop Tools & Equip. | High Pressure Hand Pump | $1200 each |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Nordstrom Hyper Grease Gun 5 gal. | $3015 each |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Rockwell Hand Held High Pressure Grease Gun | $960 each | 960 | 960 | 0
[5 empty] | Hydraulic Torque Wrench | $4000 each |  | 0 | 0
[5 empty] | Centrifugal Pump | $2500 each | 2500 | 2500 | 0
[5 empty] | Pneumatic diaphram pump | $1000 each | 1000 | 1000 | 0
[5 empty] | Bead Blaster | $1800 each |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Sand Blaster | $900 each | 900 | 900 | 0
[5 empty] | Portable Air Compressor | $600 each | 600 | 600 | 0
[5 empty] | Hydraulic Press - 25 ton | $1400 each | 1400 | 1400 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment Total | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Post Hole Digger | $1200 each |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids Title | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Steel Work Bench | $160 each | 160 | 160 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Employee Lockers | $250 each | 2000 | 2000 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Storage Cabinets | $300 each | 600 | 600 | 0
[5 empty] | Parts Washer | $1000 each | 1000 | 1000 | 0
[5 empty] | Bench Grinder | $400 each | 400 | 400 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids Total | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Drill Press | $2375 each | 2375 | 2375 | 0
O&M Mobilization BudgetO&M Mobilization Fee Title | O&M Mobilization Budget | O&M Mobilization Fee |  |  | AC/DC Welder Generator | $3100 each | 3100 | 3100 | 0
O&M Mobilization BudgetO&M Mobilization Fee | O&M Mobilization Budget | O&M Mobilization Fee |  |  | Assortment Hammer Wrenches | $5000 each |  | 0 | 0
[5 empty] | Flange Spreader | $250 each | 250 | 250 | 0
[5 empty] | Hoists /Come-a-longs | $1000 each | 1000 | 1000 | 0
[5 empty] | Miscellaneous small hand tools | $5000 set | 5000 | 5000 | 0
O&M Mobilization BudgetO&M Mobilization Fee Total | O&M Mobilization Budget | O&M Mobilization Fee |  | I/E Shop Tools & Test Equipment | Gas Detector Calibration Kit | $500 each | 500 | 500 | 0
O&M Mobilization BudgetOwner Optional Items Title | O&M Mobilization Budget | Owner Optional Items |  |  | Flow, Press, & Temp Transmitter Communicators | $5000 set | 5000 | 5000 | 0
O&M Mobilization BudgetOwner Optional Items | O&M Mobilization Budget | Owner Optional Items |  |  | Digital Thickness Gauge | $1800 each | 1800 | 1800 | 0
[5 empty] | UV IR Portable Test Kit | $4000 each | 4000 | 4000 | 0
[5 empty] | IRD Vibration Meter | $8000 each | 8000 | 8000 | 0
[5 empty] | Fluke Digital Multimeter | $350 each | 700 | 700 | 0
O&M Mobilization BudgetOwner Optional Items Total | O&M Mobilization Budget | Owner Optional Items |  |  | Thermocoupler Calibrator | $950 each | 950 | 950 | 0
[5 empty] | Precision Pressure Calibrator | $5700 each | 5700 | 5700 | 0
[5 empty] | Simpson Multimeter | $300 each |  | 0 | 0
[5 empty] | RTD Calibrator | $700 each | 700 | 700 | 0
[5 empty] | Test Gauges 0 -1500 psig. | $1000 set | 1000 | 1000 | 0
[5 empty] | Gravitometer | $5850 each |  | 0 | 0
[5 empty] | PK Tester | $4065 each | 4065 | 4065 | 0
[5 empty] | Pipeline Locator | $3900 each |  | 0 | 0
|  |  |  | Test/Troubleshooting Equipment | Beta Engine Analyzer | $60,000 each |  | 0 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) Title | O&M Mobilization Budget | Capital, Operating and BOP Spares (1996$) |  |  | Oscilloscope | $3000 each |  | 0 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) | O&M Mobilization Budget | Capital, Operating and BOP Spares (1998$) |  |  | Bore Scope (probe, light source and photo) | $15,000 each |  | 0 | 0
[5 empty] | Combustible Gas Detector | $1795 each | 1795 | 1795 | 0
[8 empty] | 0 | 0
|  |  |  | Freight | 5% |  | 3657.75 | 3657.75 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) Total | O&M Mobilization Budget | Capital, Operating and BOP Spares (1998$)
[6 empty] | Sub-Total | 76812.75 | 76812.75
Chemicals, Lubricants, Hydraulic Fluids
|  |  |  | Warehouse Stock | 1month's worth x chemicals |  | 10000 | 10000 | 0
[8 empty] | 0 | 0
|  |  |  | Freight | 5% of cost (included above) |  | 500 | 500 | 0
[6 empty] | Sub-Total | 10500 | 10500 | 0
O&M Mobilization Fee
|  |  |  | Fixed Fee |  |  | 125000 | 125000 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[6 empty] | Sub-Total | 125000 | 125000 | 0
Operator Overhead Charge (G&A)
|  |  |  | Included in the "Benefits" calculations | at 15% of base wages |  |  | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[6 empty] | Sub-Total |  | 0 | 0
Commercial Office Mobilization
|  |  |  | Within the Owner's scope |  |  | 0 | 0 | 0
[6 empty] | Sub-Total | 0 | 0 | 0
Owners' Engineer
|  |  |  | Within the Owner's scope |  |  | NA | NA | #VALUE!
[6 empty] | Sub-Total | NA | 0 | #VALUE!
Capital, Operating and BOP Spares
|  |  |  | LM6000PC package spares |  |  | 877000 | 877000 | 0
|  |  |  | BOP |  |  | 25000 | 25000 | 0
|  |  |  | Freight & Insurance |  |  | 11275 | 11275 | 0
[8 empty] | 0 | 0
[6 empty] | Sub-Total | 913275 | 913275 | 0

## O&M_Estimate
St Peter, Illinois (Ameren) Power Project, Rev 0
Commercial Operations O&M Estimate
2000 US $
|  |  |  | 3 YEAR | 20 YEAR
|  | Year 1 | Years 2+ | AVERAGE | AVERAGE
Payroll & Burden |  | 519842.8862 | 519842.8862 | 519842.8862 | 519842.8862 | Fixed
Administration and Operations Expenses
| Employee Expenses | 44750 | 44750 | 44750 | 44750
| Permanent Contract Labor | 21100 | 21100 | 21100 | 21100
| Environmental Expense | 38000 | 38000 | 38000 | 38000
| Safety Expense | 10000 | 10000 | 10000 | 10000
| Buildings & Grounds | 9287.6956 | 9287.6956 | 9287.6956 | 9287.6956
| Other Supplies & Expenses | 56580 | 56580 | 56580 | 56580
| Communications | 9960 | 9960 | 9960 | 9960
| Insurance | 3451.9491 | 3451.9491 | 3451.9491 | 3451.9491
| Control Room/Laboratory Expenses | 4690 | 4690 | 4690 | 4690
| Operations Support (Year 1 Only) | 15250 | 0 | 5083.3333 | 762.5 |  | Makeup to Reverse Osmosis |  | 216 gpm
[7 empty] | Makeup to Cooling Tower |  | 192 gpm
| Total Administration & Operations Expenses | 213069.6447 | 197819.6447 | 202902.978 | 198582.1447 | Fixed | Service Water |  | 10 gpm
[7 empty] | Potable Water |  | 2 gpm
Water Costs |  |  | 0 | 0 | 0 | Variable | Blowdown from CoolingTower |  | 41 gpm
Chemicals |  | 29716.6 | 29716.6 | 29716.6 | 29716.6 | Variable
Wastewater Costs |  |  | 0 | 0 | 0 | Variable
[7 empty] | Supply | Waste
Maintenance Expenses | [6 empty] | 420 | 41 gpm
| Painting | 7097.584 | 28390.336 | 21292.752 | 27325.6984 |  | 49140000 | 4797000
| Instruments & Controls | 3501.5625 | 7003.125 | 5835.9375 | 6828.0469
| Water Treatment System | 3178.6381 | 6357.2762 | 5297.7302 | 6198.3443
| Cooling System & Chillers | 22801.862 | 45603.7239 | 38003.1033 | 44463.6308
| Electrical/Substation/Interconnects | 21533.3758 | 43066.7516 | 35888.9597 | 41990.0828
| Gas Turbines (excluding overhaul maint.) | 54572.5 | 109145 | 90954.1667 | 106416.375
| Selective Catalytic Reduction & Ammonia System | 0 | 0 | 0 | 0
| Steam Turbine (including Scheduled Maint.) | 0 | 0 | 0 | 0
| Potable Water System | 959.6875 | 1919.375 | 1599.4792 | 1871.3906
| Fuel Handling & Compression System | 16296.875 | 32593.75 | 27161.4583 | 31778.9062
| Miscellaneous Maintenance Expense | 63806.25 | 63806.25 | 63806.25 | 63806.25
| Total Maintenance | 193748.3349 | 337885.5877 | 289839.8367 | 330678.7251 | 75% Fixed / 25% Variable
Sustaining Capital Expenses |  | 22479.025 | 22479.025 | 22479.025 | 22479.025 | Fixed
Contingency |  | 0 | 0 | 0 | 0
Total O&M Expenses (excl GT Scheduled Maint. Program) |  | 978856.4907 | 1107743.7436 | 1064781.3259 | 1101299.3809
GT Scheduled Major Maintenance ($/fired hour for 20 Yr term) |  | 44.1562 |  |  |  | Variable
SCR Catalyst Replacement Accrual ($/fired hour) | [5 empty] | Variable
GT Lease Program Annual Membership (1 unit) | [5 empty] | Fixed
Housing Colony Operating Expenses |  | NA | NA
Commercial Office Expenses |  | NA | NA | NA | NA
O&M Annual Operating Fee |  | 175000 | 175000 | 175000 | 175000 | Fixed

## Plt_Staff
St Peter, Illinois (Ameren) Power Project, Rev 0
Commercial Operations Staffing Plan
(US$)
|  | INDIVIDUAL |  | ANNUAL | TOTAL ANNUAL | TOTAL ANNUAL
| STAFFING | SALARY | HOURLY RATE | HOURS | SALARY & WAGES | BENEFITS | TOTAL
PLANT MANAGER | 1 | 85280 |  | 2080 | 85280 | 41395.472 | 126675.472
CLERK | 1
Straight Time |  |  | 12.25 | 2080 | 25480 | 16076.152 | 41556.152
Over time |  |  | 18.375 | 104 | 1911 | 560.6874 | 2471.6874
O&M SUPERVISOR | 0
O&M TECHNICIAN III | 2
Straight Time |  |  | 25 | 2080 | 104000 | 54609.44 | 158609.44
Over time |  |  | 37.5 | 416 | 31200 | 9154.08 | 40354.08
SEASONAL O&M TECHNICIAN II | 3
Straight Time |  |  | 30 | 880 | 79200 | 40244.8708 | 119444.8708
Over time |  |  | 45 | 176 | 23760 | 6971.184 | 30731.184
TOTAL | 7 |  |  |  | 350831 | 169011.8862 | 519842.8862
1. Benefits amounts includes Operator G&A allocation.
2. Assumes that Operators will be on 7 days/week shifts to cover during peak and one shift for 8 hrs/day during off-peak. No weekend coverage planned in off-season (Oct-Apr).

## Pay & Benefits Calculations
St Peter, Illinois (Ameren) Power Project, Rev 0
Pay & Benefits Calculations
POSITIONS | ANNUAL* | Annual
| SALARY | Hours
| IN US $ | 2080
PLANT MANAGER | 126675.472
MAINTENANCE MANAGER | 119159.92
PURCHASING / WAREHOUSE | 79304.72
CLERK | 41556.152
PLANT SUPERVISOR | 97808.92
TECHNICIAN III | 79304.72
TECHNICIAN II | 94108.08
Straight Time Domestic Rates
Employee Cost Breakdown
[12 empty] | Mobilization Period |  |  | Operating Period
[5 empty] | Monthly | [6 empty] | Quantity | Hours | Total | Quantity | Hours | Total
| Base | Payroll | Workers |  | Group | General | Cash
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Balance | ESOP | 401(k) | Burdened | Base
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  |  |  | Total | Annual
|  | 14.34% | 0% | 15% | 440.66 | 0% | 5% | 5% | 3% |  | Salary
Administration
Plant Manager | 41 | 5.8794 | 0 | 6.15 | 2.5423 | 0 | 2.05 | 2.05 | 1.23 | 60.9017 | 85280 | 1 | 960 | 58465.6025 | 1 | 2080 | 126675.472
Maintenance Manager | 38.4615 | 5.5154 | 0 | 5.7692 | 2.5423 | 0 | 1.9231 | 1.9231 | 1.1538 | 57.2884 | 80000 |  | 1120 | 0 |  |  | 0
Purchasing / Warehouse | 25 | 3.585 | 0 | 3.75 | 2.5423 | 0 | 1.25 | 1.25 | 0.75 | 38.1273 | 52000 |  | 1120 | 0 |  |  | 0
Clerk | 12.25 | 1.7567 | 0 | 1.8375 | 2.5423 | 0 | 0.6125 | 0.6125 | 0.3675 | 19.9789 | 25480 | 1 | 800 | 15983.1354 | 1 | 2080 | 41556.152
Operations & Maint.
Supervisor | 31.25 | 4.4813 | 0 | 4.6875 | 2.5423 | 0 | 1.5625 | 1.5625 | 0.9375 | 47.0235 | 65000 |  |  | 0 |  |  | 0
O&M TECHNICIAN III | 25 | 3.585 | 0 | 3.75 | 2.5423 | 0 | 1.25 | 1.25 | 0.75 | 38.1273 | 52000 | 2 | 480 | 36602.1785 | 2 | 2080 | 158609.44
SEASONAL O&M TECHNICIAN II | 30 | 4.302 | 0 | 4.5 | 2.5423 | 0 | 1.5 | 1.5 | 0.9 | 45.2443 | 62400 | 3 | 160 | 21717.2492 | 3 | 880 | 119444.8708
Over Time Domestic Rates
Employee Cost Breakdown
| Base | Payroll | Workers |  | Group | General
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | ESOP | 401(k) | Burdened
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  |  |  | Total
|  | 14.34% | 0% | 15% | 0 | 0% | 5% | 0% | 0%
Administration
Plant Manager | 61.5 | 8.8191 | 0 | 9.225 | 0 | 0 |  |  |  | 79.5441 |  | 1 | 0 | 0 | 1 | 0 | 0
Maintenance Manager | 57.6923 | 8.2731 | 0 | 8.6538 | 0 | 0 |  |  |  | 74.6192 |  |  |  | 0 |  |  | 0
Purchasing / Warehouse | 37.5 | 5.3775 | 0 | 5.625 | 0 | 0 |  |  |  | 48.5025 |  |  |  | 0 |  |  | 0
Clerk | 18.375 | 2.635 | 0 | 2.7563 | 0 | 0 |  |  |  | 23.7662 |  | 1 | 40 | 950.649 | 1 | 104 | 2471.6874
Operations & Maint.
Supervisor | 46.875 | 6.7219 | 0 | 7.0312 | 0 | 0 |  |  |  | 60.6281 |  |  |  | 0 |  |  | 0
O&M TECHNICIAN III | 37.5 | 5.3775 | 0 | 5.625 | 0 | 0 |  |  |  | 48.5025 |  | 2 | 96 | 9312.48 | 2 | 416 | 40354.08
SEASONAL O&M TECHNICIAN II | 45 | 6.453 | 0 | 6.75 | 0 | 0 |  |  |  | 58.203 |  | 3 | 32 | 5587.488 | 3 | 176 | 30731.184
[13 empty] | Totals | 148618.7825 |  |  | 519842.8862
Note on O28: EI: 6 months
Note on O31: EI: 5 months
Note on O34: EI: 3 months
Note on O35: EI: 1 month
Note on R35: EI: Assumes seasonal O&M technincian onsite for the 5 month dispatch season + 2 week of churn.
Note on O49: EI: 5% overtime
Note on R49: EI: 5% overtime assumed
Note on O52: EI: 20% overtime
Note on R52: EI: 20% overtime assumed
Note on O53: EI: 20% overtime
Note on R53: EI: 20% overtime assumed

## O&M_Backup
Line Item | Detail/Basis |  | Total (US $) | Calculation and Note Area
St Peter, Illinois (Ameren) Power Project, Rev 0
O&M Estimate Backup/Detail
Payroll & Burden (Total over project life)
| See detailed sheet |  | 519842.8862
0
0
0
Basis: HR data |  | Sub-Total | 519842.8862
Employee Expenses
Travel Expenses/Overtime Meals | 4 x $1,000/trip + 20 days x $150/day |  | 7000
Conferences/Training | 3 x $2000 each |  | 6000
Fees & Dues |  |  | 1000
Employees Expense | $250/month |  | 3000
Entertainment Expense | $150/employee |  | 1050
Recruiting |  |  | 1200
Season O&M Tech T&L | 5 months x $1500/month x 3 employee + $1000/churn x 3 employees |  | 25500
Basis: OEC experience |  | Sub-Total | 44750
Permanent Contract Labor
Purchasing Support | $43/hr x 100 hrs/yr |  | 4300
Janitorial | $800/month x 12 months |  | 9600
Groundskeeping/Landscaping | $400/month x 12 months |  | 4800
Uniform Services | $200/month x 12 months |  | 2400
Lab Services | costs shown in Lab Expenses category
Basis: |  | Sub-Total | 21100
Environmental Expense
Training/Awards |  |  | 2500
Permits | RATA testing |  | 16000
Materials & Supplies | Calibration/test gases | 2 stacks | 10000
Technical/Professional Services | 2 trip x $1M/trip + 4 days perdiem x $125/day |  | 2500
Technical/Professional Services | 80 manhrs x $75/hr (audit) | covered in O/H | 0
Other Outside Services |  |  | 0
Non-Hazardous Waste Handling |  |  | 5000
Other |  |  | 2000
Basis: OEC experience |  | Sub-Total | 38000
Safety Expense
Training/Awards |  |  | 2500
Permits
Company Membership & Dues |  |  | 1000
Routine Safety Supplies |  |  | 4000
Technical/Professional Services | 2 x $1M/trip + 4 days perdiem x $125/day |  | 2500
Technical/Professional Services | Labor covered in O/H
Safety Equipment Rentals
Basis: OEC experience |  | Sub-Total | 10000
Buildings & Grounds
HVAC | Scaled on MW |  | 9287.6956
Building repairs & painting | $22,900 x (plant size in MW/414MW)^.6
Road repairs
Technical/Professional Services
Outside services Contract labor
Equipment Rentals
Other Rents
Supplies
Basis: Tx City/Clear Lake experience |  | Sub-Total | 9287.6956
Other Supplies & Expenses
Office Supplies & Expenses | $500/month x 12 months |  | 6000
Postage & Express Mail | $250/month x 12 months |  | 3000
Outside Services Contract Labor | 120 hrs x $12/hr |  | 1440
Technical/Professional Services | Misc services at 40 hrs x $100/hr |  | 4000
Legal | Home office support covered in overheads |  | 0
Accounting | Home office support covered in overheads |  | 0
Office Equipment Maint. |  |  | 1200
Tax | Home office support covered in overheads |  | 0
Regional Mgmt Support | 4 trips x $1000/trip + 8 days perdiem x $150/day |  | 5200
Uniform services
Regulatory | Owner's scope |  | 0
Janitorial
Other Outside Services | Garbage & Trash |  | 3000
Office Equipment Rental |  |  | 1200
Other Rents |  |  | 2000
Radio parts/repair | 50% of Subic |  | 1800
PC Hardware (purchase) | Same as Subic for items < $1000, otherwise in Sus. Capital |  | 1000
PC Software | 1 CMMS licenses @ $750 ea.+ upgrades |  | 1500
PC Hardware Rental/Lease
PC Maintenance |  |  | 2000
Misc Freight Expenses |  |  | 2200
Utilities (office water, power, gas) | Assumed in Plant's House Load |  | 0
Public relations/Contributions |  |  | 2500
Boat maintenance/repair |  |  | 0
Vehicle & mobile equipment Lease | 2 x $600/month x 12 months/yr |  | 14400
Vehicle maintenance/repair | $500/vehicle/year |  | 1000
Vehicle fuel | see detail below |  | 3140
Boat fuel | na |  | 0
|  | Sub-Total | 56580
Communications
Phone service | $500/month x 12 months |  | 6000
Cellular phone service | 1 phones x $300/month |  | 3600
Pagers | 6 x $5/month x 12 months |  | 360
|  | Sub-Total | 9960
Insurance
Worker's Compensation | $200/employee |  | 1400
Auto Liability | $400/yr/licensed vehicle |  | 400
3rd Party/General Liability | 0.15% of Total Expenses |  | 1651.9491 | 0.0015 | Insurance costs per Paul Clayton
Basis: Enron Risk Mgmt |  | Sub-Total | 3451.9491
Control Room/Laboratory Expenses
Technical/Professional Services | Lab analysis monthly, annual, etc | $200/mo. | 2400
Reagents & Supplies |  |  | 1200
Rental Equipment
Analyzer Repairs |  |  | 1000
Contract Labor/Temporaries
Other Outside Services
Freight | 5% of 75% of total |  | 90
Basis: OEC/Vineland Experience |  | Sub-Total | 4690
Operations Support (Year 1 Only)
Operations Support Personnel | 1ea.x$350/dayx30days (includes benefits) |  | 10500
Per diem | 1ea.x$125/dayx30days |  | 3750
Home leave, travel | 1ea.x$1000 trip x 1trips (coach class) |  | 1000
Tax Protection (over 6 months) | n/a |  | 0
Ops engineer for 1 month to aid in Initial Operating Period |  | Sub-Total | 15250
Chemicals & Water Treatment
Technical/Professional Services |  |  | 0
Demin Acid/Caustic
Trailer Leasing Mixed Beds
Resin Replacement
CT Chemicals | assume at 3 cycles, ground water makeup |  | 7050
Boiler Chemicals
Desal RO Chemicals & Membrane replacement |  |  | 15442
Potable Water Chemicals | n/a
SCR Ammonia usage | 46 lbs/hr/gt x 4 gts x 1300 hrs/year x $0.2/lb |  | 0
Hydrogen (generators) | Assume air cooled
Waste Water Treatment |  |  | 2000
GT Water Wash Detergent | 2 drums / year |  | 4000
freight | 5% of total |  | 1224.6
Basis: source is 1000 ppm TDS ground water; CT flow 17000 gpm; range 10 deg F |  | Sub-Total | 29716.6
Painting
Paint & Materials | $70,000 x (plant size in MW/414)^.6 |  | 28390.336
Technical/Professional Services | Scaled on MW
Outside Contract Services
Equipment rental
Miscellaneous
Basis: 13 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 28390.336
Instruments & Controls
Repair Parts | $3,375/yr x # of GT units | fixed | 6750
Outside Repair Services
Technical/Professional Services
Outside Contract Services
Equipment rental
Miscellaneous
Freight | 5% of 75% of total |  | 253.125
Basis: Vineland, NJ experience (1 x LM6000) |  | Sub-Total | 7003.125
Water Treatment System
Repair Parts | $9,816 x (production in kpph/180 kpph)^.6 |  | 6127.4952 | 155376
Outside Repair Services | scaled on throughput and hrs of operation
Technical/Professional Services
Outside Contract Labor
Equipment rental
Miscellaneous
Freight | 5% of 75% of total |  | 229.7811
Basis: Vineland, NJ experience (1 x LM6000) |  | Sub-Total | 6357.2762
Cooling System & Chillers
Repair Parts | Scaled on plant size |  | 43955.3965
Outside Repair Services | $179,000 x (plant size in MW/414MW)^.6 x 60%
Technical/Professional Services | multiplied by factor of 60% due to no STG at this plant
Outside Contract Labor
Equipment rental
Miscellaneous
Freight | 5% of 75% of total |  | 1648.3274
Basis: 13 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 45603.7239
Electrical/Substation/Interconnects
Repair Parts | Scaled on generator MW and # generators |  | 42831.1801
Electric Meter Calibration & Testing | Scaled cost = Labor Cost + Materials Cost
Outside Repair Services | Labor cost (25% of total) = 25% x $94,000
Technical/Professional Services | Material Cost (75% of total) = 75% x $94,000 x (# gens/4.5gens)
Outside Contract Labor | x (46.5MW/104MW)^0.6
Equipment rental
Miscellaneous
Freight | 5% of 11% of total |  | 235.5715
Basis: 13 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 43066.7516
Gas Turbines (excluding overhaul maint.)
Repair Parts | $35,000 x # of GTs | fixed | 70000
Outside Repair Services | $22,000/gt x #hrs ea yr/2000 hrs x # gts | variable | 35200
Technical/Professional Services | preventive and corrective maintenance, to include
Outside Contract Labor | semi-annual boroscope, calibration & inspection by GE staff
Equipment rental | assumed to cover a few routine TIL installations each year |  |  | .
Miscellaneous | Does not include a membership into the Lease Engine Program
Freight | 5% of 75% of total |  | 3945
Basis: Vineland, NJ experience (1 x LM6000 avg annual maint = $57,000 @ 2000 hrs) |  | Sub-Total | 109145
Selective Catalytic Reduction & Ammonia System
HRSG |  |  | 0 | 69750.5052
Chemical Feed system | $3500/yr x 8700hrs/2500 hrs |  | 0
Condensate system |  |  | 0
feedwater system | NOT IN SCOPE OF WORK |  | 0
Steam distribution system |  |  | 0
Auxiliary boiler | Assuming minimal usage each year |  | 0
SCR + Ammonia system | 2% of cost $1,200,000/unit x # units |  | 0
Freight |  |  | 0
Basis: OEC Vineland Experience |  | Sub-Total | 0
Steam Turbine (including Scheduled Maint.)
Non-scheduled maint. parts/repairs |  |  | 0
Outside Repair Services
Technical/Professional Services
Scheduled Maint.
Equipment rental
Miscellaneous | NOT IN SCOPE OF WORK
Auxiliary Parts
Freight |  |  | 0
|  | Sub-Total | 0
Potable Water System
Repair Parts |  |  | 1850
Outside Repair Services
Technical/Professional Services
Outside Contract Labor
Equipment rental
Miscellaneous
Freight |  |  | 69.375
Basis: OEC Vineland Experience |  | Sub-Total | 1919.375
Fuel Handling & Compression System
Repair Parts | system, metering, valves, piping |  | 2500
Outside Repair Services | Gas compression/yr |  | 30000
Technical/Professional Services
Outside Contract Labor
Equipment rental
Miscellaneous
Freight |  |  | 93.75
Basis: Vineland, NJ experience |  | Sub-Total | 32593.75
Miscellaneous Maintenance Expense
Warehouse Supplies |  |  | 10000
Vehicle Fuel/Gasoline
Vehicle Repairs & Maintenance
Vehicle Lease
Equipment/tools rental |  |  | 6000
Lubricants/Turbine Oil/Grease/Compounds |  |  | 10000
Tools & Tool Repair |  |  | 11000
Maint. Materials & Supplies |  |  | 10000
CEMS maint |  |  | 5000
Fire Protection System |  |  | 4000
Wastewater System |  |  | 5000
Instrument Air system |  |  | 500
Radio Parts and repairs
BOP Repairs
Hydrogen
Freight | 5% of 75% of total |  | 2306.25
Basis: OEC Vineland Experience |  | Sub-Total | 63806.25 | 325851.4877
O&M Annual Fee
Fixed Fee |  |  | 175000
|  | Sub-Total | 175000
Operator Overhead Charge (G&A)
This is included in benefits loading under payroll
0%
|  | Sub-Total | 0%
Major Equipment Maintenance Program (20 year total)
2826000
| $/Fired Hr for 20 year term is calculated as: | 44.1562
| Maintenance Accrual should be: | 56.52
|  | Sub-Total | 2826000
Commercial Office Expenses
Administrative/Technical |  |  | 0
NOT IN SCOPE OF WORK
Basis: |  | Sub-Total | 0
Sustaining Project Expenses
| 10% of procurement items |  | 22479.025
Basis: Eval team concensus |  | Sub-Total | 22479.025
Vehicular Fuel Usage
1 Trucks:
1 x gal/15 miles x $1.3/gal x 30,000 miles/yr |  |  | 2600
0 Van & 1 Flat-bed Truck:
2 x gal/ 10 miles x $1.5/gal x 20 miles/day x 365 days/year |  |  | 0
1 Forklifts:
1 x 2 gal/hr x $1.5/gal x 1 hr/day x 180 days/yr |  |  | 540
0 Crane:
5 gal/hr x $1.5/gal x 40 days/yr x 8 hours/day |  |  | 0
0 Crew Boats:
20 gal/hr x 1hr/30 miles x 30 miles x 2rd trips/d x365 days/yr x $1.5/gal x 2.0 (idle factor) |  |  | 0
THESE COSTS ARE ALREADY INCLUDED ABOVE IN "OFFICE SUPPLIES/EXPENSES"
Basis: |  | Sub-Total | 3140
Note:
1/ Fixed Maintenance costs are assumed to be 50% parts, 25% labor, 25% consumables.
0..

## Chem_Cost Backup Cooling Tower
St Peter, Illinois (Ameren) Power Project, Rev 0
Chemical Cost Detail
INSTRUCTIONS: Select the appropriate cooling water configuration (OT or CT); then choose a treatment option for that process.
Default treatment process is shock chlorination using gaseous chlorine (feed 3 hrs/day at 10 ppm).
|  | Expected project capacity factor, % (default = 100): |  | 18.2648 |  | Hrs/year: |  | 1600
Once through cooling water treatment calculations:
Treatment |  |  |  | Units/Million |  | Cost/Million |  | Million lb. |  | Process | OT Cooling
Process | Cost | /Unit | x | lb. Outlet | = | lb. Outlet | x | Outlet Water | = | Cost Per | Annual
|  |  |  | Water |  | Water |  | Per Year |  | Year | Cost
Chlorination: --Choose ONE ONLY of the following treatment options--
Chlorine Gas (3 hr/day @ 10 ppm) | 0.14 | /lb. | x | 1.25 | = | 0.175 | x | 0 | = | 0
Chlorine Gas, continuous feed @ 2 ppm | 0.14 | /lb. | x | 2 | = | 0.28 | x | 0 | = | 0
Hypochlorite solution feed (3 hr/day, 10ppm) | 1 | /gal | x | 1.25 | = | 1.25 | x | 0 | = | 0
Hypochlorite generation, (in situ) | 0.03 | /kWh | x |  | = | (NO CALC) | x | 0 | = | 0
PLEASE Input chlorination cost for selected option only:
Cooling tower treatment calculations: | [8 empty] | Selected Cycles of Concentration: | 3
Treatment |  |  |  | Units/Million |  | Cost/Million |  | Million lb. |  | Process | CT Cooling
Process | Cost | /Unit | x | lb. Outlet | = | lb. Outlet | x | Outlet Water | = | Cost Per | Annual
|  |  |  | Water |  | Water |  | Per Year |  | Year | Cost
Chlorination: --Choose ONE ONLY of the following treatment options--
Chlorine Gas (3 hr/day @ 10 ppm) | 0.14 | /lb. | x | 1.25 | = | 0.175 | x | 163.2 | = | 28.56
Chlorine Gas, continuous feed @ 2 ppm | 0.14 | /lb. | x | 2 | = | 0.28 | x | 163.2 | = | 45.696
Hypochlorite solution feed (3 hr/day, 10ppm) | 1 | /gal | x | 1.25 | = | 1.25 | x | 163.2 | = | 204
Hypochlorite generation, (in situ) | 0.03 | /kWh | x |  | = | (NO CALC) | x | 163.2 | = | 0
|  |  |  | PLEASE Input chlorination cost for selected option only: | [6 empty] | 204
Additional Cooling Tower Chemical Treatment
Scale inhibitor | 2.3 | /lb. | x | 10 | = | 23 | x | 163.2 | = | 3753.6
Solids dispersant polymer | 2.5 | /lb. | x | 5 | = | 12.5 | x | 163.2 | = | 2040
Acid feed for pH/scale control | 0.043 | /lb. | x | 150 | = | 6.45 | x | 163.2 | = | 1052.64
|  |  |  | Total additional chemical treatment costs: | [6 empty] | 6846.24
|  |  |  | Total annual treatment cost: | [6 empty] | 7050.24

## Chem_Cost Backup Demin
St Peter, Illinois (Ameren) Power Project, Rev 0
Chemical Cost Backup
|  |  |  | TOTAL STEAM PRODUCTION: |  | 0 | lbs/hour |  |  | MMlbs/year stm: | 0
|  |  |  | TOTAL BOILER FEEDWATER MAKE-UP REQUIREMENTS: |  | 0 | lbs/hour |  |  | MMlbs/year BFW: | 0
|  |  |  | TOTAL DEMIN. WATER PRODUCTION: |  | 52571.4286 | lbs/hour |  |  | MMlbs/year DI: | 84.1143
|  | Expected project capacity factor, % (default = 100): |  | 18.2648 |  | Hrs/year: |  | 1600
Treatment |  |  |  | Units/MMlbs |  | Cost/Million |  | Million lb. |  | Process | Total
Process | Cost | /Unit | x | OR | = | lb. Outlet | x | Outlet Water | = | Cost Per | Cost Per
|  |  |  | Units/year |  | Water |  | Per Year |  | Year | Year
Reverse Osmosis; pretreatment
Sulfuric Acid @ 93.2% H2SO4 | 0.043 | /lb. | x | 6.84 | = | 0.29412 | x | 120.2834 | = | 35.3778
Antiscalant | 2.36 | /lb. | x | 3.8 | = | 8.968 | x | 120.2834 | = | 1078.7018
[6 empty] | Reverse Osmosis Pretreat. Cost: |  |  |  | 1114.0795 | 1114.0795
Reverse Osmosis:
Electrical Power - H.P. Pump | 0.03 | /kWh | x |  | = | (NO CALC) | x | 120.2834 | = | (NO CALC)
Replacement Prefilter Cartridges | 2 | /TIE | x | 1.85 | = | 3.7 | x | 120.2834 | = | 445.0487
Replacement Membrane Elements | 700 | /Element | x | 11.015 | elements/yr (3 yr life) |  |  |  | = | 7710.4762
Membrane Cleaning Chemicals | 127 | /Elem./yr | x | 33.0449 | elements, total |  |  |  | = | 4196.702
[6 empty] | Reverse Osmosis Cost: |  |  |  | 12352.2269 | 12352.2269
Mixed Bed Ion Exchange
(Final Demineralization):
Sulfuric Acid @ 93.2% H2SO4 | 0.043 | /lb. | x | 29.2266 | = | 1.2567 | x | 92.5257 | = | 116.2812
Caustic soda @ 100% NaOH | 0.18 | /lb. | x | 31.8836 | = | 5.739 | x | 92.5257 | = | 531.0092
Replacement Cation Resin | 75 | /cu. ft. | x | 5.5358 | = | N/A | x | N/A | = | 415.1829
Replacement Anion Resin | 165 | /cu. ft. | x | 5.5358 | = | N/A | x | N/A | = | 913.4023
[6 empty] | Mixed Bed Ion Exchange Cost: |  |  |  | 1975.8756 | 1975.8756
Boiler/Steam Cycle treatment
Phosphate product (blended liquid) | 1.3 | /lb. | x | 10 | = | 13 | x | 0 | = | 0
Amine or amine blend | 2.7 | /lb. | x | 1 | = | 2.7 | x | 0 | = | 0
Non-hydrazine oxygen scavenger | 2.7 | /lb. | x | 0.5 | = | 1.35 | x | 0 | = | 0
[6 empty] | Total Boiler Chemical Cost: |  |  |  | 0 | 0
|  |  |  | Total annual treatment cost: | [6 empty] | 15442.1821
ASSUMPTIONS: | 1) Assumed TDS of groundwater = 1000 ppm (29.24 gr/gal cations + 29.24 gr/gal anions).
2) Assumed TDS to mixed beds after RO pretreatment = 20 ppm (0.585 gr/gal cations + 0.585 gr/gal anions).
3) DI plant configuration = 2 X 100% MB's (used to calculate resin replacement costs).
4) It is assumed that groundwater utilized for DI system make-up is NOT chlorinated (therefore, no chlorination nor
chlorine removal required); well water filtration requirements are minimal, thus no addt'l chemical costs.

## LM6000PC_MMR_Gas
St Peter, Illinois (Ameren) Power Project, Rev 0
GE LM6000 - Major Maintenance Reserve
Gas Fired Operation |  |  |  |  | Project Life |  | 20 | Years
Lease Club Membership Fees Not Included | [6 empty] | 2826000 | total cost
[7 empty] | 1413000 | cost per engine
Total Number of Installed Units |  |  | 2 |  |  |  | 70650 | cost per year per engine
[7 empty] | 44.1562 | cost per FIRED hour per engine
Inputs
Annual Lease Club Fees |  |  | 0 | per engine |  |  | $201,368 for LM6000 DLE (PD) & 20% increase for liquid fuel operation
Lease Engine Usage Fee |  |  | 83650 | per week (1-26 weeks) |  |  | 50,000 hour engine refurbishment assumes 16 week usage of lease engine
Preventative Maintenance |  |  | 0 | per year |  |  | Semi-Annual Preventative Maintenance included in annual O&M
Hot Section Refurbishment / 24,000 hrs |  |  | 1403000 | per GT |  |  | Rotable exchange for the hot section
Engine Refurbishment / 50,000 hrs |  |  | 3000000 | per GT |  |  | Depot level repair
Labor & Engineering / Hot Section |  |  | 10000 |  |  |  | Misc rentals, Freight, Travel & diem for GE personnel
Labor & Engineering / Major |  |  | 25000 |  |  |  | Misc rentals, Freight, Travel & diem for GE personnel
Dispatch |  | 1600 | Fired hrs/yr
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Hours (EOY) |  | 1600 | 3200 | 4800 | 6400 | 8000 | 9600 | 11200 | 12800 | 14400 | 16000 | 17600 | 19200 | 20800 | 22400 | 24000 | 25600 | 27200 | 28800 | 30400 | 32000
Maint Inspection (C, H or M) | [15 empty] | h
Comb., Hot Sec & Major Maint. Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2806000 | 0 | 0 | 0 | 0 | 0
Preventative Miantenance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Labor & Engineering | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 0 | 0 | 0 | 0 | 0
Lease Program |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Engine Usage Fee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yearly Totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2826000 | 0 | 0 | 0 | 0 | 0 | 2826000
Assumptions:
1. Hot Gas Path inspection conducted at 25,000 fired hour intervals and Major at 50,000 hour intervals.
2. Pricing in 2000 USD. Does not include escalation beyond that.
3. Assumes that Owner will not enter the Lease Engine Membership program.
4. Maintenance and lease costs from George Graham/GE Mar 2000 e-mail.
BASE LOAD CASE
Gas Fired Operation |  |  |  |  | Project Life |  | 20 | Years
Lease Club Membership Fees Included | [6 empty] | 28438800 | total cost
[7 empty] | 14219400 | cost per engine
Total Number of Installed Units |  |  | 1 |  |  |  | 710970 | cost per year
[7 empty] | 88.8713 | cost per FIRED hour
Inputs
Annual Lease Club Fees |  |  | 0 | per engine |  |  | $201,368 for LM6000 DLE (PD) & 20% increase for liquid fuel operation
Lease Engine Usage Fee |  |  | 23900 | per week (1-26 weeks) |  |  | 48,000 hour engine refurbishment assumes assumes 12 week usage of lease engine
Preventative Maintenance |  |  | 0 | per year |  |  | Semi-Annual Preventative Maintenance
Hot Section Refurbishment / 24,000 hrs |  |  | 1403000 | per GT | (rotable exchnage) |  | excludes DLE adder
Engine Refurbishment / 48,000 hrs |  |  | 3000000 | per GT |  |  | excluding 20% adder for DLN
Labor & Engineering / Hot Section |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Labor & Engineering / Major |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Dispatch |  | 8000 | Fired hrs/yr
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Hours (EOY) |  | 8000 | 16000 | 24000 | 32000 | 40000 | 48000 | 56000 | 64000 | 72000 | 80000 | 88000 | 96000 | 104000 | 112000 | 120000 | 128000 | 136000 | 144000 | 152000 | 160000
Maint Inspection (H or M) |  |  |  | H |  |  | M |  |  |  | H |  | M |  |  | H |  |  | M
Hot Sec & Major Maint. | 0 | 0 | 0 | 2806000 | 0 | 0 | 6000000 | 0 | 0 | 0 | 2806000 | 0 | 6000000 | 0 | 0 | 2806000 | 0 | 0 | 6000000 | 0 | 0
Preventative Miantenance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Labor & Engineering | 0 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0 | 0 | 50000 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0
Lease Program |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Engine Usage Fee | 0 | 0 | 0 | 0 | 0 | 0 | 573600 | 0 | 0 | 0 | 0 | 0 | 573600 | 0 | 0 | 0 | 0 | 0 | 573600 | 0 | 0
| 0 | 0 | 0 | 2856000 | 0 | 0 | 6623600 | 0 | 0 | 0 | 2856000 | 0 | 6623600 | 0 | 0 | 2856000 | 0 | 0 | 6623600 | 0 | 0
|  | 0 | 0 | 2856000 | 2856000 | 2856000 | 9479600 | 9479600 | 9479600 | 9479600 | 12335600 | 12335600 | 18959200 | 18959200 | 18959200 | 21815200 | 21815200 | 21815200 | 28438800 | 28438800 | 28438800
Assumptions:
1. Hot Gas Path inspection conducted at 25,000 fired hour intervals.
2. Major inspection conducted at 50,000 fired hour intervals.
3. Maintenance and lease costs from George Graham/Stewart & Stevenson 12/10/99 e-mail.