## Sheet1
Data Center Project
Latest Update: |  | 2001-01-12
Analysis of Baseline and Alternatives: 20 Years
Facility Parameters: Nominal
Size: |  | 100000 | sq. ft.
Cooling: |  | 3250 | tons
Data Processing: |  | 10600 | kW
Air Moving |  | 825 | kW
Condensing: |  | 3575 | kW
Total Power: |  | 15000 | kW
Assumptions: Most Probable
24 x 7 operation
N+2 design for air-conditioning and stand-by generators
Data processing elec. demand is constant
No air-side economizers
Negligible heat gains from building envelope and lighting
CO2 fire protection system in data center for all alternatives
70oF inlet, 110oF outlet from data processing equipment
Data processing equipment has internal cooling fans
15 interruptions of 12 hour duration in the summer under interruptable rate
Utility elec. service at 13.8 kV
N+1 design for 13.8 kV/480kV transformers and switchgear
Ambient outdoor air provides ventilation and 90% of cooling for fuel cells
0.3 inches water column external static pressure for air-handling units
0.8 power factor for utility electric power
SCADA/remote monitoring costs are equal for baseline and all alternatives
20 year economic life
$0 residual value at end of economic life
34% federal corporate income tax rate
No state corporate income tax
10% cost of capital
200% declining balance depreciation
10 year useful life for air-cooled refrigerant condensing and water chilling equipment
20 year useful life for water-cooled water chilling equipment
Unit Prices: Most Probable
Elec. Usage (Firm): |  | 0.06 | $/kWh
Elec. Demand (Firm): |  | 15 | $/kW/month
Elec. Usage (Inter.): |  | 0.05 | $/kWh
Elec. Demand (Inter.): |  | 3.75 | $/kW/month
Nat. Gas Usage: |  | 0.65 | $/therm
Diesel Fuel: |  | 1.4 | $/gal
Fuel Cell
Installed Cost: |  | 1900 | $/kW
Outdoor Condensing
Unit Installed Cost:
Cost: |  | 450 | $/ton
DX Evaporator Unit
Installed Cost: |  | 1.5 | $/cfm
13.8kV/480V Transformers
and Switchgear |  | 95 | $/kW
Emer. Genset
Installed Cost: |  | 500 | $/kW
UPS Installed Cost: |  | 1000 | $/kW
Absorbtion Chiller
Installed Cost |  | 650 | $/ton
Centrifugal Chiller
Installed Cost |  | 450 | $/ton
Cooling Tower
Installed Cost |  | 200 | $/ton
Condensing System
Elec. Demand at |  | 11 | EER
Design: |  | 1.1 | kW/ton
Air Handling Elec.
Demand |  | 0.25 | kW/ton
Fuel Cell Efficiency: |  | 0.5
Fuel Cell/UPS Loading: |  | 0.85
Reformer Efficiency: |  | 0.8
Fuel Cell Vent Rate: |  | 3.5 | cfm/kW
Direct-Fired Absorbtion Chiller (Double-Effect)
C.O.P. at Design: |  | 1
Centrifugal Chiller
Efficiency at Design |  | 0.55 | kW/ton
Emer. Generator
Efficiency at Design |  | 0.0713 | gal/kWh
Transformer Impedence
Loss |  | 0.025
Fuel Cell Maint. Cost |  | 6.5 | $/kW-yr
DX Condensing Unit
Maint. Cost |  | 2500 | $/unit-yr
13.8kV/480V Transformer
and Switchgear Maint |  | 2.5 | $/kW-yr
Emer. Generator Maint.
Cost |  | 3.5 | $/kW-yr
UPS Maint. Cost |  | 17.5 | $/kW-yr
Absorbtion Chiller Maint.
Cost |  | 7500 | $/unit-yr
Centrifugal Chiller Maint.
Cost |  | 7500 | $/unit-yr
Fan-Coil Unit Maint. Cost |  | 500 | $/unit-yr
Cooling Tower Maint. Cost |  | 5000 | $/unit/yr
Pump Maint Cost |  | 500 | $/unit/yr
Air-Cooled Screw Chiller
Maint Cost |  | 12500 | $/unit/yr
Analysis of Baseline:
Elec. DX air-conditioning with outdoor condensing units; utility elec. power;
UPS for data processing equip.; emergency generators for data processing
equipment and air-conditioning equipment
Size air-conditioning units: |  |  | 32.5 | tons
|  |  | 18055.5556 | cfm
No. air-conditioning units: |  |  | 102 | units
Capital for condensing units |  |  | 1491750 | $
Capital for evaporating units |  |  | 2762500 | $
Size emergency generators: |  |  | 1500 | kW
No. emergency generators: |  |  | 12 | units
Capital for emergency |  |  | 9000000 | $
generators:
Capital for UPS: |  |  | 12470588.2353 | $
Capital for 13.8/480 kV transformers
and switchgear |  |  | 2850000 | $
Capital for Air-Conditioning and
Power: |  |  | 28574838.2353 | $
Elec Usage and Demand:
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 1.1 | kW | 3250 | tons
Condensing Usage: |  |  | 7829250 | kWh
Condensing Demand |  |  | 3575 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 1 | kW | 3250 | tons
Condensing Usage: |  |  | 7117500 | kWh
Condensing Demand: |  |  | 3250 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 0.9 | kW | 3250 | tons
Condensing Usage: |  |  | 6405750 | kWh
Condensing Demand: |  |  | 2925 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.8 | kW | 3250 | tons
Condensing Usage: |  |  | 5694000 | kWh
Condensing Demand: |  |  | 2600 | kW
Annual Condensing Usage: |  |  | 27046500 | kWh/yr
Annual Air Moving Usage: |  |  | 7117500 | kWh/yr
Annual Data Procssing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage: |  |  | 130276923.0769 | kWh/yr
Annual Elec. Usage Cost: |  |  | 7816615.3846 | $/yr
Demand Cost:
Condensing Block 1: |  |  | 165000 | $
Condensing Block 2: |  |  | 150000 | $
Condensing Block 3: |  |  | 135000 | $
Condensing Block 4: |  |  | 120000 | $
Air-Moving: |  |  | 150000 | $
Data Processing: |  |  | 1956923.0769 | $
Annual Elec. Demand Cost: |  |  | 2676923.0769 | $/yr
Annual Elec. Cost: |  |  | 10493538.4615 | $/yr
Air-Cooled Condensing Units |  |  | 255000 | $/yr
DX Evaporating Units |  |  | 51000 | $/yr
Air-Conditioning Sub-total |  |  | 306000 | $/yr
Emer. Generators |  |  | 63000 | $/yr
UPS |  |  | 218235.2941 | $/yr
13.8kV/480V transformers and switches |  |  | 75000 | $/yr
Power Conversion Sub-total |  |  | 356235.2941 | $/yr
Annual Maint. Cost |  |  | 662235.2941 | $/yr
Analysis of Alternative 1:
Elec. DX air-conditioning with outdoor condensing units; power from
fuel cells installed inside data processing space for data-processing
and air-conditioning equipment; waste heat from fuel cells vented
to atmosphere
Cooling for data processing |  |  | 3250 | tons
and air-moving:
Cooling for fuel cell heat losses |  |  | 213.25 | tons
to data processing space
Total cooling load: |  |  | 3463.25 | tons
Size condensing units: |  |  | 34.63 | tons
|  |  | 18322.7513 | cfm
No. air-conditioning units: |  |  | 102.0072 | units
Capital for condensing units |  |  | 1589629.5 | $
Capital for evaporating units |  |  | 2803579.3651 | $
Demand for condensing: |  |  | 3809.575 | kW
Demand for air moving |  |  | 865.8125 | kW
Demand for data processing: |  |  | 10600 | kW
Total demand (fuel cells): |  |  | 15275.3875 | kW
Capital for fuel cells: |  |  | 34144983.8235 | $
Capital for air-conditioning
and power: |  |  | 38538192.6886 | $
Elec Usage and Demand:
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 1.1 | kW | 3463.25 | tons
Condensing Usage: |  |  | 8342969.25 | kWh
Condensing Demand: |  |  | 3809.575 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 1.05 | kW | 3463.25 | tons
Condensing Usage: |  |  | 7963743.375 | kWh
Condensing Demand: |  |  | 3636.4125 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 1 | kW | 3463.25 | tons
Condensing Usage: |  |  | 7584517.5 | kWh
Condensing Demand: |  |  | 3463.25 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.95 | kW | 3463.25 | tons
Condensing Usage: |  |  | 7205291.625 | kWh
Condensing Demand: |  |  | 3290.0875 | kW
Annual Condensing Usage: |  |  | 31096521.75 | kWh/yr
Annual Air Moving Usage: |  |  | 7584517.5 | kWh/yr
Annual Data Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage: |  |  | 131537039.25 | kWh/yr
Annual Natural Gas Usage: |  |  | 11220109.448 | therm/yr
Annual Natural Gas Cost: |  |  | 7293071.1412 | $/yr
Air-Cooled Condensing Units |  |  | 255018.0479 | $/yr
DX Evaporating Units |  |  | 51003.6096 | $/yr
Air-Conditioning Sub-total |  |  | 306021.6575 | $/yr
Fuel Cells |  |  | 116811.7868 | $/yr
Power Conversion Sub-total |  |  | 116811.7868 | $/yr
Annual Maint. Cost |  |  | 422833.4443 | $/yr
Analysis of Alternative 2:
Elec. DX air-conditioning with outdoor condensing units; power from
fuel cells installed inside data processing space for data-processing
equipment; waste heat from fuel cells vented to atmosphere;
utility elec. power and emergency generators for air-conditioning
equipment
Cooling for data processing |  |  | 3250 | tons
and air moving:
Cooling for fuel cell heat losses |  |  | 150.6967 | tons
to data processing space
Total cooling load: |  |  | 3400.6967 | tons
Size condensing units: |  |  | 34.01 | tons
|  |  | 17994.709 | cfm
No. air-conditioning units: |  |  | 101.9911 | units
Capital for condensing units |  |  | 1560922.5 | $
Capital for evaporating units |  |  | 2752949.7354 | $
Demand for condensing: |  |  | 3740.7663 | kW
Demand for air moving |  |  | 850.1742 | kW
Total demand (emer. generators) |  |  | 4590.9405 | kW
Size emergency generators: |  |  | 1530 | kW
No. emer. generators: |  |  | 5.0006 | units
Capital for emer. generators |  |  | 3825470.25 | $
Capital for 13.8kV/480V transformers |  |  | 872278.695 | $
and switchgear
Demand for data processing: |  |  | 10600 | kW
Total demand (fuel cells): |  |  | 10600 | kW
Capital for fuel cells: |  |  | 23694117.6471 | $
Capital for air-conditioning
and power: |  |  | 32705738.8275 | $
Elec Usage and Demand (Utility):
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 1.1 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 8192278.27 | kWh
Condensing Demand: |  |  | 3740.7663 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 1.05 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7819901.985 | kWh
Condensing Demand: |  |  | 3570.7315 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 1 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7447525.7 | kWh
Condensing Demand: |  |  | 3400.6967 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.95 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7075149.415 | kWh
Condensing Demand: |  |  | 3230.6618 | kW
Annual Condensing Usage: |  |  | 30534855.37 | kWh/yr
Annual Air Moving Usage: |  |  | 7447525.7 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 37982381.07 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 2337377.2966 | $/yr
Demand Cost:
Condensing Block 1: |  |  | 172650.7538 | $
Condensing Block 2: |  |  | 164802.9923 | $
Condensing Block 3: |  |  | 156955.2308 | $
Condensing Block 4: |  |  | 149107.4692 | $
Air-Moving: |  |  | 156955.2308 | $
Annual Elec. Demand Cost (Utility): |  |  | 800471.6769 | $/yr
Annual Elec. Cost (Utility): |  |  | 3137848.9735 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Annual Energy Cost: |  |  | 8286249.8935 | $/yr
Air-Cooled Condensing Units |  |  | 254977.7026 | $/yr
DX Evaporating Units |  |  | 50995.5405 | $/yr
Air-Conditioning Sub-total |  |  | 305973.2432 | $/yr
Emer. Generators |  |  | 26778.2918 | $/yr
13.8kV/480V transformers and switches |  |  | 22954.7025 | $/yr
Fuel Cells |  |  | 81058.8235 | $/yr
Power Conversion Sub-total |  |  | 130791.8178 | $/yr
Annual Maint. Cost |  |  | 436765.0609 | $/yr
Analysis of Alternative 3:
Elec. air-conditioning with water-cooled centrifugal chillers; power from
fuel cells installed inside data processing space for data-processing
equipment; waste heat from fuel cells vented to atmosphere;
utility elec. power and emergency generators for air-conditioning
equipment
Cooling for data processing |  |  | 3250 | tons
and air moving
Cooling for fuel cell heat losses |  |  | 150.6967 | tons
to data processing space
Total cooling load: |  |  | 3400.6967 | tons
Size fan-coil units: |  |  | 34.01 | tons
|  |  | 17994.709 | cfm
No. air-conditioning units: |  |  | 101.9911 | units
Capital for fan-coil units |  |  | 2752949.7354 | $
Size centrifugal chillers |  |  | 1134 | tons
No. centrifugal chillers |  |  | 4.9989 | units
Capital for centrifugal chillers |  |  | 2550913.5 | $
Capital for cooling towers |  |  | 1133739.3333 | $
Demand for air-conditioning:
Cent. Chillers |  |  | 1870.3832 | kW
Evap. Pumps |  |  | 225 | kW
Cond. Pumps |  |  | 168.75 | kW
Clg. Twr. Fans |  |  | 112.5 | kW
Fan-Coil Units |  |  | 850.1742 | kW
Sub-total |  |  | 3226.8073 | kW
Total demand (emer. generators) |  |  | 3226.8073 | kW
Size emergency generators: |  |  | 1075 | kW
No. emer. generators: |  |  | 5.0017 | units
Capital for emer. generators |  |  | 2688403.6667 | $
Capital for 13.8kV/480V transformers |  |  | 613093.3933 | $
and switchgear
Demand for data processing: |  |  | 10600 | kW
Total demand (fuel cells): |  |  | 10600 | kW
Capital for fuel cells: |  |  | 23694117.6471 | $
Capital for air-conditioning
and power: |  |  | 33433217.2758 | $
Elec Usage and Demand (Utility):
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 0.55 | kW | 3400.6967 | tons
Water Chilling Usage: |  |  | 4096139.135 | kWh
Water Chilling Demand: |  |  | 1870.3832 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 0.475 | kW | 3400.6967 | tons
Water Chilling Usage: |  |  | 3537574.7075 | kWh
Water Chilling Demand: |  |  | 1615.3309 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 0.4 | kW | 3400.6967 | tons
Water Chilling Usage: |  |  | 2979010.28 | kWh
Water Chilling Demand: |  |  | 1360.2787 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.325 | kW | 3400.6967 | tons
Water Chilling Usage |  |  | 2420445.8525 | kWh
Water Chilling Demand |  |  | 1105.2264 | kW
Annual Water Chilling Usage: |  |  | 13033169.975 | kWh/yr
Annual Air Moving Usage: |  |  | 7447525.7 | kWh/yr
Evap. Pumps |  |  | 1971000 | kWh/yr
Cond. Pumps |  |  | 1478250 | kWh/yr
Clg. Twr. Fans |  |  | 985500 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 24915445.675 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 1533258.1954 | $/yr
Demand Cost:
Water Chilling Block 1: |  |  | 86325.3769 | $
Water Chilling Block 2: |  |  | 74553.7346 | $
Water Chilling Block 3: |  |  | 62782.0923 | $
Water Chilling Block 4: |  |  | 51010.45 | $
Air-Moving: |  |  | 156955.2308 | $
Evap. Pumps: |  |  | 41538.4615 | $
Cond. Pumps: |  |  | 31153.8462 | $
Clg. Twr. Pumps: |  |  | 20769.2308 | $
Annual Elec. Demand Cost (Utility): |  |  | 525088.4231 | $/yr
Annual Elec. Cost (Utility): |  |  | 2058346.6185 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Annual Energy Cost: |  |  | 7206747.5385 | $/yr
Centrifugal Chillers |  |  | 37491.3801 | $/yr
Fan-Coil Units |  |  | 50995.5405 | $/yr
Cooling Towers |  |  | 24994.2534 | $/yr
Pumps |  |  | 4998.8507 | $/yr
Air-Conditioning Sub-total |  |  | 118480.0247 | $/yr
Emer. Generators |  |  | 18818.8257 | $/yr
13.8kV/480V transformers and switches |  |  | 16134.0367 | $/yr
Fuel Cells |  |  | 81058.8235 | $/yr
Power Conversion Sub-total |  |  | 116011.6859 | $/yr
Annual Maint. Cost |  |  | 234491.7105 | $/yr
Analysis of Alternative 4:
Same as Alternative 3 except add one absorbtion chiller and cooling
tower to utilize the nat. gas not converted by the hydrogen reformers;
delete one centrifugal chiller and one emer. generator
Nat. Gas not converted to hydrogen: |  |  | 1584123.36 | therm/yr
Heat available for water chilling: |  |  | 18083600 | btu/hr
Water chilling by abs. chiller: |  |  | 1506.9667 | tons
Size absorbtion chillers: |  |  | 753.5 | tons
No. absorbtion chillers: |  |  | 2 | units
Additional capital for abs. chiller: |  |  | 979550 | $
Additional capital for cooling tower: |  |  | 301400 | $
Additional capital (total): |  |  | 1280950 | $
Capital reduction for cent. chiller |  |  | 510300 | $
Capital reduction for emer. generator |  |  | 537500 | $
Capital reduction for 13.8kV/480V |  |  | 118503 | $
transformer and switchgear
Capital reduction (total): |  |  | 1166303 | $
Capital reduction (net): |  |  | 114647 | $
Capital for air-conditioning |  |  | 33547864.2758 | $
and power:
Elec Usage and Demand (Utility):
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 0.55 | kW | 1506.9667 | tons
Water Chilling Usage: |  |  | 1815141.35 | kWh
Water Chilling Demand: |  |  | 828.8317 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 0.475 | kW | 1506.9667 | tons
Water Chilling Usage: |  |  | 1567622.075 | kWh
Water Chilling Demand: |  |  | 715.8092 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 0.4 | kW | 1506.9667 | tons
Water Chilling Usage: |  |  | 1320102.8 | kWh
Water Chilling Demand: |  |  | 602.7867 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.325 | kW | 1506.9667 | tons
Water Chilling Usage |  |  | 1072583.525 | kWh
Water Chilling Demand |  |  | 489.7642 | kW
Reduced Water Chilling Usage: |  |  | 5775449.75 | kWh/yr
Additional Clg. Twr. Fan Usage |  |  | 328500 | kWh/yr
Reduced Air-Cond. Usage (Net) |  |  | 5446949.75 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 19468495.925 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 1198061.2877 | $/yr
Demand Cost:
Water Chilling Block 1: |  |  | 38253.7692 | $
Water Chilling Block 2: |  |  | 33037.3462 | $
Water Chilling Block 3: |  |  | 27820.9231 | $
Water Chilling Block 4: |  |  | 22604.5 | $
Reduced Water Chilling Demand |  |  | 121716.5385 | $
Addl. Clg. Twr. Fan Demand |  |  | 6923.0769 | $
Reduced Air-Cond. Demand (Net): |  |  | 114793.4615 | $
Annual Elec. Demand Cost (Utility): |  |  | 410294.9615 | $/yr
Annual Elec. Cost (Utility): |  |  | 1608356.2492 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Annual Energy Cost: |  |  | 6756757.1692 | $/yr
Centrifugal Chillers |  |  | 29991.3801 | $/yr
Absorbtion chillers |  |  | 15000 | $/yr
Fan-Coil Units |  |  | 50995.5405 | $/yr
Cooling Towers |  |  | 39994.2534 | $/yr
Pumps |  |  | 5998.8507 | $/yr
Air-Conditioning Sub-total |  |  | 141980.0247 | $/yr
Emer. Generators |  |  | 15056.3257 | $/yr
13.8kV/480V transformers and switches |  |  | 13015.5367 | $/yr
Fuel Cells |  |  | 81058.8235 | $/yr
Power Conversion Sub-total |  |  | 109130.6859 | $/yr
Annual Maint. Cost |  |  | 251110.7105 | $/yr
Analysis of Alternative 5:
Same as Alternative 4 except utility elec. power for air-conditioning
will be at interruptable (reduced) rate; operate emer. generators during
interruptions
Capital for air-conditioning |  |  | 33547864.2758 | $
and power:
Annual Air-Conditioning Usage: |  |  | 19468495.925 | kWh/yr
Reduced Water Chilling Usage: |  |  | 5775449.75 | kWh/yr
Additional Clg. Twr. Fan Usage |  |  | 328500 | kWh/yr
Reduced Air-Cond. Usage (Net) |  |  | 5446949.75 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 14021546.175 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 719053.65 | $/yr
Demand Cost:
Water Chilling Block 1: |  |  | 21581.3442 | $
Water Chilling Block 2: |  |  | 18638.4337 | $
Water Chilling Block 3: |  |  | 15695.5231 | $
Water Chilling Block 4: |  |  | 12752.6125 | $
Air-Moving: |  |  | 39238.8077 | $
Evap. Pumps: |  |  | 10384.6154 | $
Cond. Pumps: |  |  | 7788.4615 | $
Clg. Twr. Pumps: |  |  | 5192.3077 | $
Annual Elec. Demand Cost (Utility): |  |  | 131272.1058 | $/yr
Demand Cost:
Water Chilling Block 1: |  |  | 9563.4423 | $
Water Chilling Block 2: |  |  | 8259.3365 | $
Water Chilling Block 3: |  |  | 6955.2308 | $
Water Chilling Block 4: |  |  | 5651.125 | $
Reduced Water Chilling Demand |  |  | 30429.1346 | $
Addl. Clg. Twr. Fan Demand |  |  | 1730.7692 | $
Reduced Air-Cond. Demand (Net): |  |  | 28698.3654 | $
Annual Elec. Demand Cost (Utility): |  |  | 102573.7404 | $/yr
Annual Elec. Cost (Utility): |  |  | 821627.3904 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Summer Elec. Demand (Utility): |  |  | 2435.4757 | kW
Annual Diesel Usage: |  |  | 31256.8947 | gal/yr
Annual Diesel Cost: |  |  | 43759.6526 | $/yr
Annual Energy Cost: |  |  | 6013787.963 | $/yr
Annual Maint Cost: |  |  | 251110.7105 | $/yr
Analysis of Alternative 6:
Same as Alternative 2 except utility elec. power for air-conditioning
will be at interruptable (reduced) rate; operate emer. generators during
interruptions
Capital for air-conditioning |  |  | 32705738.8275
and power:
Elec Usage and Demand (Utility):
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 1.1 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 8192278.27 | kWh
Condensing Demand: |  |  | 3740.7663 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 1.05 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7819901.985 | kWh
Condensing Demand: |  |  | 3570.7315 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 1 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7447525.7 | kWh
Condensing Demand: |  |  | 3400.6967 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.95 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7075149.415 | kWh
Condensing Demand: |  |  | 3230.6618 | kW
Annual Condensing Usage: |  |  | 30534855.37 | kWh/yr
Annual Air Moving Usage: |  |  | 7447525.7 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 37982381.07 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 1947814.4138 | $/yr
Demand Cost:
Condensing Block 1: |  |  | 43162.6885 | $
Condensing Block 2: |  |  | 41200.7481 | $
Condensing Block 3: |  |  | 39238.8077 | $
Condensing Block 4: |  |  | 37276.8673 | $
Air-Moving: |  |  | 39238.8077 | $
Annual Elec. Demand Cost (Utility): |  |  | 200117.9192 | $/yr
Annual Elec. Cost (Utility): |  |  | 2147932.3331 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Summer Elec. Demand (Utility): |  |  | 3740.7663 | kW
Annual Diesel Usage: |  |  | 48008.9951 | gal/yr
Annual Diesel Cost: |  |  | 67212.5932 | $/yr
Annual Energy Cost: |  |  | 7363545.8462 | $/yr
Ammual Maint Cost: |  |  | 436765.0609 | $/yr
Analysis of Alternative 7:
Same as Alternative 3 except utility elec. power for air-conditioning
will be at interruptable (reduced) rate; operate emer. generators during
interruptions
Capital for air-conditioning |  |  | 33433217.2758 | $
and power:
Elec Usage and Demand (Utility):
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 0.55 | kW | 3400.6967 | tons
Water Chilling Usage: |  |  | 4096139.135 | kWh
Water Chilling Demand: |  |  | 1870.3832 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 0.475 | kW | 3400.6967 | tons
Water Chilling Usage: |  |  | 3537574.7075 | kWh
Water Chilling Demand: |  |  | 1615.3309 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 0.4 | kW | 3400.6967 | tons
Water Chilling Usage: |  |  | 2979010.28 | kWh
Water Chilling Demand: |  |  | 1360.2787 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.325 | kW | 3400.6967 | tons
Water Chilling Usage |  |  | 2420445.8525 | kWh
Water Chilling Demand |  |  | 1105.2264 | kW
Annual Water Chilling Usage: |  |  | 13033169.975 | kWh/yr
Annual Air Moving Usage: |  |  | 7447525.7 | kWh/yr
Evap. Pumps |  |  | 1971000 | kWh/yr
Cond. Pumps |  |  | 1478250 | kWh/yr
Clg. Twr. Fans |  |  | 985500 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 24915445.675 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 1277715.1628 | $/yr
Demand Cost:
Water Chilling Block 1: |  |  | 21581.3442 | $
Water Chilling Block 2: |  |  | 18638.4337 | $
Water Chilling Block 3: |  |  | 15695.5231 | $
Water Chilling Block 4: |  |  | 12752.6125 | $
Air-Moving: |  |  | 39238.8077 | $
Evap. Pumps: |  |  | 10384.6154 | $
Cond. Pumps: |  |  | 7788.4615 | $
Clg. Twr. Pumps: |  |  | 5192.3077 | $
Annual Elec. Demand Cost (Utility): |  |  | 131272.1058 | $/yr
Annual Elec. Cost (Utility): |  |  | 1408987.2686 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Summer Elec. Demand (Utility): |  |  | 3226.8073 | kW
Annual Diesel Usage: |  |  | 41412.8453 | gal/yr
Annual Diesel Cost: |  |  | 57977.9834 | $/yr
Annual Energy Cost: |  |  | 6557388.1886 | $/yr
Annual Maint Cost: |  |  | 234491.7105 | $/yr
Analysis of Alternative 8:
Elec. air-conditioning with air-cooled screw chillers; power from
fuel cells installed inside data processing space for data-processing
equipment; waste heat from fuel cells vented to atmosphere;
utility elec. power and emergency generators for air-conditioning
equipment
Cooling for data processing |  |  | 3250 | tons
and air moving
Cooling for fuel cell heat losses |  |  | 150.6967 | tons
to data processing space
Total cooling load: |  |  | 3400.6967 | tons
Size fan-coil units: |  |  | 34.01 | tons
|  |  | 17994.709 | cfm
No. air-conditioning units: |  |  | 101.9911 | units
Capital for fan-coil units |  |  | 2752949.7354 | $
Size air-cooled screw chillers |  |  | 425 | tons
No. air-cooled screw chillers |  |  | 10.0016 | units
Capital for screw chillers |  |  | 1912813.5 | $
Demand for water chilling: |  |  | 3740.7663 | kW
Demand for water pumping: |  |  | 240 | kW
Demand for air moving |  |  | 850.1742 | kW
Total demand (emer. generators) |  |  | 4830.9405 | kW
Size emergency generators: |  |  | 1610 | kW
No. emer. generators: |  |  | 5.0006 | units
Capital for emer. generators |  |  | 4025470.25 | $
Capital for 13.8kV/480V transformers |  |  | 917878.695 | $
and switchgear
Demand for data processing: |  |  | 10600 | kW
Total demand (fuel cells): |  |  | 10600 | kW
Capital for fuel cells: |  |  | 23694117.6471 | $
Capital for air-conditioning |  |  | 33303229.8275 | $
and power:
Elec Usage and Demand (Utility):
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 1.1 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 8192278.27 | kWh
Condensing Demand: |  |  | 3740.7663 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 1.05 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7819901.985 | kWh
Condensing Demand: |  |  | 3570.7315 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 1 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7447525.7 | kWh
Condensing Demand: |  |  | 3400.6967 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.95 | kW | 3400.6967 | tons
Condensing Usage: |  |  | 7075149.415 | kWh
Condensing Demand: |  |  | 3230.6618 | kW
Annual Condensing Usage: |  |  | 30534855.37 | kWh/yr
Annual Air Moving Usage: |  |  | 7447525.7 | kWh/yr
Annual Water Pumping Usage: |  |  | 2102400 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 40084781.07 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 2466755.7582 | $/yr
Demand Cost:
Condensing Block 1: |  |  | 172650.7538 | $
Condensing Block 2: |  |  | 164802.9923 | $
Condensing Block 3: |  |  | 156955.2308 | $
Condensing Block 4: |  |  | 149107.4692 | $
Air-Moving: |  |  | 156955.2308 | $
Water Pumping |  |  | 44307.6923 | $
Annual Elec. Demand Cost (Utility): |  |  | 844779.3692 | $/yr
Annual Elec. Cost (Utility): |  |  | 3311535.1274 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Annual Energy Cost: |  |  | 8459936.0474 | $/yr
Air-Cooled Screw Chillers |  |  | 125020.4902 | $/yr
Fan-Coil Units |  |  | 50995.5405 | $/yr
Pumps |  |  | 5000.8196 | $/yr
Air-Conditioning Sub-total |  |  | 181016.8503 | $/yr
Emer. Generators |  |  | 28178.2918 | $/yr
13.8kV/480V transformers and switches |  |  | 24154.7025 | $/yr
Fuel Cells |  |  | 81058.8235 | $/yr
Power Conversion Sub-total |  |  | 133391.8178 | $/yr
Annual Maint. Cost |  |  | 314408.6681 | $/yr
Analysis of Alternative 9:
Same as Alternative 8 except add two absorbtion chillers and cooling
towers to utilize the nat. gas not converted by the hydrogen reformers;
reduce air-cooled screw chillers and emer. generators
Nat. Gas not converted to hydrogen: |  |  | 1584123.36 | therm/yr
Heat available for water chilling: |  |  | 18083600 | btu/hr
Water chilling by abs. chiller: |  |  | 1506.9667 | tons
Size absorbtion chillers: |  |  | 753.5 | tons
No. absorbtion chillers: |  |  | 2 | units
Additional capital for abs. chiller: |  |  | 979550 | $
Additional capital for cooling tower: |  |  | 602800 | $
Additional capital (total): |  |  | 1582350 | $
Capital reduction for screw chillers |  |  | 382500 | $
Capital reduction for emer. generator |  |  | 467500 | $
Capital reduction for 13.8kV/480V |  |  | 177650 | $
transformers and switchgear
Capital reduction (total): |  |  | 1027650 | $
Capital reduction (net): |  |  | 554700 | $
Capital for air-conditioning |  |  | 33857929.8275 | $
and power:
Elec Usage and Demand (Utility):
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 1.1 | kW | 1506.9667 | tons
Water Chilling Usage: |  |  | 3630282.7 | kWh
Water Chilling Demand: |  |  | 1657.6633 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 1.05 | kW | 1506.9667 | tons
Water Chilling Usage: |  |  | 3465269.85 | kWh
Water Chilling Demand: |  |  | 1582.315 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 1 | kW | 1506.9667 | tons
Water Chilling Usage: |  |  | 3300257 | kWh
Water Chilling Demand: |  |  | 1506.9667 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.95 | kW | 1506.9667 | tons
Water Chilling Usage |  |  | 3135244.15 | kWh
Water Chilling Demand |  |  | 1431.6183 | kW
Reduced Water Chilling Usage: |  |  | 13531053.7 | kWh/yr
Additional Clg. Twr. Fan Usage |  |  | 657000 | kWh/yr
Additional Cond. Wtr. Pump Usage |  |  | 657000 | kWh/yr
Reduced Air-Cond. Usage (Net) |  |  | 12217053.7 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 27867727.37 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 1714937.0689 | $/yr
Demand Cost:
Water Chilling Block 1: |  |  | 76507.5385 | $
Water Chilling Block 2: |  |  | 73029.9231 | $
Water Chilling Block 3: |  |  | 69552.3077 | $
Water Chilling Block 4: |  |  | 66074.6923 | $
Reduced Water Chilling Demand |  |  | 285164.4615 | $
Addl. Clg. Twr. Fan Demand |  |  | 13846.1538 | $
Addl. Cond. Wtr. Pump Demand |  |  | 13846.1538 | $
Reduced Air-Cond. Demand (Net): |  |  | 257472.1538 | $
Annual Elec. Demand Cost (Utility): |  |  | 587307.2154 | $/yr
Annual Elec. Cost (Utility): |  |  | 2302244.2843 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Annual Energy Cost: |  |  | 7450645.2043 | $/yr
Air-Cooled Screw Chillers |  |  | 100020.4902 | $/yr
Absorbtion chillers |  |  | 15000 | $/yr
Fan-Coil Units |  |  | 50995.5405 | $/yr
Cooling Towers |  |  | 20000 | $/yr
Pumps |  |  | 6000.8196 | $/yr
Air-Conditioning Sub-total |  |  | 192016.8503 | $/yr
Emer. Generators |  |  | 24905.7918 | $/yr
13.8kV/480V transformers and switches |  |  | 21817.2025 | $/yr
Fuel Cells |  |  | 7272.3529 | $/yr
Power Conversion Sub-total |  |  | 53995.3472 | $/yr
Annual Maint. Cost |  |  | 246012.1975 | $/yr
Analysis of Alternative 10:
Same as Alternative 9 except utility elec. power for air-conditioning
will be at interruptable (reduced) rate; operate emer. generators during
interruptions
Capital for air-conditioning |  |  | 33857929.8275 | $
and power:
Annual Air-Conditioning Usage: |  |  | 27867727.37 | kWh/yr
Annual Elec. Usage Cost (Utility): |  |  | 1429114.2241 | $/yr
Demand Cost:
Water Chilling Block 1: |  |  | 43162.6885 | $
Water Chilling Block 2: |  |  | 41200.7481 | $
Water Chilling Block 3: |  |  | 39238.8077 | $
Water Chilling Block 4: |  |  | 37276.8673 | $
Air-Moving: |  |  | 39238.8077 | $
Evap. Pumps: |  |  | 11076.9231 | $
Annual Elec. Demand Cost (Utility): |  |  | 211194.8423 | $/yr
Demand Cost:
Water Chilling Block 1: |  |  | 19126.8846 | $
Water Chilling Block 2: |  |  | 18257.4808 | $
Water Chilling Block 3: |  |  | 17388.0769 | $
Water Chilling Block 4: |  |  | 16518.6731 | $
Reduced Water Chilling Demand |  |  | 71291.1154 | $
Addl. Clg. Twr. Fan Demand |  |  | 3461.5385 | $
Addl. Cond. Wtr. Pump Demand |  |  | 3461.5385 | $
Reduced Air-Cond. Demand (Net): |  |  | 64368.0385 | $
Annual Elec. Demand Cost (Utility): |  |  | 146826.8038 | $/yr
Annual Elec. Cost (Utility): |  |  | 1575941.0279 | $/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 92856000 | kWh/yr
Annual Natural Gas Usage: |  |  | 7920616.8 | therm/yr
Annual Natural Gas Cost: |  |  | 5148400.92 | $/yr
Summer Elec. Demand (Utility): |  |  | 4980.9405 | kW
Annual Diesel Usage: |  |  | 63925.3904 | gal/yr
Annual Diesel Cost: |  |  | 89495.5465 | $/yr
Annual Energy Cost: |  |  | 6813837.4945 | $/yr
Annual Maint Cost: |  |  | 246012.1975 | $/yr
Analysis of Alternative 11:
Elec. air-conditioning with water-cooled centrifugal chillers; power from
fuel cells installed inside data processing space for data-processing
and air-conditioning equipment; waste heat from fuel cells vented
to atmosphere
Cooling for data processing |  |  | 3250 | tons
and air-moving:
Cooling for fuel cell heat losses |  |  | 213.25 | tons
to data processing space
Total cooling load: |  |  | 3463.25 | tons
Size fan-coil units: |  |  | 34.63 | tons
|  |  | 18322.7513 | cfm
No. air-conditioning units: |  |  | 102.0072 | units
Capital for fan-coil units |  |  | 2803579.3651 | $
Size centrifugal chillers |  |  | 1154 | tons
No. centrifugal chillers |  |  | 5.0011 | units
Capital for centrifugal chillers |  |  | 2597062.5 | $
Capital for cooling towers |  |  | 1154250 | $
Demand for air-conditioning:
Cent. Chillers |  |  | 1904.7875 | kW
Evap. Pumps |  |  | 225 | kW
Cond. Pumps |  |  | 168.75 | kW
Clg. Twr. Fans |  |  | 112.5 | kW
Fan-Coil Units |  |  | 865.8125 | kW
Data Processing |  |  | 10600 | kW
Total demand (fuel cells) |  |  | 13876.85 | kW
Capital for fuel cells: |  |  | 31018841.1765 | $
Capital for air-conditioning
and power: |  |  | 37573733.0415 | $
Elec Usage and Demand (Utility):
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 0.55 | kW | 3463.25 | tons
Water Chilling Usage: |  |  | 4171484.625 | kWh
Water Chilling Demand: |  |  | 1904.7875 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 0.475 | kW | 3463.25 | tons
Water Chilling Usage: |  |  | 3602645.8125 | kWh
Water Chilling Demand: |  |  | 1645.0438 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 0.4 | kW | 3463.25 | tons
Water Chilling Usage: |  |  | 3033807 | kWh
Water Chilling Demand: |  |  | 1385.3 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.325 | kW | 3463.25 | tons
Water Chilling Usage |  |  | 2464968.1875 | kWh
Water Chilling Demand |  |  | 1125.5563 | kW
Annual Water Chilling Usage: |  |  | 13272905.625 | kWh/yr
Annual Air Moving Usage: |  |  | 7584517.5 | kWh/yr
Evap. Pumps |  |  | 1971000 | kWh/yr
Cond. Pumps |  |  | 1478250 | kWh/yr
Clg. Twr. Fans |  |  | 985500 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 25292173.125 | kWh/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 118148173.125 | kWh/yr
Annual Natural Gas Usage: |  |  | 10078039.1676 | therm/yr
Annual Natural Gas Cost: |  |  | 6550725.4589 | $/yr
Annual Energy Cost: |  |  | 6550725.4589 | $/yr
Centrifugal Chillers |  |  | 37508.1239 | $/yr
Fan-Coil Units |  |  | 51003.6096 | $/yr
Cooling Towers |  |  | 25005.4159 | $/yr
Pumps |  |  | 5001.0832 | $/yr
Air-Conditioning Sub-total |  |  | 118518.2326 | $/yr
Fuel Cells |  |  | 106117.0882 | $/yr
Power Conversion Sub-total |  |  | 106117.0882 | $/yr
Annual Maint. Cost |  |  | 224635.3209 | $/yr
Analysis of Alternative 12:
Same as Alternative 11 except add one absorbtion chiller and cooling
tower to utilize the nat. gas not converted by the hydrogen reformers;
delete one centrifugal chiller
Nat. Gas not converted to hydrogen: |  |  | 1902850 | therm/yr
Heat available for water chilling: |  |  | 21722031.9635 | btu/hr
Water chilling by abs. chiller: |  |  | 1810.1693 | tons
Size absorbtion chillers: |  |  | 905 | tons
No. absorbtion chillers: |  |  | 2 | units
Additional capital for abs. chiller: |  |  | 1176500 | $
Additional capital for cooling tower: |  |  | 362000 | $
Additional capital (total): |  |  | 1538500 | $
Capital reduction for cent. chiller |  |  | 519300 | $
Capital reduction for fuel cells |  |  | 1418741.1765 | $
Capital reduction (total): |  |  | 1938041.1765 | $
Capital reduction (net): |  |  | -399541.1765 | $
Capital for air-conditioning |  |  | 37174191.8651 | $
and power:
Block 1: |  |  | 2190 | hr/yr | 3 | month/yr
Summer |  |  | 0.55 | kW | 1810.1693 | tons
Water Chilling Usage: |  |  | 2180348.9583 | kWh
Water Chilling Demand: |  |  | 995.5931 | kW
Block 2: |  |  | 2190 | hr/yr | 3 | month/yr
Spring |  |  | 0.475 | kW | 1810.1693 | tons
Water Chilling Usage: |  |  | 1883028.6458 | kWh
Water Chilling Demand: |  |  | 859.8304 | kW
Block 3: |  |  | 2190 | hr/yr | 3 | month/yr
Fall |  |  | 0.4 | kW | 1810.1693 | tons
Water Chilling Usage: |  |  | 1585708.3333 | kWh
Water Chilling Demand: |  |  | 724.0677 | kW
Block 4: |  |  | 2190 | hr/yr | 3 | month/yr
Winter |  |  | 0.325 | kW | 1810.1693 | tons
Water Chilling Usage |  |  | 1288388.0208 | kWh
Water Chilling Demand |  |  | 588.305 | kW
Reduced Water Chilling Usage: |  |  | 6937473.9583 | kWh/yr
Additional Clg. Twr. Fan Usage |  |  | 328500 | kWh/yr
Reduced Air-Cond. Usage (Net) |  |  | 6608973.9583 | kWh/yr
Annual Air-Conditioning Usage: |  |  | 18683199.1667 | kWh/yr
Annual Data-Processing Usage: |  |  | 92856000 | kWh/yr
Annual Elec. Usage (Fuel Cell): |  |  | 111539199.1667 | kWh/yr
Annual Natural Gas Usage: |  |  | 9514293.6889 | therm/yr
Annual Natural Gas Cost: |  |  | 6184290.8978 | $/yr
Annual Energy Cost: |  |  | 6184290.8978 | $/yr
Centrifugal Chillers |  |  | 30008.1239 | $/yr
Absorbtion chillers |  |  | 15000 | $/yr
Fan-Coil Units |  |  | 51003.6096 | $/yr
Cooling Towers |  |  | 40005.4159 | $/yr
Pumps |  |  | 6001.0832 | $/yr
Air-Conditioning Sub-total |  |  | 142018.2326 | $/yr
Fuel Cells |  |  | 101263.5 | $/yr
Power Conversion Sub-total |  |  | 101263.5 | $/yr
Annual Maint. Cost |  |  | 243281.7326 | $/yr
Summary of Results
|  |  | Savings |  | Savings |  | Savings |  | Savings |  | Savings |  | Savings |  | Savings |  | Savings |  | Savings |  | Savings |  | Savings |  | Savings
| Baseline | Alt. 1 | v/Baseline | Alt. 2 | v/Baseline | Alt.3 | v/Baseline | Alt. 4 | v/Baseline | Alt. 5 | v/Baseline | Alt. 6 | v/Baseline | Alt. 7 | v/Baseline | Alt. 8 | v/Baseline | Alt. 9 | v/Baseline | Alt. 10 | v/Baseline | Alt. 11 | v/Baseline | Alt. 12 | v/Baseline
Capital
Expenditure
Year 0 | 28574838.2353 | 38538192.6886 | -9963354.4533 | 32705738.8275 | -4130900.5922 | 33433217.2758 | -4858379.0405 | 33547864.2758 | -4973026.0405 | 33547864.2758 | -4973026.0405 | 32705738.8275 | -4130900.5922 | 33433217.2758 | -4858379.0405 | 33303229.8275 | -4728391.5922 | 33857929.8275 | -5283091.5922 | 33857929.8275 | -5283091.5922 | 37573733.0415 | -8998894.8063 | 37174191.8651 | -8599353.6298
|  |  | -34.87% |  | -14.46% |  | -17% |  | -17.4% |  | -17.4% |  | -14.46% |  | -17% |  | -16.55% |  | -18.49% |  | -18.49% |  | -31.49% |  | -30.09%
Year 10 | 1491750 | 1589629.5 | -97879.5 | 1560922.5 | -69172.5 | 0 | 1491750 | 0 | 1491750 | 0 | 1491750 | 1560922.5 | -69172.5 | 0 | 1491750 | 1912813.5 | -421063.5 | 1912813.5 | -421063.5 | 1912813.5 | -421063.5 | 0 | 1491750 | 0 | 1491750
|  |  | -6.561% |  | -4.637% |  | 100% |  | 100% |  | 100% |  | -4.637% |  | 100% |  | -28.23% |  | -28.23% |  | -28.23% |  | 100% |  | 100%
Annual | 10493538.4615 | 7293071.1412 | 3200467.3203 | 8286249.8935 | 2207288.568 | 7206747.5385 | 3286790.9231 | 6756757.1692 | 3736781.2923 | 6013787.963 | 4479750.4986 | 7363545.8462 | 3129992.6153 | 6557388.1886 | 3936150.2729 | 8459936.0474 | 2033602.4142 | 7450645.2043 | 3042893.2572 | 6813837.4945 | 3679700.9671 | 6550725.4589 | 3942813.0026 | 6184290.8978 | 4309247.5637
Energy Cost |  |  | 30.5% |  | 21.03% |  | 31.32% |  | 35.61% |  | 42.69% |  | 29.83% |  | 37.51% |  | 19.38% |  | 29% |  | 35.07% |  | 37.57% |  | 41.07%
Annual | 662235.2941 | 422833.4443 | 239401.8498 | 436765.0609 | 225470.2332 | 234491.7105 | 427743.5836 | 251110.7105 | 411124.5836 | 251110.7105 | 411124.5836 | 436765.0609 | 225470.2332 | 234491.7105 | 427743.5836 | 314408.6681 | 347826.626 | 246012.1975 | 416223.0966 | 246012.1975 | 416223.0966 | 224635.3209 | 437599.9732 | 243281.7326 | 418953.5615
Opns & Maint Cost |  |  | 36.15% |  | 34.05% |  | 64.59% |  | 62.08% |  | 62.08% |  | 34.05% |  | 64.59% |  | 52.52% |  | 62.85% |  | 62.85% |  | 66.08% |  | 63.26%
NPV of After-Tax Savings |  |  | 6292375.2259 |  | 9508109.7907 |  | 16588080.5101 |  | 18908479.6279 |  | 23083107.6946 |  | 14596467.211 |  | 20194911.4987 |  | 8441779.6128 |  | 12339001.2047 |  | 15917124.3842 |  | 13457838.4448 |  | 15932809.0108
at 10% Discount Rate
NPV of After-Tax Savings |  |  | -954383.7572 |  | 3675876.5283 |  | 3675876.5283 |  | 8599543.1272 |  | 10987496.678 |  | 6580645.8401 |  | 9401045.3178 |  | 2842332.319 |  | 4677399.3248 |  | 6724142.6071 |  | 3491593.5448 |  | 5090171.7257
at 20% Discount Rate
NPV of After-Tax Savings |  |  | -4604526.4856 |  | 662187.5787 |  | 2539894.348 |  | 3279747.3453 |  | 4744696.8777 |  | 2448182.07 |  | 3819565.1148 |  | -57562.3937 |  | 762358.5169 |  | 2017984.1188 |  | -1565706.0508 |  | -423670.4216
at 35% Discount Rate
After-Tax IRR |  |  | -237.5% |  | Positive |  | Positive |  | Positive |  | Positive |  | Positive |  | Positive |  | Positive |  | >150% |  | >150% |  | -187.5% |  | -134.9%
[5 empty] | Cash Flow |  | Cash Flow |  | Cash Flow |  | Cash Flow |  | Cash Flow |  | Cash Flow |  | Cash Flow
Elec. Rate that Drives
After-Tax NPV Negative
at 10% Discount Rate
and $0.65/Therm Nat. Gas Rate
Energy |  |  | $0.04/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.04/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh
Demand |  |  | $9.00/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $9.00/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month
Blended |  |  | $0.525/kWh |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | $0.525/kWh |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038
Elec. Rate that Drives
After-Tax NPV Negative
at 20% Discount Rate
and $0.65/Therm Nat. Gas Rate
Energy |  |  | $0.04/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.04/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.04/kWh |  | $0.03/kWh
Demand |  |  | $9.00/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $9.00/kW/month |  | $6/kW/month |  | $6/kW/month |  | $9.00/kW/month |  | $6/kW/month
Blended |  |  | $0.525/kWh |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | $0.525/kWh |  | 0.038 |  | 0.038 |  | $0.525/kWh |  | 0.038
Elec. Rate that Drives
After-Tax NPV Negative
at 35% Discount Rate
and $0.65/Therm Nat. Gas Rate
Energy |  |  | $0.05/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.04/kWh |  | $0.03/kWh |  | $0.03/kWh |  | $0.04/kWh |  | $0.04/kWh
Demand |  |  | $12/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $6/kW/month |  | $9/kW/month |  | $6/kW/month |  | $6/kW/month |  | $9.00/kW/month |  | $9.00/kW/month
Blended |  |  | $0.667/kWh |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.038 |  | 0.525 |  | 0.038 |  | 0.038 |  | $0.525/kWh |  | $0.525/kWh
Alternate 1 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Bal | Depr | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -9963354.4533 | [6 empty] | -9963354.4533 | 1 | -9963354.4533 | 1 | -9963354.4533 | 1 | -9963354.4533 | 1 | -9963354.4533 |  |  |  | 1 | -9963354.4533 | -9865474.9533 |  |  | -97879.5 | [5 empty] | -9963354.4533 |  |  |  |  | 1 | -9963354.4533 | 1 | -9963354.4533 | 1 | -9963354.4533 |  |  |  | 1 | -9963354.4533
1 |  | 8957231.058 | 3439869.1702 | 1006123.3953 | 1538022.669 | 1015094.9616 | 646627.8104 | 1661722.7719 | 0.9091 | 1510672.172 | 0.7407 | 1230838.0572 | 0.6667 | 1107870.5721 | 0.5714 | 949508.3919 |  |  |  | 0.8333 | 1384713.5859 |  | 8878927.458 | 986547.4953 |  | 78303.6 | 19575.9 |  |  |  |  | 8957231.058 | 1006123.3953 | 8967019.008 | 996335.4453 | 0.5 | 830861.386 | 0.4444 | 738469.5998 | 0.4 | 664689.1088 |  |  |  | 0.03636 | 60420.24
2 |  | 8053677.5922 | 3439869.1702 | 903553.4658 | 1730947.9451 | 1142425.6438 | 581033.2165 | 1723458.8603 | 0.8264 | 1424266.4021 | 0.6669 | 1149374.7139 | 0.4444 | 765905.1175 | 0.3265 | 562709.3179 |  |  |  | 0.6944 | 1196769.8326 |  | 7991034.7122 | 887892.7458 |  | 62642.88 | 15660.72 |  |  |  |  | 8053677.5922 | 903553.4658 | 8070317.1072 | 896701.9008 | 0.25 | 430864.7151 | 0.1613 | 277993.9142 | 0.016 | 27575.3418 |  |  |  | 0.13223 | 227892.9651
3 |  | 7242045.545 | 3439869.1702 | 811632.0472 | 1904032.5684 | 1256661.4952 | 522184.4446 | 1778845.9398 | 0.7513 | 1336446.9545 | 0.4046 | 719721.0672 | 0.2963 | 527072.0519 | 0.1866 | 331932.6524 |  |  |  | 0.5787 | 1029418.1453 |  | 7191931.241 | 799103.4712 |  | 50114.304 | 12528.576 |  |  |  |  | 7242045.545 | 811632.0472 | 7263285.3965 | 807031.7107 | 0.125 | 222355.7425 | 0.0878 | 156182.6735 | 0.064 | 113846.1401 |  |  |  | 0.04808 | 85526.9128
4 |  | 6512829.5601 | 3439869.1702 | 729215.9849 | 2059370.2292 | 1359184.3513 | 469369.6399 | 1828553.9912 | 0.683 | 1248902.376 | 0.3011 | 550577.6068 | 0.1975 | 361139.4133 | 0.1066 | 194923.8555 |  |  |  | 0.4823 | 881911.59 |  | 6472738.1169 | 719193.1241 |  | 40091.4432 | 10022.8608 |  |  |  |  | 6512829.5601 | 729215.9849 | 6536956.8568 | 726328.5396 | 0.0625 | 114284.6245 | 0.039 | 71313.6057 | 0.0256 | 46810.9822 |  |  |  | 0.01749 | 31980.495
5 |  | 5857537.4597 | 3439869.1702 | 655292.1003 | 2198823.3239 | 1451223.3937 | 421955.5877 | 1873178.9815 | 0.6209 | 1163056.8296 | 0.223 | 417718.9129 | 0.1317 | 246697.6719 | 0.0609 | 114076.6 |  |  |  | 0.4019 | 752830.6327 |  | 5825464.3052 | 647273.8117 |  | 32073.1546 | 8018.2886 |  |  |  |  | 5857537.4597 | 655292.1003 | 5883261.1711 | 653695.6857 | 0.03125 | 58536.8432 | 0.0173 | 32405.9964 | 0.0102 | 19106.4256 |  |  |  | 0.00636 | 11913.4183
6 |  | 5268576.3983 | 3439869.1702 | 588961.0614 | 2324050.4689 | 1533873.3095 | 379378.3584 | 1913251.6679 | 0.5645 | 1080030.5665 | 0.1652 | 316069.1755 | 0.0878 | 167983.4964 | 0.0348 | 66581.158 |  |  |  | 0.3349 | 640747.9836 |  | 5242917.8747 | 582546.4305 |  | 25658.5236 | 6414.6309 |  |  |  |  | 5268576.3983 | 588961.0614 | 5294935.054 | 588326.1171 | 0.01563 | 29904.1236 | 0.0077 | 14732.0378 | 0.0041 | 7844.3318 |  |  |  | 0.00231 | 4419.6114
7 |  | 4737869.9799 | 3439869.1702 | 530706.4184 | 2435375.7538 | 1607347.9975 | 341527.7616 | 1948875.7591 | 0.5132 | 1000163.0396 | 0.1224 | 238542.3929 | 0.0585 | 114009.2319 | 0.0199 | 38782.6276 |  |  |  | 0.2791 | 543931.2244 |  | 4718626.0872 | 524291.7875 |  | 19243.8927 | 6414.6309 |  |  |  |  | 4737869.9799 | 530706.4184 | 4765441.5486 | 529493.5054 | 0.00781 | 15220.7197 | 0.0034 | 6626.1776 | 0.0016 | 3118.2012 |  |  |  | 0.00084 | 1637.0556
8 |  | 4259592.7403 | 3439869.1702 | 478277.2396 | 2535632.6565 | 1673517.5533 | 307440.4146 | 1980957.9679 | 0.4665 | 924116.892 | 0.0906 | 179474.7919 | 0.039 | 77257.3607 | 0.0199 | 39421.0636 |  |  |  | 0.2326 | 460770.8233 |  | 4246763.4785 | 471862.6087 |  | 12829.2618 | 6414.6309 |  |  |  |  | 4259592.7403 | 478277.2396 | 4288897.3938 | 476544.1549 | 0.00391 | 7745.5457 | 0.0015 | 2971.437 | 0.000665 | 1317.337 |  |  |  | 0.000306 | 606.1731
9 |  | 3828501.7615 | 3439869.1702 | 431090.9788 | 2625928.0152 | 1733112.4901 | 276739.9927 | 2009852.4827 | 0.4241 | 852378.4379 | 0.0671 | 134861.1016 | 0.026 | 52256.1646 | 0.0065 | 13064.0411 |  |  |  | 0.1938 | 389509.4112 |  | 3822087.1306 | 424676.3478 |  | 6414.6309 | 6414.6309 |  |  |  |  | 3828501.7615 | 431090.9788 | 3860007.6544 | 428889.7394 | 0.00195 | 3919.2123 | 0.0007 | 1406.8967 | 0.000262 | 526.5814 |  |  |  | 0.000111 | 223.0936
10 | -97879.5 | 3439878.4176 | 3439869.1702 | 388623.344 | 2707257.9844 | 1786790.2697 | 249087.8031 | 1937998.5729 | 0.3855 | 747098.4498 | 0.0497 | 96318.5291 | 0.0173 | 33527.3753 | 0.0037 | 7170.5947 |  |  |  | 0.1615 | 312986.7695 |  | 3439878.4176 | 382208.7131 |  | 0 | 6414.6309 | -97879.5 |  |  | -97879.5 | 3439878.4176 | 388623.344 | 3474006.8889 | 386000.7654 | 0.00098 | 1899.2386 | 0.0003 | 581.3996 | 0.000105 | 203.4899 |  |  |  | 4e-05 | 77.5199
11 |  | 3174194.1758 | 3439869.1702 | 363563.7418 | 2758886.0108 | 1820864.7671 | 231534.2742 | 2052399.0413 | 0.3505 | 719365.864 | 0.0368 | 75528.2847 | 0.116 | 238078.2888 | 0.0021 | 4310.038 |  |  |  | 0.1346 | 276252.911 |  | 3095890.5758 | 343987.8418 |  |  |  |  | 78303.6 | 19575.9 |  | 3174194.1758 | 363563.7418 | 3126606.2001 | 347400.6889 | 0.00049 | 1005.6755 | 0.00013 | 266.8119 | 4.2e-05 | 86.2008 |  |  |  | 1.47e-05 | 30.1703
12 |  | 2814545.6141 | 3439869.1702 | 359648.5618 | 2798766.047 | 1847185.591 | 217975.0619 | 2065160.6529 | 0.3186 | 657960.184 | 0.0273 | 56378.8858 | 0.0077 | 15901.737 | 0.0012 | 2478.1928 |  |  |  | 0.1122 | 231711.0253 |  | 2751902.7341 | 343987.8418 |  |  |  |  | 62642.88 | 15660.72 |  | 2814545.6141 | 359648.5618 | 2779205.5112 | 347400.6889 | 0.00024 | 495.6386 | 5.9e-05 | 121.8445 | 1.7e-05 | 35.1077 |  |  |  | 5.3e-06 | 10.9454
13 |  | 2458029.1963 | 3439869.1702 | 356516.4178 | 2837549.8328 | 1872782.8896 | 204788.5747 | 2077571.4643 | 0.2897 | 601872.4532 | 0.0273 | 56717.701 | 0.0051 | 10595.6145 | 0.0007 | 1454.3 |  |  |  | 0.0935 | 194252.9319 |  | 2407914.8923 | 343987.8418 |  |  |  |  | 50114.304 | 12528.576 |  | 2458029.1963 | 356516.4178 | 2431804.8223 | 347400.6889 | 0.00012 | 249.3086 | 2.6e-05 | 54.0169 | 6.7e-06 | 13.9197 |  |  |  | 1.9e-06 | 3.9474
14 |  | 2104018.4937 | 3439869.1702 | 354010.7026 | 2875456.6182 | 1897801.368 | 191900.2677 | 2089701.6357 | 0.2633 | 550218.4407 | 0.0202 | 42211.973 | 0.0034 | 7104.9856 | 0.0004 | 835.8807 |  |  |  | 0.0779 | 162787.7574 |  | 2063927.0505 | 343987.8418 |  |  |  |  | 40091.4432 | 10022.8608 |  | 2104018.4937 | 354010.7026 | 2084404.1334 | 347400.6889 | 6e-05 | 125.3821 | 1.2e-05 | 25.0764 | 2.7e-06 | 5.6422 |  |  |  | 7e-07 | 1.4628
15 |  | 1752012.3633 | 3439869.1702 | 352006.1304 | 2912661.8034 | 1922356.7903 | 179250.5047 | 2101607.2949 | 0.2394 | 503124.7864 | 0.015 | 31524.1094 | 0.0023 | 4833.6968 | 0.0002 | 420.3215 |  |  |  | 0.0649 | 136394.3134 |  | 1719939.2088 | 343987.8418 |  |  |  |  | 32073.1546 | 8018.2886 |  | 1752012.3633 | 352006.1304 | 1737003.4445 | 347400.6889 | 3e-05 | 63.0482 | 5e-06 | 10.508 | 1.1e-06 | 2.3118 |  |  |  | 3e-07 | 0.63048
16 |  | 1401609.8907 | 3439869.1702 | 350402.4727 | 2949305.7084 | 1946541.7676 | 166791.577 | 2113333.3445 | 0.2176 | 459861.3358 | 0.0111 | 23458.0001 | 0.0015 | 3170 | 0.0001 | 211.3333 |  |  |  | 0.0541 | 114331.3339 |  | 1375951.367 | 343987.8418 |  |  |  |  | 25658.5236 | 6414.6309 |  | 1401609.8907 | 350402.4727 | 1389602.7556 | 347400.6889 | 1e-05 | 21.1333 | 2.3e-06 | 4.8607 | 4e-07 | 0.84533 |  |  |  | 9e-08 | 0.1902
17 |  | 1051207.418 | 3439869.1702 | 350402.4727 | 2984345.9557 | 1969668.3308 | 154877.8929 | 2124546.2237 | 0.1978 | 420235.243 | 0.0082 | 17421.279 | 0.001 | 2124.5462 | 0.0001 | 212.4546 |  |  |  | 0.0451 | 95817.0347 |  | 1031963.5253 | 343987.8418 |  |  |  |  | 19243.8927 | 6414.6309 |  | 1051207.418 | 350402.4727 | 1042202.0667 | 347400.6889 | 8e-06 | 16.9964 | 1e-06 | 2.1245 | 2e-07 | 0.42491 |  |  |  | 3e-08 | 0.063736
18 |  | 700804.9453 | 3439869.1702 | 350402.4727 | 3019386.203 | 1992794.8939 | 142964.2088 | 2135759.1028 | 0.1799 | 384223.0626 | 0.0045 | 9610.916 | 0.0007 | 1495.0314 | 7e-05 | 149.5031 |  |  |  | 0.0376 | 80304.5423 |  | 687975.6835 | 343987.8418 |  |  |  |  | 12829.2618 | 6414.6309 |  | 700804.9453 | 350402.4727 | 694801.3778 | 347400.6889 | 4e-06 | 8.543 | 5e-07 | 1.0679 | 1e-07 | 0.21358 |  |  |  | 1e-08 | 0.021358
19 |  | 350402.4727 | 3439869.1702 | 350402.4727 | 3054426.4502 | 2015921.4571 | 131050.5248 | 2146971.9819 | 0.1635 | 351029.919 | 0.0033 | 7085.0075 | 0.0005 | 1073.486 | 2e-05 | 42.9394 |  |  |  | 0.0313 | 67200.223 |  | 343987.8418 | 343987.8418 |  |  |  |  | 6414.6309 | 6414.6309 |  | 350402.4727 | 350402.4727 | 347400.6889 | 347400.6889 | 2e-07 | 0.42939 | 2e-07 | 0.42939 | 3e-08 | 0.064409 |  |  |  | 0 | 0
20 |  | 0 | 3439869.1702 | 350402.4727 | 3089466.6975 | 2039048.0203 | 119136.8407 | 2158184.861 | 0.1486 | 320706.2704 | 0.0025 | 5395.4622 | 0.0003 | 647.4555 | 1e-05 | 21.5818 |  |  |  | 0.0261 | 56328.6249 |  | 0 | 343987.8418 |  |  |  |  | 0 | 6414.6309 |  | 0 | 350402.4727 | 0 | 347400.6889 | 1e-07 | 0.21582 | 1e-07 | 0.21582 | 1e-08 | 0.021582 |  |  |  | 0 | 0
| -10061233.9533 |  | 68797383.4031 | 10061233.9533 | 51339692.9415 | 33884197.3414 | 5935614.7569 | 29758578.145 |  | 6292375.2259 |  | -4604526.4856 |  | -6224611.156 |  | -7635047.6054 | 0.24436 | -0.076323 | -0.60331 |  | -954383.7572 | [9 empty] | -10061233.9533 |  | 10061233.9533 |  |  |  | -8245775.9314 |  | -8660183.7591 |  | -9078171.7616 | -2.3754 | -3.9744 | -3.9297 |  | -9538609.5368 | -3.4291
Alternative 2 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -4130900.5922 | [6 empty] | -4130900.5922 | 1 | -4130900.5922 | 1 | -4130900.5922 | 1 | -4130900.5922 | 1 | -4130900.5922 |  |  |  | 1 | -4130900.5922 | -4061728.0922 |  |  | -69172.5 | [5 empty] | -4130900.5922 |  |  |  |  | 1 | -4130900.5922 | 1 | -4130900.5922 | 1 | -4130900.5922 |  |  |  | 1 | -4130900.5922
1 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.9091 | 1459669.8773 | 0.7407 | 1189283.3331 | 0.6667 | 1070467.3932 | 0.5714 | 917451.7301 |  |  |  | 0.8333 | 1337963.82 |  | 3655555.283 | 406172.8092 |  | 55338 | 13834.5 |  |  |  |  | 3710893.283 | 420007.3092 | 3717810.533 | 413090.0592 | 0.5 | 802810.4044 | 0.4444 | 713537.8874 | 0.4 | 642248.3235 |  |  |  | 0.03636 | 58380.3726
2 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.8264 | 1326885.0364 | 0.6669 | 1070788.5174 | 0.4444 | 713537.8874 | 0.3265 | 524235.1941 |  |  |  | 0.6944 | 1114943.0896 |  | 3289999.7547 | 365555.5283 |  | 44270.4 | 11067.6 |  |  |  |  | 3334270.1547 | 376623.1283 | 3346029.4797 | 371781.0533 | 0.25 | 401405.2022 | 0.1613 | 258986.6365 | 0.016 | 25689.9329 |  |  |  | 0.13223 | 212311.2395
3 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.7513 | 1206302.9136 | 0.4046 | 649634.1792 | 0.2963 | 475745.4456 | 0.1866 | 299608.8429 |  |  |  | 0.5787 | 929172.762 |  | 2960999.7792 | 328999.9755 |  | 35416.32 | 8854.08 |  |  |  |  | 2996416.0992 | 337854.0555 | 3011426.5317 | 334602.948 | 0.125 | 200702.6011 | 0.0878 | 140973.507 | 0.064 | 102759.7318 |  |  |  | 0.04808 | 77198.2485
4 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.683 | 1096639.0124 | 0.3011 | 483452.4255 | 0.1975 | 317110.1097 | 0.1066 | 171159.1782 |  |  |  | 0.4823 | 774390.9161 |  | 2664899.8013 | 296099.9779 |  | 28333.056 | 7083.264 |  |  |  |  | 2693232.8573 | 303183.2419 | 2710283.8786 | 301142.6532 | 0.0625 | 100351.3005 | 0.039 | 62619.2115 | 0.0256 | 41103.8927 |  |  |  | 0.01749 | 28081.5051
5 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.6209 | 996929.9602 | 0.223 | 358053.4404 | 0.1317 | 211460.2605 | 0.0609 | 97782.3073 |  |  |  | 0.4019 | 645299.003 |  | 2398409.8212 | 266489.9801 |  | 22666.4448 | 5666.6112 |  |  |  |  | 2421076.266 | 272156.5913 | 2439255.4907 | 271028.3879 | 0.03125 | 50175.6503 | 0.0173 | 27777.24 | 0.0102 | 16377.3322 |  |  |  | 0.00636 | 10211.7483
6 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.5645 | 906372.9466 | 0.1652 | 265248.5576 | 0.0878 | 140973.507 | 0.0348 | 55875.6041 |  |  |  | 0.3349 | 537722.4089 |  | 2158568.8391 | 239840.9821 |  | 18133.1558 | 4533.289 |  |  |  |  | 2176701.9949 | 244374.2711 | 2195329.9416 | 243925.5491 | 0.01563 | 25095.8532 | 0.0077 | 12363.2802 | 0.0041 | 6583.0453 |  |  |  | 0.00231 | 3708.9841
7 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.5132 | 824004.5991 | 0.1224 | 196527.987 | 0.0585 | 93928.8173 | 0.0199 | 31951.8541 |  |  |  | 0.2791 | 448128.7677 |  | 1942711.9551 | 215856.8839 |  | 13599.8669 | 4533.289 |  |  |  |  | 1956311.822 | 220390.1729 | 1975796.9475 | 219532.9942 | 0.00781 | 12539.8985 | 0.0034 | 5459.1107 | 0.0016 | 2568.9933 |  |  |  | 0.00084 | 1348.7215
8 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.4665 | 749022.1073 | 0.0906 | 145469.2453 | 0.039 | 62619.2115 | 0.0199 | 31951.8541 |  |  |  | 0.2326 | 373467.4001 |  | 1748440.7596 | 194271.1955 |  | 9066.5779 | 4533.289 |  |  |  |  | 1757507.3376 | 198804.4845 | 1778217.2527 | 197579.6947 | 0.00391 | 6277.9774 | 0.0015 | 2408.4312 | 0.000665 | 1067.7378 |  |  |  | 0.000306 | 491.32
9 |  | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1605620.8088 | 0.4241 | 680943.785 | 0.0671 | 107737.1563 | 0.026 | 41746.141 | 0.0065 | 10436.5353 |  |  |  | 0.1938 | 311169.3127 |  | 1573596.6837 | 174844.076 |  | 4533.289 | 4533.289 |  |  |  |  | 1578129.9726 | 179377.3649 | 1600395.5274 | 177821.7253 | 0.00195 | 3130.9606 | 0.0007 | 1123.9346 | 0.000262 | 420.6727 |  |  |  | 0.000111 | 178.2239
10 | -69172.5 | 0 | 2432758.8012 | 0 | 2432758.8012 | 1605620.8088 | 0 | 1536448.3088 | 0.3855 | 592300.823 | 0.0497 | 76361.4809 | 0.0173 | 26580.5557 | 0.0037 | 5684.8587 |  |  |  | 0.1615 | 248136.4019 |  | 1416237.0153 | 157359.6684 |  | 0 | 4533.289 | -69172.5 |  |  | -69172.5 | 1416237.0153 | 161892.9573 | 1440355.9747 | 160039.5527 | 0.00098 | 1505.7193 | 0.0003 | 460.9345 | 0.000105 | 161.3271 |  |  |  | 4e-05 | 61.4579
11 |  | 55338 | 2432758.8012 | 13834.5 | 2418924.3012 | 1596490.0388 | 6585.222 | 1603075.2608 | 0.3505 | 561877.8789 | 0.0368 | 58993.1696 | 0.116 | 185956.7302 | 0.0021 | 3366.458 |  |  |  | 0.1346 | 215773.9301 |  | 1274613.3138 | 141623.7015 | [7 empty] | 1329951.3138 | 155458.2015 | 1296320.3772 | 144035.5975 | 0.00049 | 785.5069 | 0.00013 | 208.3998 | 4.2e-05 | 67.3292 |  |  |  | 1.47e-05 | 23.5652
12 |  | 44270.4 | 2432758.8012 | 11067.6 | 2421691.2012 | 1598316.1928 | 5268.1776 | 1603584.3704 | 0.3186 | 510901.9804 | 0.0273 | 43777.8533 | 0.0077 | 12347.5997 | 0.0012 | 1924.3012 |  |  |  | 0.1122 | 179922.1664 |  | 1132989.6122 | 141623.7015 | [7 empty] | 1177260.0122 | 152691.3015 | 1152284.7798 | 144035.5975 | 0.00024 | 384.8602 | 5.9e-05 | 94.6115 | 1.7e-05 | 27.2609 |  |  |  | 5.3e-06 | 8.499
13 |  | 35416.32 | 2432758.8012 | 8854.08 | 2423904.7212 | 1599777.116 | 4214.5421 | 1603991.6581 | 0.2897 | 464676.3833 | 0.0273 | 43788.9723 | 0.0051 | 8180.3575 | 0.0007 | 1122.7942 |  |  |  | 0.0935 | 149973.22 |  | 991365.9107 | 141623.7015 | [7 empty] | 1026782.2307 | 150477.7815 | 1008249.1823 | 144035.5975 | 0.00012 | 192.479 | 2.6e-05 | 41.7038 | 6.7e-06 | 10.7467 |  |  |  | 1.9e-06 | 3.0476
14 |  | 28333.056 | 2432758.8012 | 7083.264 | 2425675.5372 | 1600945.8545 | 3371.6337 | 1604317.4882 | 0.2633 | 422416.7946 | 0.0202 | 32407.2133 | 0.0034 | 5454.6795 | 0.0004 | 641.727 |  |  |  | 0.0779 | 124976.3323 |  | 849742.2092 | 141623.7015 | [7 empty] | 878075.2652 | 148706.9655 | 864213.5848 | 144035.5975 | 6e-05 | 96.259 | 1.2e-05 | 19.2518 | 2.7e-06 | 4.3317 |  |  |  | 7e-07 | 1.123
15 |  | 22666.4448 | 2432758.8012 | 5666.6112 | 2427092.19 | 1601880.8454 | 2697.3069 | 1604578.1523 | 0.2394 | 384136.0097 | 0.015 | 24068.6723 | 0.0023 | 3690.5298 | 0.0002 | 320.9156 |  |  |  | 0.0649 | 104137.1221 |  | 708118.5077 | 141623.7015 | [7 empty] | 730784.9525 | 147290.3127 | 720177.9874 | 144035.5975 | 3e-05 | 48.1373 | 5e-06 | 8.0229 | 1.1e-06 | 1.765 |  |  |  | 3e-07 | 0.48137
16 |  | 18133.1558 | 2432758.8012 | 4533.289 | 2428225.5122 | 1602628.8381 | 2157.8455 | 1604786.6836 | 0.2176 | 349201.5824 | 0.0111 | 17813.1322 | 0.0015 | 2407.18 | 0.0001 | 160.4787 |  |  |  | 0.0541 | 86818.9596 |  | 566494.8061 | 141623.7015 | [7 empty] | 584627.962 | 146156.9905 | 576142.3899 | 144035.5975 | 1e-05 | 16.0479 | 2.3e-06 | 3.691 | 4e-07 | 0.64191 |  |  |  | 9e-08 | 0.14443
17 |  | 13599.8669 | 2432758.8012 | 4533.289 | 2428225.5122 | 1602628.8381 | 2003.7137 | 1604632.5518 | 0.1978 | 317396.3187 | 0.0082 | 13157.9869 | 0.001 | 1604.6326 | 0.0001 | 160.4633 |  |  |  | 0.0451 | 72368.9281 |  | 424871.1046 | 141623.7015 | [7 empty] | 438470.9715 | 146156.9905 | 432106.7924 | 144035.5975 | 8e-06 | 12.8371 | 1e-06 | 1.6046 | 2e-07 | 0.32093 |  |  |  | 3e-08 | 0.048139
18 |  | 9066.5779 | 2432758.8012 | 4533.289 | 2428225.5122 | 1602628.8381 | 1849.5819 | 1604478.42 | 0.1799 | 288645.6678 | 0.0045 | 7220.1529 | 0.0007 | 1123.1349 | 7e-05 | 112.3135 |  |  |  | 0.0376 | 60328.3886 |  | 283247.4031 | 141623.7015 | [7 empty] | 292313.981 | 146156.9905 | 288071.1949 | 144035.5975 | 4e-06 | 6.4179 | 5e-07 | 0.80224 | 1e-07 | 0.16045 |  |  |  | 1e-08 | 0.016045
19 |  | 4533.289 | 2432758.8012 | 4533.289 | 2428225.5122 | 1602628.8381 | 1695.4501 | 1604324.2881 | 0.1635 | 262307.0211 | 0.0033 | 5294.2702 | 0.0005 | 802.1621 | 2e-05 | 32.0865 |  |  |  | 0.0313 | 50215.3502 |  | 141623.7015 | 141623.7015 | [7 empty] | 146156.9905 | 146156.9905 | 144035.5975 | 144035.5975 | 2e-07 | 0.32086 | 2e-07 | 0.32086 | 3e-08 | 0.04813 |  |  |  | 0 | 0
20 |  | 0 | 2432758.8012 | 4533.289 | 2428225.5122 | 1602628.8381 | 1541.3182 | 1604170.1563 | 0.1486 | 238379.6852 | 0.0025 | 4010.4254 | 0.0003 | 481.251 | 1e-05 | 16.0417 |  |  |  | 0.0261 | 41868.8411 |  | 0 | 141623.7015 | [7 empty] | 0 | 146156.9905 | -2.3283e-10 | 144035.5975 | 1e-07 | 0.16042 | 1e-07 | 0.16042 | 1e-08 | 0.016042 |  |  |  | 0 | 0
| -4200073.0922 |  | 48655176.0235 | 69172.5 | 48586003.5235 | 32066762.3255 | 31384.7918 | 27898074.025 |  | 9508109.7907 |  | 662187.5787 |  | -754683.0058 |  | -1976905.0536 | 0.36871 | 0.4201 | 0.34563 |  | 3675876.5283 | [9 empty] | -4200073.0922 |  | 4200073.0922 |  |  |  | -2525361.998 |  | -2904811.8496 |  | -3291806.9819 | -0.15112 | -0.66383 | -0.62652 |  | -3738891.8459 | -0.34071
Alternative 3 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -4858379.0405 | [6 empty] | -4858379.0405 | 1 | -4858379.0405 | 1 | -4858379.0405 | 1 | -4858379.0405 | 1 | -4858379.0405 |  |  |  | 1 | -4858379.0405 | -4858379.0405 |  |  | 0 | [5 empty] | -4858379.0405 |  |  |  |  | 1 | -4858379.0405 | 1 | -4858379.0405 | 1 | -4858379.0405 |  |  |  | 1 | -4858379.0405
1 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.9091 | 2228742.9912 | 0.7407 | 1815894.768 | 0.6667 | 1634476.9027 | 0.5714 | 1400840.1113 |  |  |  | 0.8333 | 2042912.2589 |  | 4372541.1365 | 485837.9041 |  | 0 | 0 |  |  |  |  | 4372541.1365 | 485837.9041 |  |  | 0.5 | 1225796.3872 | 0.4444 | 1089487.8289 | 0.4 | 980637.1098 |  |  |  | 0.03636 | 89139.9133
2 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.8264 | 2025996.2688 | 0.6669 | 1634967.2213 | 0.4444 | 1089487.8289 | 0.3265 | 800445.0408 |  |  |  | 0.6944 | 1702386.0225 |  | 3935287.0228 | 437254.1136 |  | 0 | 0 |  |  |  |  | 3935287.0228 | 437254.1136 |  |  | 0.25 | 612898.1936 | 0.1613 | 395441.9145 | 0.016 | 39225.4844 |  |  |  | 0.13223 | 324174.1126
3 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.7513 | 1841881.6514 | 0.4046 | 991914.4365 | 0.2963 | 726406.9391 | 0.1866 | 457467.2117 |  |  |  | 0.5787 | 1418736.7385 |  | 3541758.3206 | 393528.7023 |  | 0 | 0 |  |  |  |  | 3541758.3206 | 393528.7023 |  |  | 0.125 | 306449.0968 | 0.0878 | 215249.8456 | 0.064 | 156901.9376 |  |  |  | 0.04808 | 117872.5806
4 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.683 | 1674437.8649 | 0.3011 | 738174.5844 | 0.1975 | 484189.5729 | 0.1066 | 261339.7898 |  |  |  | 0.4823 | 1182403.1951 |  | 3187582.4885 | 354175.8321 |  | 0 | 0 |  |  |  |  | 3187582.4885 | 354175.8321 |  |  | 0.0625 | 153224.5484 | 0.039 | 95612.1182 | 0.0256 | 62760.775 |  |  |  | 0.01749 | 42877.1318
5 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.6209 | 1522193.9536 | 0.223 | 546705.1887 | 0.1317 | 322874.7684 | 0.0609 | 149302 |  |  |  | 0.4019 | 985295.136 |  | 2868824.2397 | 318758.2489 |  | 0 | 0 |  |  |  |  | 2868824.2397 | 318758.2489 |  |  | 0.03125 | 76612.2742 | 0.0173 | 42412.555 | 0.0102 | 25006.2463 |  |  |  | 0.00636 | 15592.13
6 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.5645 | 1383924.1212 | 0.1652 | 405003.1263 | 0.0878 | 215249.8456 | 0.0348 | 85315.4285 |  |  |  | 0.3349 | 821038.4201 |  | 2581941.8157 | 286882.424 |  | 0 | 0 |  |  |  |  | 2581941.8157 | 286882.424 |  |  | 0.01563 | 38318.3951 | 0.0077 | 18877.2644 | 0.0041 | 10051.5304 |  |  |  | 0.00231 | 5663.1793
7 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.5132 | 1258157.4118 | 0.1224 | 300074.9556 | 0.0585 | 143418.1773 | 0.0199 | 48786.6962 |  |  |  | 0.2791 | 684239.5433 |  | 2323747.6341 | 258194.1816 |  | 0 | 0 |  |  |  |  | 2323747.6341 | 258194.1816 |  |  | 0.00781 | 19146.9396 | 0.0034 | 8335.4154 | 0.0016 | 3922.5484 |  |  |  | 0.00084 | 2059.3379
8 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.4665 | 1143668.0293 | 0.0906 | 222114.3054 | 0.039 | 95612.1182 | 0.0199 | 48786.6962 |  |  |  | 0.2326 | 570240.4793 |  | 2091372.8707 | 232374.7634 |  | 0 | 0 |  |  |  |  | 2091372.8707 | 232374.7634 |  |  | 0.00391 | 9585.7277 | 0.0015 | 3677.3892 | 0.000665 | 1630.3092 |  |  |  | 0.000306 | 750.1874
9 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.4241 | 1039720.4956 | 0.0671 | 164501.8752 | 0.026 | 63741.4121 | 0.0065 | 15935.353 |  |  |  | 0.1938 | 475118.6797 |  | 1882235.5836 | 209137.2871 |  | 0 | 0 |  |  |  |  | 1882235.5836 | 209137.2871 |  |  | 0.00195 | 4780.6059 | 0.0007 | 1716.1149 | 0.000262 | 642.3173 |  |  |  | 0.000111 | 272.1268
10 | 1491750 | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 3943342.7744 | 0.3855 | 1520158.6395 | 0.0497 | 195984.1359 | 0.0173 | 68219.83 | 0.0037 | 14590.3683 |  |  |  | 0.1615 | 636849.8581 |  | 1694012.0253 | 188223.5584 |  | 0 | 0 | 0 |  |  | 0 | 1694012.0253 | 188223.5584 |  |  | 0.00098 | 3864.4759 | 0.0003 | 1183.0028 | 0.000105 | 414.051 |  |  |  | 4e-05 | 157.7337
11 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.3505 | 859283.2674 | 0.0368 | 90218.6141 | 0.116 | 284384.7618 | 0.0021 | 5148.3448 |  |  |  | 0.1346 | 329984.3874 |  | 1524610.8227 | 169401.2025 |  |  |  |  | 0 | 0 |  | 1524610.8227 | 169401.2025 |  |  | 0.00049 | 1201.2805 | 0.00013 | 318.7071 | 4.2e-05 | 102.9669 |  |  |  | 1.47e-05 | 36.0384
12 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.3186 | 781077.4579 | 0.0273 | 66928.4827 | 0.0077 | 18877.2644 | 0.0012 | 2941.9113 |  |  |  | 0.1122 | 275068.7093 |  | 1355209.6202 | 169401.2025 |  |  |  |  | 0 | 0 |  | 1355209.6202 | 169401.2025 |  |  | 0.00024 | 588.3823 | 5.9e-05 | 144.644 | 1.7e-05 | 41.6771 |  |  |  | 5.3e-06 | 12.9934
13 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.2897 | 710226.4267 | 0.0273 | 66928.4827 | 0.0051 | 12503.1231 | 0.0007 | 1716.1149 |  |  |  | 0.0935 | 229223.9244 |  | 1185808.4177 | 169401.2025 |  |  |  |  | 0 | 0 |  | 1185808.4177 | 169401.2025 |  |  | 0.00012 | 294.1911 | 2.6e-05 | 63.7414 | 6.7e-06 | 16.4257 |  |  |  | 1.9e-06 | 4.658
14 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.2633 | 645504.3775 | 0.0202 | 49522.174 | 0.0034 | 8335.4154 | 0.0004 | 980.6371 |  |  |  | 0.0779 | 190979.0771 |  | 1016407.2152 | 169401.2025 |  |  |  |  | 0 | 0 |  | 1016407.2152 | 169401.2025 |  |  | 6e-05 | 147.0956 | 1.2e-05 | 29.4191 | 2.7e-06 | 6.6193 |  |  |  | 7e-07 | 1.7161
15 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.2394 | 586911.3102 | 0.015 | 36773.8916 | 0.0023 | 5638.6634 | 0.0002 | 490.3186 |  |  |  | 0.0649 | 159108.3711 |  | 847006.0126 | 169401.2025 |  |  |  |  | 0 | 0 |  | 847006.0126 | 169401.2025 |  |  | 3e-05 | 73.5478 | 5e-06 | 12.258 | 1.1e-06 | 2.6968 |  |  |  | 3e-07 | 0.73548
16 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.2176 | 533466.5877 | 0.0111 | 27212.6798 | 0.0015 | 3677.3892 | 0.0001 | 245.1593 |  |  |  | 0.0541 | 132631.1691 |  | 677604.8101 | 169401.2025 |  |  |  |  | 0 | 0 |  | 677604.8101 | 169401.2025 |  |  | 1e-05 | 24.5159 | 2.3e-06 | 5.6387 | 4e-07 | 0.98064 |  |  |  | 9e-08 | 0.22064
17 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.1978 | 484925.0508 | 0.0082 | 20103.0608 | 0.001 | 2451.5928 | 0.0001 | 245.1593 |  |  |  | 0.0451 | 110566.8341 |  | 508203.6076 | 169401.2025 |  |  |  |  | 0 | 0 |  | 508203.6076 | 169401.2025 |  |  | 8e-06 | 19.6127 | 1e-06 | 2.4516 | 2e-07 | 0.49032 |  |  |  | 3e-08 | 0.073548
18 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.1799 | 441041.5401 | 0.0045 | 11032.1675 | 0.0007 | 1716.1149 | 7e-05 | 171.6115 |  |  |  | 0.0376 | 92179.8883 |  | 338802.4051 | 169401.2025 |  |  |  |  | 0 | 0 |  | 338802.4051 | 169401.2025 |  |  | 4e-06 | 9.8064 | 5e-07 | 1.2258 | 1e-07 | 0.24516 |  |  |  | 1e-08 | 0.024516
19 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.1635 | 400835.4186 | 0.0033 | 8090.2562 | 0.0005 | 1225.7964 | 2e-05 | 49.0319 |  |  |  | 0.0313 | 76734.8538 |  | 169401.2025 | 169401.2025 |  |  |  |  | 0 | 0 |  | 169401.2025 | 169401.2025 |  |  | 2e-07 | 0.49032 | 2e-07 | 0.49032 | 3e-08 | 0.073548 |  |  |  | 0 | 0
20 |  | 0 | 3714534.5067 | 0 | 3714534.5067 | 2451592.7744 | 0 | 2451592.7744 | 0.1486 | 364306.6863 | 0.0025 | 6128.9819 | 0.0003 | 735.4778 | 1e-05 | 24.5159 |  |  |  | 0.0261 | 63986.5714 |  | 0 | 169401.2025 |  |  |  |  | 0 | 0 |  | 0 | 169401.2025 |  |  | 1e-07 | 0.24516 | 1e-07 | 0.24516 | 1e-08 | 0.024516 |  |  |  | 0 | 0
| -3366629.0405 |  | 74290690.1336 |  | 74290690.1336 | 49031855.4881 | 0 | 45665226.4476 |  | 16588080.5101 |  | 2539894.348 |  | 324843.954 |  | -1563557.5401 | 0.3952 | 0.522 | 0.54301 |  | 7321305.0773 | [9 empty] | -4858379.0405 |  | 4858379.0405 |  |  |  | -2405343.2284 |  | -2985806.7705 |  | -3577014.5313 | 0.28564 | -0.035958 | -0.012588 |  | -4259764.1469 | 0.19022
Alternative 4 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -4973026.0405 | [6 empty] | -4973026.0405 | 1 | -4973026.0405 | 1 | -4973026.0405 | 1 | -4973026.0405 | 1 | -4973026.0405 |  |  |  | 1 | -4973026.0405 | -4973026.0405 |  |  | 0 | [5 empty] | -4973026.0405 |  |  |  |  | 1 | -4973026.0405 | 1 | -4973026.0405 | 1 | -4973026.0405 |  |  |  | 1 | -4973026.0405
1 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.9091 | 2488768.413 | 0.7407 | 2027753.5623 | 0.6667 | 1825169.8393 | 0.5714 | 1564274.8555 |  |  |  | 0.8333 | 2281256.9778 |  | 4475723.4365 | 497302.6041 |  | 0 | 0 |  |  |  |  | 4475723.4365 | 497302.6041 |  |  | 0.5 | 1368808.939 | 0.4444 | 1216597.385 | 0.4 | 1095047.1512 |  |  |  | 0.03636 | 99539.786
2 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.8264 | 2262367.4145 | 0.6669 | 1825717.3629 | 0.4444 | 1216597.385 | 0.3265 | 893832.2372 |  |  |  | 0.6944 | 1901001.8546 |  | 4028151.0928 | 447572.3436 |  | 0 | 0 |  |  |  |  | 4028151.0928 | 447572.3436 |  |  | 0.25 | 684404.4695 | 0.1613 | 441577.7637 | 0.016 | 43801.886 |  |  |  | 0.13223 | 361995.212
3 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.7513 | 2056772.3118 | 0.4046 | 1107640.1935 | 0.2963 | 811156.1773 | 0.1866 | 510839.4961 |  |  |  | 0.5787 | 1584259.4661 |  | 3625335.9836 | 402815.1093 |  | 0 | 0 |  |  |  |  | 3625335.9836 | 402815.1093 |  |  | 0.125 | 342202.2348 | 0.0878 | 240362.8497 | 0.064 | 175207.5442 |  |  |  | 0.04808 | 131624.6676
4 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.683 | 1869793.0107 | 0.3011 | 824296.7431 | 0.1975 | 540679.5309 | 0.1066 | 291830.0658 |  |  |  | 0.4823 | 1320353.1026 |  | 3262802.3852 | 362533.5984 |  | 0 | 0 |  |  |  |  | 3262802.3852 | 362533.5984 |  |  | 0.0625 | 171101.1174 | 0.039 | 106767.0972 | 0.0256 | 70083.0177 |  |  |  | 0.01749 | 47879.5679
5 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.6209 | 1699786.9405 | 0.223 | 610488.7868 | 0.1317 | 360544.2745 | 0.0609 | 166720.9288 |  |  |  | 0.4019 | 1100248.6252 |  | 2936522.1467 | 326280.2385 |  | 0 | 0 |  |  |  |  | 2936522.1467 | 326280.2385 |  |  | 0.03125 | 85550.5587 | 0.0173 | 47360.7893 | 0.0102 | 27923.7024 |  |  |  | 0.00636 | 17411.2497
6 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.5645 | 1545385.2922 | 0.1652 | 452254.4735 | 0.0878 | 240362.8497 | 0.0348 | 95269.1022 |  |  |  | 0.3349 | 916828.2274 |  | 2642869.932 | 293652.2147 |  | 0 | 0 |  |  |  |  | 2642869.932 | 293652.2147 |  |  | 0.01563 | 42788.9674 | 0.0077 | 21079.6577 | 0.0041 | 11224.2333 |  |  |  | 0.00231 | 6323.8973
7 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.5132 | 1404945.495 | 0.1224 | 335084.4283 | 0.0585 | 160150.6459 | 0.0199 | 54478.5958 |  |  |  | 0.2791 | 764069.1498 |  | 2378582.9388 | 264286.9932 |  | 0 | 0 |  |  |  |  | 2378582.9388 | 264286.9932 |  |  | 0.00781 | 21380.7956 | 0.0034 | 9307.9008 | 0.0016 | 4380.1886 |  |  |  | 0.00084 | 2299.599
8 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.4665 | 1277098.7401 | 0.0906 | 248028.1798 | 0.039 | 106767.0972 | 0.0199 | 54478.5958 |  |  |  | 0.2326 | 636769.9184 |  | 2140724.6449 | 237858.2939 |  | 0 | 0 |  |  |  |  | 2140724.6449 | 237858.2939 |  |  | 0.00391 | 10704.0859 | 0.0015 | 4106.4268 | 0.000665 | 1820.5159 |  |  |  | 0.000306 | 837.7111
9 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.4241 | 1161023.7421 | 0.0671 | 183694.1596 | 0.026 | 71178.0648 | 0.0065 | 17794.5162 |  |  |  | 0.1938 | 530550.3448 |  | 1926652.1804 | 214072.4645 |  | 0 | 0 |  |  |  |  | 1926652.1804 | 214072.4645 |  |  | 0.00195 | 5338.3549 | 0.0007 | 1916.3325 | 0.000262 | 717.2559 |  |  |  | 0.000111 | 303.8756
10 | 1491750 | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 4229367.8781 | 0.3855 | 1630421.317 | 0.0497 | 210199.5835 | 0.0173 | 73168.0643 | 0.0037 | 15648.6611 |  |  |  | 0.1615 | 683042.9123 |  | 1733986.9624 | 192665.218 |  | 0 | 0 |  |  |  | 0 | 1733986.9624 | 192665.218 |  |  | 0.00098 | 4144.7805 | 0.0003 | 1268.8104 | 0.000105 | 444.0836 |  |  |  | 4e-05 | 169.1747
11 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.3505 | 959535.0663 | 0.0368 | 100744.3379 | 0.116 | 317563.6739 | 0.0021 | 5748.9975 |  |  |  | 0.1346 | 368483.3664 |  | 1560588.2662 | 173398.6962 |  |  |  |  | 0 | 0 |  | 1560588.2662 | 173398.6962 |  |  | 0.00049 | 1341.4328 | 0.00013 | 355.8903 | 4.2e-05 | 114.98 |  |  |  | 1.47e-05 | 40.243
12 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.3186 | 872205.056 | 0.0273 | 74736.9681 | 0.0077 | 21079.6577 | 0.0012 | 3285.1415 |  |  |  | 0.1122 | 307160.7259 |  | 1387189.5699 | 173398.6962 |  |  |  |  | 0 | 0 |  | 1387189.5699 | 173398.6962 |  |  | 0.00024 | 657.0283 | 5.9e-05 | 161.5195 | 1.7e-05 | 46.5395 |  |  |  | 5.3e-06 | 14.5094
13 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.2897 | 793087.8993 | 0.0273 | 74736.9681 | 0.0051 | 13961.8512 | 0.0007 | 1916.3325 |  |  |  | 0.0935 | 255967.2716 |  | 1213790.8737 | 173398.6962 |  |  |  |  | 0 | 0 |  | 1213790.8737 | 173398.6962 |  |  | 0.00012 | 328.5141 | 2.6e-05 | 71.1781 | 6.7e-06 | 18.342 |  |  |  | 1.9e-06 | 5.2015
14 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.2633 | 720814.7873 | 0.0202 | 55299.8811 | 0.0034 | 9307.9008 | 0.0004 | 1095.0472 |  |  |  | 0.0779 | 213260.4327 |  | 1040392.1774 | 173398.6962 |  |  |  |  | 0 | 0 |  | 1040392.1774 | 173398.6962 |  |  | 6e-05 | 164.2571 | 1.2e-05 | 32.8514 | 2.7e-06 | 7.3916 |  |  |  | 7e-07 | 1.9163
15 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.2394 | 655385.72 | 0.015 | 41064.2682 | 0.0023 | 6296.5211 | 0.0002 | 547.5236 |  |  |  | 0.0649 | 177671.4003 |  | 866993.4812 | 173398.6962 |  |  |  |  | 0 | 0 |  | 866993.4812 | 173398.6962 |  |  | 3e-05 | 82.1285 | 5e-06 | 13.6881 | 1.1e-06 | 3.0114 |  |  |  | 3e-07 | 0.82129
16 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.2176 | 595705.6503 | 0.0111 | 30387.5584 | 0.0015 | 4106.4268 | 0.0001 | 273.7618 |  |  |  | 0.0541 | 148105.1272 |  | 693594.785 | 173398.6962 |  |  |  |  | 0 | 0 |  | 693594.785 | 173398.6962 |  |  | 1e-05 | 27.3762 | 2.3e-06 | 6.2965 | 4e-07 | 1.095 |  |  |  | 9e-08 | 0.24639
17 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.1978 | 541500.8163 | 0.0082 | 22448.4666 | 0.001 | 2737.6179 | 0.0001 | 273.7618 |  |  |  | 0.0451 | 123466.5663 |  | 520196.0887 | 173398.6962 |  |  |  |  | 0 | 0 |  | 520196.0887 | 173398.6962 |  |  | 8e-06 | 21.9009 | 1e-06 | 2.7376 | 2e-07 | 0.54752 |  |  |  | 3e-08 | 0.082129
18 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.1799 | 492497.4563 | 0.0045 | 12319.2805 | 0.0007 | 1916.3325 | 7e-05 | 191.6333 |  |  |  | 0.0376 | 102934.4322 |  | 346797.3925 | 173398.6962 |  |  |  |  | 0 | 0 |  | 346797.3925 | 173398.6962 |  |  | 4e-06 | 10.9505 | 5e-07 | 1.3688 | 1e-07 | 0.27376 |  |  |  | 1e-08 | 0.027376
19 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.1635 | 447600.5231 | 0.0033 | 9034.139 | 0.0005 | 1368.8089 | 2e-05 | 54.7524 |  |  |  | 0.0313 | 85687.4396 |  | 173398.6962 | 173398.6962 |  |  |  |  | 0 | 0 |  | 173398.6962 | 173398.6962 |  |  | 2e-07 | 0.54752 | 2e-07 | 0.54752 | 3e-08 | 0.082129 |  |  |  | 0 | 0
20 |  | 0 | 4147905.8759 | 0 | 4147905.8759 | 2737617.8781 | 0 | 2737617.8781 | 0.1486 | 406810.0167 | 0.0025 | 6844.0447 | 0.0003 | 821.2854 | 1e-05 | 27.3762 |  |  |  | 0.0261 | 71451.8266 |  | 0 | 173398.6962 |  |  |  |  | 0 | 0 |  | 0 | 173398.6962 |  |  | 1e-07 | 0.27376 | 1e-07 | 0.27376 | 1e-08 | 0.027376 |  |  |  | 0 | 0
| -3481276.0405 |  | 82958117.5182 |  | 82958117.5182 | 54752357.562 | 0 | 51271081.5214 |  | 18908479.6279 |  | 3279747.3453 |  | 811907.9646 |  | -1294444.6585 | 0.40246 | 0.54935 | 0.59636 |  | 8599543.1272 | [9 empty] | -4973026.0405 |  | 4973026.0405 |  |  |  | -2233967.3271 |  | -2882034.6758 |  | -3542184.1714 | 0.40556 | 0.13822 | 0.15857 |  | -4304578.2523 | 0.33847
Alternative 5 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -4973026.0405 | [6 empty] | -4973026.0405 | 1 | -4973026.0405 | 1 | -4973026.0405 | 1 | -4973026.0405 | 1 | -4973026.0405 |  |  |  | 1 | -4973026.0405 | -4973026.0405 |  |  | 0 | [5 empty] | -4973026.0405 |  |  |  |  | 1 | -4973026.0405 | 1 | -4973026.0405 | 1 | -4973026.0405 |  |  |  | 1 | -4973026.0405
1 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.9091 | 2934554.3946 | 0.7407 | 2390962.9744 | 0.6667 | 2152092.6354 | 0.5714 | 1844466.3745 |  |  |  | 0.8333 | 2689873.6959 |  | 4475723.4365 | 497302.6041 |  | 0 | 0 |  |  |  |  | 4475723.4365 | 497302.6041 |  |  | 0.5 | 1613988.7771 | 0.4444 | 1434513.2251 | 0.4 | 1291191.0217 |  |  |  | 0.03636 | 117369.2639
2 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.8264 | 2667600.6508 | 0.6669 | 2152738.2309 | 0.4444 | 1434513.2251 | 0.3265 | 1053934.6715 |  |  |  | 0.6944 | 2241507.6137 |  | 4028151.0928 | 447572.3436 |  | 0 | 0 |  |  |  |  | 4028151.0928 | 447572.3436 |  |  | 0.25 | 806994.3886 | 0.1613 | 520672.7795 | 0.016 | 51647.6409 |  |  |  | 0.13223 | 426835.472
3 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.7513 | 2425179.5365 | 0.4046 | 1306039.7184 | 0.2963 | 956449.7493 | 0.1866 | 602340.6116 |  |  |  | 0.5787 | 1868030.6106 |  | 3625335.9836 | 402815.1093 |  | 0 | 0 |  |  |  |  | 3625335.9836 | 402815.1093 |  |  | 0.125 | 403497.1943 | 0.0878 | 283416.4293 | 0.064 | 206590.5635 |  |  |  | 0.04808 | 155201.1608
4 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.683 | 2204708.6695 | 0.3011 | 971944.0416 | 0.1975 | 637525.567 | 0.1066 | 344102.4073 |  |  |  | 0.4823 | 1556853.5744 |  | 3262802.3852 | 362533.5984 |  | 0 | 0 |  |  |  |  | 3262802.3852 | 362533.5984 |  |  | 0.0625 | 201748.5971 | 0.039 | 125891.1246 | 0.0256 | 82636.2254 |  |  |  | 0.01749 | 56455.7134
5 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.6209 | 2004251.2634 | 0.223 | 719838.9946 | 0.1317 | 425124.6439 | 0.0609 | 196583.8331 |  |  |  | 0.4019 | 1297324.179 |  | 2936522.1467 | 326280.2385 |  | 0 | 0 |  |  |  |  | 2936522.1467 | 326280.2385 |  |  | 0.03125 | 100874.2986 | 0.0173 | 55844.0117 | 0.0102 | 32925.3711 |  |  |  | 0.00636 | 20529.9372
6 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.5645 | 1822193.3294 | 0.1652 | 533261.892 | 0.0878 | 283416.4293 | 0.0348 | 112333.6189 |  |  |  | 0.3349 | 1081049.6829 |  | 2642869.932 | 293652.2147 |  | 0 | 0 |  |  |  |  | 2642869.932 | 293652.2147 |  |  | 0.01563 | 50453.2892 | 0.0077 | 24855.4272 | 0.0041 | 13234.708 |  |  |  | 0.00231 | 7456.6282
7 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.5132 | 1656598.0808 | 0.1224 | 395104.4526 | 0.0585 | 188836.6869 | 0.0199 | 64236.7533 |  |  |  | 0.2791 | 900928.5354 |  | 2378582.9388 | 264286.9932 |  | 0 | 0 |  |  |  |  | 2378582.9388 | 264286.9932 |  |  | 0.00781 | 25210.5047 | 0.0034 | 10975.1237 | 0.0016 | 5164.7641 |  |  |  | 0.00084 | 2711.5011
8 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.4665 | 1505851.529 | 0.0906 | 292454.7664 | 0.039 | 125891.1246 | 0.0199 | 64236.7533 |  |  |  | 0.2326 | 750827.5791 |  | 2140724.6449 | 237858.2939 |  | 0 | 0 |  |  |  |  | 2140724.6449 | 237858.2939 |  |  | 0.00391 | 12621.3922 | 0.0015 | 4841.9663 | 0.000665 | 2146.6051 |  |  |  | 0.000306 | 987.7611
9 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.4241 | 1368985.2807 | 0.0671 | 216597.2939 | 0.026 | 83927.4164 | 0.0065 | 20981.8541 |  |  |  | 0.1938 | 625582.05 |  | 1926652.1804 | 214072.4645 |  | 0 | 0 |  |  |  |  | 1926652.1804 | 214072.4645 |  |  | 0.00195 | 6294.5562 | 0.0007 | 2259.5843 | 0.000262 | 845.7301 |  |  |  | 0.000111 | 358.3055
10 | 1491750 | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 4719727.5542 | 0.3855 | 1819454.9722 | 0.0497 | 234570.4594 | 0.0173 | 81651.2867 | 0.0037 | 17462.992 |  |  |  | 0.1615 | 762236 |  | 1733986.9624 | 192665.218 |  | 0 | 0 | 0 |  |  | 0 | 1733986.9624 | 192665.218 |  |  | 0.00098 | 4625.333 | 0.0003 | 1415.9183 | 0.000105 | 495.5714 |  |  |  | 4e-05 | 188.7891
11 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.3505 | 1131406.1328 | 0.0368 | 118789.574 | 0.116 | 374445.3963 | 0.0021 | 6778.7529 |  |  |  | 0.1346 | 434485.7788 |  | 1560588.2662 | 173398.6962 |  |  |  |  | 0 | 0 |  | 1560588.2662 | 173398.6962 |  |  | 0.00049 | 1581.709 | 0.00013 | 419.6371 | 4.2e-05 | 135.5751 |  |  |  | 1.47e-05 | 47.4513
12 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.3186 | 1028433.6488 | 0.0273 | 88123.7872 | 0.0077 | 24855.4272 | 0.0012 | 3873.5731 |  |  |  | 0.1122 | 362179.0816 |  | 1387189.5699 | 173398.6962 |  |  |  |  | 0 | 0 |  | 1387189.5699 | 173398.6962 |  |  | 0.00024 | 774.7146 | 5.9e-05 | 190.4507 | 1.7e-05 | 54.8756 |  |  |  | 5.3e-06 | 17.1083
13 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.2897 | 935145.0975 | 0.0273 | 88123.7872 | 0.0051 | 16462.6855 | 0.0007 | 2259.5843 |  |  |  | 0.0935 | 301815.9013 |  | 1213790.8737 | 173398.6962 |  |  |  |  | 0 | 0 |  | 1213790.8737 | 173398.6962 |  |  | 0.00012 | 387.3573 | 2.6e-05 | 83.9274 | 6.7e-06 | 21.6274 |  |  |  | 1.9e-06 | 6.1332
14 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.2633 | 849926.49 | 0.0202 | 65205.1466 | 0.0034 | 10975.1237 | 0.0004 | 1291.191 |  |  |  | 0.0779 | 251459.4515 |  | 1040392.1774 | 173398.6962 |  |  |  |  | 0 | 0 |  | 1040392.1774 | 173398.6962 |  |  | 6e-05 | 193.6787 | 1.2e-05 | 38.7357 | 2.7e-06 | 8.7155 |  |  |  | 7e-07 | 2.2596
15 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.2394 | 772777.8265 | 0.015 | 48419.6633 | 0.0023 | 7424.3484 | 0.0002 | 645.5955 |  |  |  | 0.0649 | 209495.7433 |  | 866993.4812 | 173398.6962 |  |  |  |  | 0 | 0 |  | 866993.4812 | 173398.6962 |  |  | 3e-05 | 96.8393 | 5e-06 | 16.1399 | 1.1e-06 | 3.5508 |  |  |  | 3e-07 | 0.96839
16 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.2176 | 702407.9158 | 0.0111 | 35830.5509 | 0.0015 | 4841.9663 | 0.0001 | 322.7978 |  |  |  | 0.0541 | 174633.5857 |  | 693594.785 | 173398.6962 |  |  |  |  | 0 | 0 |  | 693594.785 | 173398.6962 |  |  | 1e-05 | 32.2798 | 2.3e-06 | 7.4243 | 4e-07 | 1.2912 |  |  |  | 9e-08 | 0.29052
17 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.1978 | 638493.9602 | 0.0082 | 26469.4159 | 0.001 | 3227.9776 | 0.0001 | 322.7978 |  |  |  | 0.0451 | 145581.7877 |  | 520196.0887 | 173398.6962 |  |  |  |  | 0 | 0 |  | 520196.0887 | 173398.6962 |  |  | 8e-06 | 25.8238 | 1e-06 | 3.228 | 2e-07 | 0.6456 |  |  |  | 3e-08 | 0.096839
18 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.1799 | 580713.162 | 0.0045 | 14525.899 | 0.0007 | 2259.5843 | 7e-05 | 225.9584 |  |  |  | 0.0376 | 121371.956 |  | 346797.3925 | 173398.6962 |  |  |  |  | 0 | 0 |  | 346797.3925 | 173398.6962 |  |  | 4e-06 | 12.9119 | 5e-07 | 1.614 | 1e-07 | 0.3228 |  |  |  | 1e-08 | 0.03228
19 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.1635 | 527774.3301 | 0.0033 | 10652.3259 | 0.0005 | 1613.9888 | 2e-05 | 64.5596 |  |  |  | 0.0313 | 101035.6974 |  | 173398.6962 | 173398.6962 |  |  |  |  | 0 | 0 |  | 173398.6962 | 173398.6962 |  |  | 2e-07 | 0.6456 | 2e-07 | 0.6456 | 3e-08 | 0.096839 |  |  |  | 0 | 0
20 |  | 0 | 4890875.0822 | 0 | 4890875.0822 | 3227977.5542 | 0 | 3227977.5542 | 0.1486 | 479677.4646 | 0.0025 | 8069.9439 | 0.0003 | 968.3933 | 1e-05 | 32.2798 |  |  |  | 0.0261 | 84250.2142 |  | 0 | 173398.6962 |  |  |  |  | 0 | 0 |  | 0 | 173398.6962 |  |  | 1e-07 | 0.3228 | 1e-07 | 0.3228 | 1e-08 | 0.03228 |  |  |  | 0 | 0
| -3481276.0405 |  | 97817501.6433 |  | 97817501.6433 | 64559551.0846 | 0 | 61078275.044 |  | 23083107.6946 |  | 4744696.8777 |  | 1843477.6153 |  | -636529.081 | 0.41468 | 0.59531 | 0.68583 |  | 10987496.678 | [9 empty] | -4973026.0405 |  | 4973026.0405 |  |  |  | -1743611.4267 |  | -2507578.3251 |  | -3285921.1063 | 0.60626 | 0.42942 | 0.44458 |  | -4184857.1678 | 0.58616
Alternative 6 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -4130900.5922 | [6 empty] | -4130900.5922 | 1 | -4130900.5922 | 1 | -4130900.5922 | 1 | -4130900.5922 | 1 | -4130900.5922 |  |  |  | 1 | -4130900.5922 | -4061728.0922 |  |  | -69172.5 | [5 empty] | -4130900.5922 |  |  |  |  | 1 | -4130900.5922 | 1 | -4130900.5922 | 1 | -4130900.5922 |  |  |  | 1 | -4130900.5922
1 |  | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2214605.48 | 0.9091 | 2013297.8419 | 0.7407 | 1640358.279 | 0.6667 | 1476477.4735 | 0.5714 | 1265425.5713 |  |  |  | 0.8333 | 1845430.7465 |  | 3655555.283 | 406172.8092 |  | 55338 | 13834.5 | [6 empty] | 3717810.533 | 413090.0592 | 0.5 | 1107302.74 | 0.4444 | 984170.6753 | 0.4 | 885842.192 |  |  |  | 0.03636 | 80523.0553
2 |  | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2214605.48 | 0.8264 | 1830149.9687 | 0.6669 | 1476920.3946 | 0.4444 | 984170.6753 | 0.3265 | 723068.6892 |  |  |  | 0.6944 | 1537822.0453 |  | 3289999.7547 | 365555.5283 |  | 44270.4 | 11067.6 | [6 empty] | 3346029.4797 | 371781.0533 | 0.25 | 553651.37 | 0.1613 | 357215.8639 | 0.016 | 35433.6877 |  |  |  | 0.13223 | 292837.2826
3 |  | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2214605.48 | 0.7513 | 1663833.0971 | 0.4046 | 896029.3772 | 0.2963 | 656187.6037 | 0.1866 | 413245.3826 |  |  |  | 0.5787 | 1281592.1913 |  | 2960999.7792 | 328999.9755 |  | 35416.32 | 8854.08 | [6 empty] | 3011426.5317 | 334602.948 | 0.125 | 276825.685 | 0.0878 | 194442.3611 | 0.064 | 141734.7507 |  |  |  | 0.04808 | 106478.2315
4 |  | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2214605.48 | 0.683 | 1512575.5428 | 0.3011 | 666817.71 | 0.1975 | 437384.5823 | 0.1066 | 236076.9442 |  |  |  | 0.4823 | 1068104.223 |  | 2664899.8013 | 296099.9779 |  | 28333.056 | 7083.264 | [6 empty] | 2710283.8786 | 301142.6532 | 0.0625 | 138412.8425 | 0.039 | 86369.6137 | 0.0256 | 56693.9003 |  |  |  | 0.01749 | 38732.3425
5 |  | 0 | 3131351.6153 | 0 | 3131351.6153 | 2066692.0661 | 0 | 2066692.0661 | 0.6209 | 1283209.1038 | 0.223 | 460872.3307 | 0.1317 | 272183.3451 | 0.0609 | 125861.5468 |  |  |  | 0.4019 | 830603.5414 |  | 2398409.8212 | 266489.9801 |  | 22666.4448 | 5666.6112 | [6 empty] | 2439255.4907 | 271028.3879 | 0.03125 | 64584.1271 | 0.0173 | 35753.7727 | 0.0102 | 21080.2591 |  |  |  | 0.00636 | 13144.1615
6 |  | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2214605.48 | 0.5645 | 1250144.7935 | 0.1652 | 365852.8253 | 0.0878 | 194442.3611 | 0.0348 | 77068.2707 |  |  |  | 0.3349 | 741671.3752 |  | 2158568.8391 | 239840.9821 |  | 18133.1558 | 4533.289 | [6 empty] | 2195329.9416 | 243925.5491 | 0.01563 | 34614.2837 | 0.0077 | 17052.4622 | 0.0041 | 9079.8825 |  |  |  | 0.00231 | 5115.7387
7 |  | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2214605.48 | 0.5132 | 1136535.5323 | 0.1224 | 271067.7108 | 0.0585 | 129554.4206 | 0.0199 | 44070.6491 |  |  |  | 0.2791 | 618096.3895 |  | 1942711.9551 | 215856.8839 |  | 13599.8669 | 4533.289 | [6 empty] | 1975796.9475 | 219532.9942 | 0.00781 | 17296.0688 | 0.0034 | 7529.6586 | 0.0016 | 3543.3688 |  |  |  | 0.00084 | 1860.2686
8 |  | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2214605.48 | 0.4665 | 1033113.4564 | 0.0906 | 200643.2565 | 0.039 | 86369.6137 | 0.0199 | 44070.6491 |  |  |  | 0.2326 | 515117.2346 |  | 1748440.7596 | 194271.1955 |  | 9066.5779 | 4533.289 | [6 empty] | 1778217.2527 | 197579.6947 | 0.00391 | 8659.1074 | 0.0015 | 3321.9082 | 0.000665 | 1472.7126 |  |  |  | 0.000306 | 677.6693
9 |  | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2214605.48 | 0.4241 | 939214.1841 | 0.0671 | 148600.0277 | 0.026 | 57579.7425 | 0.0065 | 14394.9356 |  |  |  | 0.1938 | 429190.542 |  | 1573596.6837 | 174844.076 |  | 4533.289 | 4533.289 | [6 empty] | 1600395.5274 | 177821.7253 | 0.00195 | 4318.4807 | 0.0007 | 1550.2238 | 0.000262 | 580.2266 |  |  |  | 0.000111 | 245.8212
10 | -69172.5 | 0 | 3355462.8485 | 0 | 3355462.8485 | 2214605.48 | 0 | 2145432.98 | 0.3855 | 827064.4138 | 0.0497 | 106628.0191 | 0.0173 | 37115.9906 | 0.0037 | 7938.102 |  |  |  | 0.1615 | 346487.4263 |  | 1416237.0153 | 157359.6684 |  | 0 | 4533.289 | -69172.5 |  |  | -69172.5 |  |  | 1440355.9747 | 160039.5527 | 0.00098 | 2102.5243 | 0.0003 | 643.6299 | 0.000105 | 225.2705 |  |  |  | 4e-05 | 85.8173
11 |  | 55338 | 3355462.8485 | 13834.5 | 3336094.5485 | 2201822.402 | 6585.222 | 2208407.624 | 0.3505 | 774046.8722 | 0.0368 | 81269.4006 | 0.116 | 256175.2844 | 0.0021 | 4637.656 |  |  |  | 0.1346 | 297251.6662 |  | 1274613.3138 | 141623.7015 | [9 empty] | 1296320.3772 | 144035.5975 | 0.00049 | 1082.1197 | 0.00013 | 287.093 | 4.2e-05 | 92.7531 |  |  |  | 1.47e-05 | 32.4636
12 |  | 44270.4 | 3355462.8485 | 11067.6 | 3339968.2085 | 2204379.0176 | 5268.1776 | 2209647.1952 | 0.3186 | 703993.5964 | 0.0273 | 60323.3684 | 0.0077 | 17014.2834 | 0.0012 | 2651.5766 |  |  |  | 0.1122 | 247922.4153 |  | 1132989.6122 | 141623.7015 | [9 empty] | 1152284.7798 | 144035.5975 | 0.00024 | 530.3153 | 5.9e-05 | 130.3692 | 1.7e-05 | 37.564 |  |  |  | 5.3e-06 | 11.7111
13 |  | 35416.32 | 3355462.8485 | 8854.08 | 3343067.1365 | 2206424.3101 | 4214.5421 | 2210638.8521 | 0.2897 | 640422.0755 | 0.0273 | 60350.4407 | 0.0051 | 11274.2581 | 0.0007 | 1547.4472 |  |  |  | 0.0935 | 206694.7327 |  | 991365.9107 | 141623.7015 | [9 empty] | 1008249.1823 | 144035.5975 | 0.00012 | 265.2767 | 2.6e-05 | 57.4766 | 6.7e-06 | 14.8113 |  |  |  | 1.9e-06 | 4.2002
14 |  | 28333.056 | 3355462.8485 | 7083.264 | 3345546.2789 | 2208060.5441 | 3371.6337 | 2211432.1777 | 0.2633 | 582270.0924 | 0.0202 | 44670.93 | 0.0034 | 7518.8694 | 0.0004 | 884.5729 |  |  |  | 0.0779 | 172270.5666 |  | 849742.2092 | 141623.7015 | [9 empty] | 864213.5848 | 144035.5975 | 6e-05 | 132.6859 | 1.2e-05 | 26.5372 | 2.7e-06 | 5.9709 |  |  |  | 7e-07 | 1.548
15 |  | 22666.4448 | 3355462.8485 | 5666.6112 | 3347529.5928 | 2209369.5312 | 2697.3069 | 2212066.8382 | 0.2394 | 529568.8011 | 0.015 | 33181.0026 | 0.0023 | 5087.7537 | 0.0002 | 442.4134 |  |  |  | 0.0649 | 143563.1378 |  | 708118.5077 | 141623.7015 | [9 empty] | 720177.9874 | 144035.5975 | 3e-05 | 66.362 | 5e-06 | 11.0603 | 1.1e-06 | 2.4333 |  |  |  | 3e-07 | 0.66362
16 |  | 18133.1558 | 3355462.8485 | 4533.289 | 3349116.2439 | 2210416.721 | 2157.8455 | 2212574.5665 | 0.2176 | 481456.2257 | 0.0111 | 24559.5777 | 0.0015 | 3318.8618 | 0.0001 | 221.2575 |  |  |  | 0.0541 | 119700.284 |  | 566494.8061 | 141623.7015 | [9 empty] | 576142.3899 | 144035.5975 | 1e-05 | 22.1257 | 2.3e-06 | 5.0889 | 4e-07 | 0.88503 |  |  |  | 9e-08 | 0.19913
17 |  | 13599.8669 | 3355462.8485 | 4533.289 | 3349569.5728 | 2210715.9181 | 2003.7137 | 2212719.6318 | 0.1978 | 437675.9432 | 0.0082 | 18144.301 | 0.001 | 2212.7196 | 0.0001 | 221.272 |  |  |  | 0.0451 | 99793.6554 |  | 424871.1046 | 141623.7015 | [9 empty] | 432106.7924 | 144035.5975 | 8e-06 | 17.7018 | 1e-06 | 2.2127 | 2e-07 | 0.44254 |  |  |  | 3e-08 | 0.066382
18 |  | 9066.5779 | 3355462.8485 | 4533.289 | 3350022.9017 | 2211015.1151 | 1849.5819 | 2212864.697 | 0.1799 | 398094.359 | 0.0045 | 9957.8911 | 0.0007 | 1549.0053 | 7e-05 | 154.9005 |  |  |  | 0.0376 | 83203.7126 |  | 283247.4031 | 141623.7015 | [9 empty] | 288071.1949 | 144035.5975 | 4e-06 | 8.8515 | 5e-07 | 1.1064 | 1e-07 | 0.22129 |  |  |  | 1e-08 | 0.022129
19 |  | 4533.289 | 3355462.8485 | 4533.289 | 3350476.2306 | 2211314.3122 | 1695.4501 | 2213009.7623 | 0.1635 | 361827.0961 | 0.0033 | 7302.9322 | 0.0005 | 1106.5049 | 2e-05 | 44.2602 |  |  |  | 0.0313 | 69267.2056 |  | 141623.7015 | 141623.7015 | [9 empty] | 144035.5975 | 144035.5975 | 2e-07 | 0.4426 | 2e-07 | 0.4426 | 3e-08 | 0.06639 |  |  |  | 0 | 0
20 |  | 0 | 3355462.8485 | 4533.289 | 3350929.5595 | 2211613.5093 | 1541.3182 | 2213154.8275 | 0.1486 | 328874.8074 | 0.0025 | 5532.8871 | 0.0003 | 663.9464 | 1e-05 | 22.1315 |  |  |  | 0.0261 | 57763.341 |  | 0 | 141623.7015 | [9 empty] | -2.3283e-10 | 144035.5975 | 1e-07 | 0.22132 | 1e-07 | 0.22132 | 1e-08 | 0.022132 |  |  |  | 0 | 0
| -4200073.0922 |  | 66885145.7361 |  | 66792837.5251 | 44083272.7666 | 31384.7918 | 39914584.4661 |  | 14596467.211 |  | 2448182.07 |  | 506486.7034 |  | -1168852.364 | 0.40038 | 0.53913 | 0.57558 |  | 6580645.8401 | [9 empty] | -4200073.0922 |  | 0 |  |  |  | -1921007.2602 |  | -2442328.8143 |  | -2975059.1716 | 0.3615 | 0.07878 | 0.10386 |  | -3591149.3295 | 0.29277
Alternative 7 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -4858379.0405 | [6 empty] | -4858379.0405 | 1 | -4858379.0405 | 1 | -4858379.0405 | 1 | -4858379.0405 | 1 | -4858379.0405 |  |  |  | 1 | -4858379.0405 | -4858379.0405 |  |  | 0 | [5 empty] | -4858379.0405 |  |  |  |  | 1 | -4858379.0405 | 1 | -4858379.0405 | 1 | -4858379.0405 |  |  |  | 1 | -4858379.0405
1 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.9091 | 2618362.4973 | 0.7407 | 2133341.8785 | 0.6667 | 1920209.3025 | 0.5714 | 1645729.1068 |  |  |  | 0.8333 | 2400045.6154 |  | 4372541.1365 | 485837.9041 |  | 0 | 0 |  |  |  |  | 4372541.1365 | 485837.9041 |  |  | 0.5 | 1440084.9727 | 0.4444 | 1279947.5237 | 0.4 | 1152067.9781 |  |  |  | 0.03636 | 104722.9792
2 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.8264 | 2380172.4428 | 0.6669 | 1920785.3365 | 0.4444 | 1279947.5237 | 0.3265 | 940375.4871 |  |  |  | 0.6944 | 1999990.01 |  | 3935287.0228 | 437254.1136 |  | 0 | 0 |  |  |  |  | 3935287.0228 | 437254.1136 |  |  | 0.25 | 720042.4863 | 0.1613 | 464571.4122 | 0.016 | 46082.7191 |  |  |  | 0.13223 | 380844.8719
3 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.7513 | 2163871.6799 | 0.4046 | 1165316.7599 | 0.2963 | 853394.3548 | 0.1866 | 537439.7118 |  |  |  | 0.5787 | 1666754.3474 |  | 3541758.3206 | 393528.7023 |  | 0 | 0 |  |  |  |  | 3541758.3206 | 393528.7023 |  |  | 0.125 | 360021.2432 | 0.0878 | 252878.9212 | 0.064 | 184330.8765 |  |  |  | 0.04808 | 138478.571
4 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.683 | 1967156.0727 | 0.3011 | 867219.1705 | 0.1975 | 568833.5642 | 0.1066 | 307026.1162 |  |  |  | 0.4823 | 1389105.9646 |  | 3187582.4885 | 354175.8321 |  | 0 | 0 |  |  |  |  | 3187582.4885 | 354175.8321 |  |  | 0.0625 | 180010.6216 | 0.039 | 112326.6279 | 0.0256 | 73732.3506 |  |  |  | 0.01749 | 50372.7323
5 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.6209 | 1788297.5191 | 0.223 | 642277.8978 | 0.1317 | 379318.3818 | 0.0609 | 175402.3497 |  |  |  | 0.4019 | 1157540.301 |  | 2868824.2397 | 318758.2489 |  | 0 | 0 |  |  |  |  | 2868824.2397 | 318758.2489 |  |  | 0.03125 | 90005.3108 | 0.0173 | 49826.9401 | 0.0102 | 29377.7334 |  |  |  | 0.00636 | 18317.8809
6 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.5645 | 1625855.9341 | 0.1652 | 475804.075 | 0.0878 | 252878.9212 | 0.0348 | 100229.9141 |  |  |  | 0.3349 | 964568.9147 |  | 2581941.8157 | 286882.424 |  | 0 | 0 |  |  |  |  | 2581941.8157 | 286882.424 |  |  | 0.01563 | 45017.0562 | 0.0077 | 22177.3086 | 0.0041 | 11808.6968 |  |  |  | 0.00231 | 6653.1926
7 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.5132 | 1478103.2159 | 0.1224 | 352532.8013 | 0.0585 | 168489.9418 | 0.0199 | 57315.3819 |  |  |  | 0.2791 | 803855.4317 |  | 2323747.6341 | 258194.1816 |  | 0 | 0 |  |  |  |  | 2323747.6341 | 258194.1816 |  |  | 0.00781 | 22494.1273 | 0.0034 | 9792.5778 | 0.0016 | 4608.2719 |  |  |  | 0.00084 | 2419.3428
8 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.4665 | 1343599.2795 | 0.0906 | 260943.397 | 0.039 | 112326.6279 | 0.0199 | 57315.3819 |  |  |  | 0.2326 | 669927.5293 |  | 2091372.8707 | 232374.7634 |  | 0 | 0 |  |  |  |  | 2091372.8707 | 232374.7634 |  |  | 0.00391 | 11261.4645 | 0.0015 | 4320.2549 | 0.000665 | 1915.313 |  |  |  | 0.000306 | 881.332
9 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.4241 | 1221480.0738 | 0.0671 | 193259.4033 | 0.026 | 74884.4186 | 0.0065 | 18721.1046 |  |  |  | 0.1938 | 558176.9354 |  | 1882235.5836 | 209137.2871 |  | 0 | 0 |  |  |  |  | 1882235.5836 | 209137.2871 |  |  | 0.00195 | 5616.3314 | 0.0007 | 2016.119 | 0.000262 | 754.6045 |  |  |  | 0.000111 | 319.6989
10 | 1491750 | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 4371919.9453 | 0.3855 | 1685375.1389 | 0.0497 | 217284.4213 | 0.0173 | 75634.2151 | 0.0037 | 16176.1038 |  |  |  | 0.1615 | 706065.0712 |  | 1694012.0253 | 188223.5584 |  | 0 | 0 | 0 |  |  | 0 | 1694012.0253 | 188223.5584 |  |  | 0.00098 | 4284.4815 | 0.0003 | 1311.576 | 0.000105 | 459.0516 |  |  |  | 4e-05 | 174.8768
11 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.3505 | 1009499.5658 | 0.0368 | 105990.254 | 0.116 | 334099.7137 | 0.0021 | 6048.3569 |  |  |  | 0.1346 | 387670.8746 |  | 1524610.8227 | 169401.2025 |  |  |  |  | 0 | 0 |  | 1524610.8227 | 169401.2025 |  |  | 0.00049 | 1411.2833 | 0.00013 | 374.4221 | 4.2e-05 | 120.9671 |  |  |  | 1.47e-05 | 42.3385
12 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.3186 | 917622.1446 | 0.0273 | 78628.6395 | 0.0077 | 22177.3086 | 0.0012 | 3456.2039 |  |  |  | 0.1122 | 323155.0679 |  | 1355209.6202 | 169401.2025 |  |  |  |  | 0 | 0 |  | 1355209.6202 | 169401.2025 |  |  | 0.00024 | 691.2408 | 5.9e-05 | 169.93 | 1.7e-05 | 48.9629 |  |  |  | 5.3e-06 | 15.2649
13 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.2897 | 834385.2332 | 0.0273 | 78628.6395 | 0.0051 | 14688.8667 | 0.0007 | 2016.119 |  |  |  | 0.0935 | 269295.8899 |  | 1185808.4177 | 169401.2025 |  |  |  |  | 0 | 0 |  | 1185808.4177 | 169401.2025 |  |  | 0.00012 | 345.6204 | 2.6e-05 | 74.8844 | 6.7e-06 | 19.2971 |  |  |  | 1.9e-06 | 5.4723
14 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.2633 | 758348.7466 | 0.0202 | 58179.4329 | 0.0034 | 9792.5778 | 0.0004 | 1152.068 |  |  |  | 0.0779 | 224365.2387 |  | 1016407.2152 | 169401.2025 |  |  |  |  | 0 | 0 |  | 1016407.2152 | 169401.2025 |  |  | 6e-05 | 172.8102 | 1.2e-05 | 34.562 | 2.7e-06 | 7.7765 |  |  |  | 7e-07 | 2.0161
15 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.2394 | 689512.6849 | 0.015 | 43202.5492 | 0.0023 | 6624.3909 | 0.0002 | 576.034 |  |  |  | 0.0649 | 186923.0295 |  | 847006.0126 | 169401.2025 |  |  |  |  | 0 | 0 |  | 847006.0126 | 169401.2025 |  |  | 3e-05 | 86.4051 | 5e-06 | 14.4008 | 1.1e-06 | 3.1682 |  |  |  | 3e-07 | 0.86405
16 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.2176 | 626724.9801 | 0.0111 | 31969.8864 | 0.0015 | 4320.2549 | 0.0001 | 288.017 |  |  |  | 0.0541 | 155817.194 |  | 677604.8101 | 169401.2025 |  |  |  |  | 0 | 0 |  | 677604.8101 | 169401.2025 |  |  | 1e-05 | 28.8017 | 2.3e-06 | 6.6244 | 4e-07 | 1.1521 |  |  |  | 9e-08 | 0.25922
17 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.1978 | 569697.6152 | 0.0082 | 23617.3936 | 0.001 | 2880.1699 | 0.0001 | 288.017 |  |  |  | 0.0451 | 129895.6645 |  | 508203.6076 | 169401.2025 |  |  |  |  | 0 | 0 |  | 508203.6076 | 169401.2025 |  |  | 8e-06 | 23.0414 | 1e-06 | 2.8802 | 2e-07 | 0.57603 |  |  |  | 3e-08 | 0.086405
18 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.1799 | 518142.5732 | 0.0045 | 12960.7648 | 0.0007 | 2016.119 | 7e-05 | 201.6119 |  |  |  | 0.0376 | 108294.3899 |  | 338802.4051 | 169401.2025 |  |  |  |  | 0 | 0 |  | 338802.4051 | 169401.2025 |  |  | 4e-06 | 11.5207 | 5e-07 | 1.4401 | 1e-07 | 0.28802 |  |  |  | 1e-08 | 0.028802
19 |  | 0 | 4363893.8565 | 0 | 4363893.8565 | 2880169.9453 | 0 | 2880169.9453 | 0.1635 | 470907.7861 | 0.0033 | 9504.5608 | 0.0005 | 1440.085 | 2e-05 | 57.6034 |  |  |  | 0.0313 | 90149.3193 |  | 169401.2025 | 169401.2025 |  |  |  |  | 0 | 0 |  | 169401.2025 | 169401.2025 |  |  | 2e-07 | 0.57603 | 2e-07 | 0.57603 | 3e-08 | 0.086405 |  |  |  | 0 | 0
20 |  | 0 | 3937511.2729 | 0 | 3937511.2729 | 2598757.4401 | 0 | 2598757.4401 | 0.1486 | 386175.3556 | 0.0025 | 6496.8936 | 0.0003 | 779.6272 | 1e-05 | 25.9876 |  |  |  | 0.0261 | 67827.5692 |  | 0 | 169401.2025 |  |  |  |  | 0 | 0 |  | 0 | 169401.2025 |  |  | 1e-07 | 0.25988 | 1e-07 | 0.25988 | 1e-08 | 0.025988 |  |  |  | 0 | 0
| -3366629.0405 |  | 86851494.5474 |  | 86851494.5474 | 57321986.4013 | 0 | 53955357.3607 |  | 20194911.4987 |  | 3819565.1148 |  | 1226357.3247 |  | -988538.364 | 0.40831 | 0.57094 | 0.63842 |  | 9401045.3178 | [9 empty] | -4858379.0405 |  | 4858379.0405 |  |  |  | -1976769.3857 |  | -2658529.7993 |  | -3353039.1446 | 0.49992 | 0.27512 | 0.29302 |  | -4155127.2321 | 0.4549
Alternative 8 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -4728391.5922 | [6 empty] | -4728391.5922 | 1 | -4728391.5922 | 1 | -4728391.5922 | 1 | -4728391.5922 | 1 | -4728391.5922 |  |  |  | 1 | -4728391.5922 | -4728391.5922 |  |  | -421063.5 | [5 empty] | -5149455.0922 |  |  |  |  | 1 | -4728391.5922 | 1 | -4728391.5922 | 1 | -4728391.5922 |  |  |  | 1 | -4728391.5922
1 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.9091 | 1428871.7127 | 0.7407 | 1164190.1634 | 0.6667 | 1047881.1691 | 0.5714 | 898094.0453 |  |  |  | 0.8333 | 1309733.5806 |  | 4255552.433 | 472839.1592 |  | 336850.8 | 84212.7 | [6 empty] | 4255552.433 | 472839.1592 | 0.5 | 785871.5833 | 0.4444 | 698482.6632 | 0.4 | 628697.2666 |  |  |  | 0.03636 | 57148.5815
2 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.8264 | 1298888.5528 | 0.6669 | 1048195.5177 | 0.4444 | 698482.6632 | 0.3265 | 513174.1439 |  |  |  | 0.6944 | 1091418.4548 |  | 3829997.1897 | 425555.2433 |  | 269480.64 | 67370.16 | [6 empty] | 3829997.1897 | 425555.2433 | 0.25 | 392935.7916 | 0.1613 | 253522.1728 | 0.016 | 25147.8907 |  |  |  | 0.13223 | 207831.5989
3 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.7513 | 1180850.641 | 0.4046 | 635927.2852 | 0.2963 | 465707.5002 | 0.1866 | 293287.2749 |  |  |  | 0.5787 | 909567.7705 |  | 3446997.4707 | 382999.719 |  | 215584.512 | 53896.128 | [6 empty] | 3446997.4707 | 382999.719 | 0.125 | 196467.8958 | 0.0878 | 137999.05 | 0.064 | 100591.5627 |  |  |  | 0.04808 | 75569.4114
4 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.683 | 1073500.5827 | 0.3011 | 473251.8674 | 0.1975 | 310419.2754 | 0.1066 | 167547.8215 |  |  |  | 0.4823 | 758051.7292 |  | 3102297.7237 | 344699.7471 |  | 172467.6096 | 43116.9024 | [6 empty] | 3102297.7237 | 344699.7471 | 0.0625 | 98233.9479 | 0.039 | 61297.9835 | 0.0256 | 40236.6251 |  |  |  | 0.01749 | 27489.0021
5 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.6209 | 975895.3321 | 0.223 | 350498.7261 | 0.1317 | 206998.575 | 0.0609 | 95719.1588 |  |  |  | 0.4019 | 631683.5786 |  | 2792067.9513 | 310229.7724 |  | 137974.0877 | 34493.5219 | [6 empty] | 2792067.9513 | 310229.7724 | 0.03125 | 49116.974 | 0.0173 | 27191.1568 | 0.0102 | 16031.7803 |  |  |  | 0.00636 | 9996.2865
6 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.5645 | 887249.0175 | 0.1652 | 259651.9711 | 0.0878 | 137999.05 | 0.0348 | 54696.6622 |  |  |  | 0.3349 | 526376.7865 |  | 2512861.1562 | 279206.7951 |  | 110379.2701 | 27594.8175 | [6 empty] | 2512861.1562 | 279206.7951 | 0.01563 | 24566.3457 | 0.0077 | 12102.4224 | 0.0041 | 6444.147 |  |  |  | 0.00231 | 3630.7267
7 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.5132 | 806618.5931 | 0.1224 | 192381.3636 | 0.0585 | 91946.9752 | 0.0199 | 31277.689 |  |  |  | 0.2791 | 438673.5178 |  | 2261575.0405 | 251286.1156 |  | 82784.4526 | 27594.8175 | [6 empty] | 2261575.0405 | 251286.1156 | 0.00781 | 12275.3141 | 0.0034 | 5343.9268 | 0.0016 | 2514.7891 |  |  |  | 0.00084 | 1320.2643
8 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.4665 | 733218.1872 | 0.0906 | 142399.9309 | 0.039 | 61297.9835 | 0.0199 | 31277.689 |  |  |  | 0.2326 | 365587.4605 |  | 2035417.5365 | 226157.5041 |  | 55189.6351 | 27594.8175 | [6 empty] | 2035417.5365 | 226157.5041 | 0.00391 | 6145.5158 | 0.0015 | 2357.6147 | 0.000665 | 1045.2092 |  |  |  | 0.000306 | 480.9534
9 |  | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1571743.1665 | 0.4241 | 666576.2769 | 0.0671 | 105463.9665 | 0.026 | 40865.3223 | 0.0065 | 10216.3306 |  |  |  | 0.1938 | 304603.8257 |  | 1831875.7828 | 203541.7536 |  | 27594.8175 | 27594.8175 | [6 empty] | 1831875.7828 | 203541.7536 | 0.00195 | 3064.8992 | 0.0007 | 1100.2202 | 0.000262 | 411.7967 |  |  |  | 0.000111 | 174.4635
10 | -421063.5 | 0 | 2381429.0402 | 0 | 2381429.0402 | 1571743.1665 | 0 | 1150679.6665 | 0.3855 | 443587.0114 | 0.0497 | 57188.7794 | 0.0173 | 19906.7582 | 0.0037 | 4257.5148 |  |  |  | 0.1615 | 185834.7661 |  | 1648688.2046 | 183187.5783 |  | 0 | 27594.8175 | -421063.5 |  |  | -421063.5 |  |  | 1648688.2046 | 183187.5783 | 0.00098 | 1127.6661 | 0.0003 | 345.2039 | 0.000105 | 120.8214 |  |  |  | 4e-05 | 46.0272
11 |  | 336850.8 | 2381429.0402 | 84212.7 | 2263531.2602 | 1493930.6317 | 40085.2452 | 1534015.8769 | 0.3505 | 537672.5649 | 0.0368 | 56451.7843 | 0.116 | 177945.8417 | 0.0021 | 3221.4333 |  |  |  | 0.1346 | 206478.537 |  | 1483819.3841 | 164868.8205 | [9 empty] | 1483819.3841 | 164868.8205 | 0.00049 | 751.6678 | 0.00013 | 199.4221 | 4.2e-05 | 64.4287 |  |  |  | 1.47e-05 | 22.55
12 |  | 269480.64 | 2381429.0402 | 67370.16 | 2287110.8162 | 1509493.1387 | 32068.1962 | 1541561.3348 | 0.3186 | 491141.4413 | 0.0273 | 42084.6244 | 0.0077 | 11870.0223 | 0.0012 | 1849.8736 |  |  |  | 0.1122 | 172963.1818 |  | 1318950.5636 | 164868.8205 | [9 empty] | 1318950.5636 | 164868.8205 | 0.00024 | 369.9747 | 5.9e-05 | 90.9521 | 1.7e-05 | 26.2065 |  |  |  | 5.3e-06 | 8.1703
13 |  | 215584.512 | 2381429.0402 | 53896.128 | 2305974.461 | 1521943.1442 | 25654.5569 | 1547597.7012 | 0.2897 | 448339.054 | 0.0273 | 42249.4172 | 0.0051 | 7892.7483 | 0.0007 | 1083.3184 |  |  |  | 0.0935 | 144700.3851 |  | 1154081.7432 | 164868.8205 | [9 empty] | 1154081.7432 | 164868.8205 | 0.00012 | 185.7117 | 2.6e-05 | 40.2375 | 6.7e-06 | 10.3689 |  |  |  | 1.9e-06 | 2.9404
14 |  | 172467.6096 | 2381429.0402 | 43116.9024 | 2321065.3768 | 1531903.1487 | 20523.6455 | 1552426.7942 | 0.2633 | 408753.9749 | 0.0202 | 31359.0212 | 0.0034 | 5278.2511 | 0.0004 | 620.9707 |  |  |  | 0.0779 | 120934.0473 |  | 989212.9227 | 164868.8205 | [9 empty] | 989212.9227 | 164868.8205 | 6e-05 | 93.1456 | 1.2e-05 | 18.6291 | 2.7e-06 | 4.1916 |  |  |  | 7e-07 | 1.0867
15 |  | 137974.0877 | 2381429.0402 | 34493.5219 | 2333138.1095 | 1539871.1523 | 16418.9164 | 1556290.0687 | 0.2394 | 372575.8424 | 0.015 | 23344.351 | 0.0023 | 3579.4672 | 0.0002 | 311.258 |  |  |  | 0.0649 | 101003.2255 |  | 824344.1023 | 164868.8205 | [9 empty] | 824344.1023 | 164868.8205 | 3e-05 | 46.6887 | 5e-06 | 7.7815 | 1.1e-06 | 1.7119 |  |  |  | 3e-07 | 0.46689
16 |  | 110379.2701 | 2381429.0402 | 27594.8175 | 2342796.2956 | 1546245.5551 | 13135.1331 | 1559380.6883 | 0.2176 | 339321.2378 | 0.0111 | 17309.1256 | 0.0015 | 2339.071 | 0.0001 | 155.9381 |  |  |  | 0.0541 | 84362.4952 |  | 659475.2818 | 164868.8205 | [9 empty] | 659475.2818 | 164868.8205 | 1e-05 | 15.5938 | 2.3e-06 | 3.5866 | 4e-07 | 0.62375 |  |  |  | 9e-08 | 0.14034
17 |  | 82784.4526 | 2381429.0402 | 27594.8175 | 2345555.7774 | 1548066.8131 | 12196.9094 | 1560263.7224 | 0.1978 | 308620.1643 | 0.0082 | 12794.1625 | 0.001 | 1560.2637 | 0.0001 | 156.0264 |  |  |  | 0.0451 | 70367.8939 |  | 494606.4614 | 164868.8205 | [9 empty] | 494606.4614 | 164868.8205 | 8e-06 | 12.4821 | 1e-06 | 1.5603 | 2e-07 | 0.31205 |  |  |  | 3e-08 | 0.046808
18 |  | 55189.6351 | 2381429.0402 | 27594.8175 | 2348315.2591 | 1549888.071 | 11258.6856 | 1561146.7566 | 0.1799 | 280850.3015 | 0.0045 | 7025.1604 | 0.0007 | 1092.8027 | 7e-05 | 109.2803 |  |  |  | 0.0376 | 58699.118 |  | 329737.6409 | 164868.8205 | [9 empty] | 329737.6409 | 164868.8205 | 4e-06 | 6.2446 | 5e-07 | 0.78057 | 1e-07 | 0.15611 |  |  |  | 1e-08 | 0.015611
19 |  | 27594.8175 | 2381429.0402 | 27594.8175 | 2351074.7409 | 1551709.329 | 10320.4618 | 1562029.7907 | 0.1635 | 255391.8708 | 0.0033 | 5154.6983 | 0.0005 | 781.0149 | 2e-05 | 31.2406 |  |  |  | 0.0313 | 48891.5324 |  | 164868.8205 | 164868.8205 | [9 empty] | 164868.8205 | 164868.8205 | 2e-07 | 0.31241 | 2e-07 | 0.31241 | 3e-08 | 0.046861 |  |  |  | 0 | 0
20 |  | 0 | 2381429.0402 | 27594.8175 | 2353834.2226 | 1553530.5869 | 9382.238 | 1562912.8249 | 0.1486 | 232248.8458 | 0.0025 | 3907.2821 | 0.0003 | 468.8738 | 1e-05 | 15.6291 |  |  |  | 0.0261 | 40792.0247 |  | 0 | 164868.8205 | [9 empty] | -4.6566e-10 | 164868.8205 | 1e-07 | 0.15629 | 1e-07 | 0.15629 | 1e-08 | 0.015629 |  |  |  | 0 | 0
| -5149455.0922 |  | 47628580.8032 |  | 47066686.7208 | 31064013.2357 | 191043.988 | 26105602.1315 |  | 8441779.6128 |  | -57562.3937 |  | -1434077.9632 |  | -2621288.2937 | 0.34831 | 0.34373 | 0.19802 |  | 2842332.319 | [9 empty] | -5570518.5922 |  | 0 |  |  |  | -3157103.6811 |  | -3528285.7595 |  | -3907041.6416 | -0.47304 | -1.1264 | -1.0789 |  | -4344668.8595 | -0.73195
Alternative 9 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -5283091.5922 | [6 empty] | -5283091.5922 | 1 | -5283091.5922 | 1 | -5283091.5922 | 1 | -5283091.5922 | 1 | -5283091.5922 |  |  |  | 1 | -5283091.5922 | -5283091.5922 |  |  | 0 | [5 empty] | -5283091.5922 |  |  |  |  | 1 | -5283091.5922 | 1 | -5283091.5922 | 1 | -5283091.5922 |  |  |  | 1 | -5283091.5922
1 |  | 4754782.433 | 3459116.3538 | 528309.1592 | 2455328.9513 | 1620517.1079 | 341287.7169 | 1961804.8247 | 0.9091 | 1783476.7662 | 0.7407 | 1453108.8337 | 0.6667 | 1307935.2766 | 0.5714 | 1120975.2768 |  |  |  | 0.8333 | 1634771.9604 |  | 4754782.433 | 528309.1592 |  | 0 | 0 | [8 empty] | 0.5 | 980902.4124 | 0.4444 | 871826.0641 | 0.4 | 784721.9299 |  |  |  | 0.03636 | 71331.2234
2 |  | 4279304.1897 | 3459116.3538 | 475478.2433 | 2555707.6916 | 1686767.0764 | 307158.9452 | 1993926.0216 | 0.8264 | 1647780.4642 | 0.6669 | 1329749.2638 | 0.4444 | 886100.724 | 0.3265 | 651016.8461 |  |  |  | 0.6944 | 1384582.2294 |  | 4279304.1897 | 475478.2433 |  | 0 | 0 | [8 empty] | 0.25 | 498481.5054 | 0.1613 | 321620.2673 | 0.016 | 31902.8163 |  |  |  | 0.13223 | 263656.8378
3 |  | 3851373.7707 | 3459116.3538 | 427930.419 | 2646048.5578 | 1746392.0481 | 276443.0507 | 2022835.0988 | 0.7513 | 1519756.0097 | 0.4046 | 818439.081 | 0.2963 | 599366.0398 | 0.1866 | 377461.0294 |  |  |  | 0.5787 | 1170614.6717 |  | 3851373.7707 | 427930.419 |  | 0 | 0 | [8 empty] | 0.125 | 252854.3873 | 0.0878 | 177604.9217 | 0.064 | 129461.4463 |  |  |  | 0.04808 | 97257.9115
4 |  | 3466236.3937 | 3459116.3538 | 385137.3771 | 2727355.3374 | 1800054.5227 | 248798.7456 | 2048853.2683 | 0.683 | 1399366.7822 | 0.3011 | 616909.7191 | 0.1975 | 404648.5205 | 0.1066 | 218407.7584 |  |  |  | 0.4823 | 988161.9313 |  | 3466236.3937 | 385137.3771 |  | 0 | 0 | [8 empty] | 0.0625 | 128053.3293 | 0.039 | 79905.2775 | 0.0256 | 52450.6437 |  |  |  | 0.01749 | 35833.4192
5 |  | 3119612.7543 | 3459116.3538 | 346623.6394 | 2800531.439 | 1848350.7498 | 223918.871 | 2072269.6208 | 0.6209 | 1286672.2075 | 0.223 | 462116.1254 | 0.1317 | 272917.9091 | 0.0609 | 126201.2199 |  |  |  | 0.4019 | 832845.1606 |  | 3119612.7543 | 346623.6394 |  | 0 | 0 | [8 empty] | 0.03125 | 64758.4256 | 0.0173 | 35850.2644 | 0.0102 | 21137.1501 |  |  |  | 0.00636 | 13179.6348
6 |  | 2807651.4789 | 3459116.3538 | 311961.2754 | 2866389.9305 | 1891817.3541 | 201526.9839 | 2093344.3381 | 0.5645 | 1181692.8788 | 0.1652 | 345820.4846 | 0.0878 | 183795.6329 | 0.0348 | 72848.383 |  |  |  | 0.3349 | 701061.0188 |  | 2807651.4789 | 311961.2754 |  | 0 | 0 | [8 empty] | 0.01563 | 32718.972 | 0.0077 | 16118.7514 | 0.0041 | 8582.7118 |  |  |  | 0.00231 | 4835.6254
7 |  | 2526886.331 | 3459116.3538 | 280765.1479 | 2925662.5728 | 1930937.2981 | 181374.2855 | 2112311.5836 | 0.5132 | 1084038.3047 | 0.1224 | 258546.9378 | 0.0585 | 123570.2276 | 0.0199 | 42035.0005 |  |  |  | 0.2791 | 589546.163 |  | 2526886.331 | 280765.1479 |  | 0 | 0 | [8 empty] | 0.00781 | 16497.1535 | 0.0034 | 7181.8594 | 0.0016 | 3379.6985 |  |  |  | 0.00084 | 1774.3417
8 |  | 2274197.6979 | 3459116.3538 | 252688.6331 | 2979007.9509 | 1966145.2476 | 163236.857 | 2129382.1046 | 0.4665 | 993356.7518 | 0.0906 | 192922.0187 | 0.039 | 83045.9021 | 0.0199 | 42374.7039 |  |  |  | 0.2326 | 495294.2775 |  | 2274197.6979 | 252688.6331 |  | 0 | 0 | [8 empty] | 0.00391 | 8325.884 | 0.0015 | 3194.0732 | 0.000665 | 1416.0391 |  |  |  | 0.000306 | 651.5909
9 |  | 2046777.9281 | 3459116.3538 | 227419.7698 | 3027018.7912 | 1997832.4022 | 146913.1713 | 2144745.5735 | 0.4241 | 909586.5977 | 0.0671 | 143912.428 | 0.026 | 55763.3849 | 0.0065 | 13940.8462 |  |  |  | 0.1938 | 415651.6921 |  | 2046777.9281 | 227419.7698 |  | 0 | 0 | [8 empty] | 0.00195 | 4182.2539 | 0.0007 | 1501.3219 | 0.000262 | 561.9233 |  |  |  | 0.000111 | 238.0668
10 | -421063.5 | 1842100.1353 | 3459116.3538 | 204677.7928 | 3070228.5475 | 2026350.8413 | 132221.8542 | 1737509.1955 | 0.3855 | 669809.7949 | 0.0497 | 86354.207 | 0.0173 | 30058.9091 | 0.0037 | 6428.784 |  |  |  | 0.1615 | 280607.7351 |  | 1842100.1353 | 204677.7928 |  | 0 | 0 | -421063.5 |  |  | -421063.5 |  |  |  |  | 0.00098 | 1702.759 | 0.0003 | 521.2528 | 0.000105 | 182.4385 |  |  |  | 4e-05 | 69.5004
11 |  | 1994740.9218 | 3459116.3538 | 268422.7135 | 2991219.5481 | 1974204.9018 | 159084.9139 | 2133289.8157 | 0.3505 | 747718.0804 | 0.0368 | 78505.0652 | 0.116 | 247461.6186 | 0.0021 | 4479.9086 |  |  |  | 0.1346 | 287140.8092 |  | 1657890.1218 | 184210.0135 |  |  |  |  | 336850.8 | 84212.7 | [5 empty] | 0.00049 | 1045.312 | 0.00013 | 277.3277 | 4.2e-05 | 89.5982 |  |  |  | 1.47e-05 | 31.3594
12 |  | 1743160.7482 | 3459116.3538 | 251580.1735 | 3033220.1055 | 2001925.2696 | 144804.7244 | 2146729.9941 | 0.3186 | 683948.1761 | 0.0273 | 58605.7288 | 0.0077 | 16529.821 | 0.0012 | 2576.076 |  |  |  | 0.1122 | 240863.1053 |  | 1473680.1082 | 184210.0135 |  |  |  |  | 269480.64 | 67370.16 | [5 empty] | 0.00024 | 515.2152 | 5.9e-05 | 126.6571 | 1.7e-05 | 36.4944 |  |  |  | 5.3e-06 | 11.3777
13 |  | 1505054.6067 | 3459116.3538 | 238106.1415 | 3070504.7516 | 2026533.1361 | 132127.9447 | 2158661.0808 | 0.2897 | 625364.1151 | 0.0273 | 58931.4475 | 0.0051 | 11009.1715 | 0.0007 | 1511.0628 |  |  |  | 0.0935 | 201834.8111 |  | 1289470.0947 | 184210.0135 |  |  |  |  | 215584.512 | 53896.128 | [5 empty] | 0.00012 | 259.0393 | 2.6e-05 | 56.1252 | 6.7e-06 | 14.463 |  |  |  | 1.9e-06 | 4.1015
14 |  | 1277727.6908 | 3459116.3538 | 227326.9159 | 3104016.6688 | 2048651.0014 | 120733.8929 | 2169384.8943 | 0.2633 | 571199.0427 | 0.0202 | 43821.5749 | 0.0034 | 7375.9086 | 0.0004 | 867.754 |  |  |  | 0.0779 | 168995.0833 |  | 1105260.0812 | 184210.0135 |  |  |  |  | 172467.6096 | 43116.9024 | [5 empty] | 6e-05 | 130.1631 | 1.2e-05 | 26.0326 | 2.7e-06 | 5.8573 |  |  |  | 7e-07 | 1.5186
15 |  | 1059024.1553 | 3459116.3538 | 218703.5354 | 3134510.4028 | 2068776.8659 | 110366.0233 | 2179142.8892 | 0.2394 | 521686.8077 | 0.015 | 32687.1433 | 0.0023 | 5012.0286 | 0.0002 | 435.8286 |  |  |  | 0.0649 | 141426.3735 |  | 921050.0676 | 184210.0135 |  |  |  |  | 137974.0877 | 34493.5219 | [5 empty] | 3e-05 | 65.3743 | 5e-06 | 10.8957 | 1.1e-06 | 2.3971 |  |  |  | 3e-07 | 0.65374
16 |  | 847219.3243 | 3459116.3538 | 211804.8311 | 3162589.5903 | 2087309.1296 | 100819.0996 | 2188128.2292 | 0.2176 | 476136.7027 | 0.0111 | 24288.2233 | 0.0015 | 3282.1923 | 0.0001 | 218.8128 |  |  |  | 0.0541 | 118377.7372 |  | 736840.0541 | 184210.0135 |  |  |  |  | 110379.2701 | 27594.8175 | [5 empty] | 1e-05 | 21.8813 | 2.3e-06 | 5.0327 | 4e-07 | 0.87525 |  |  |  | 9e-08 | 0.19693
17 |  | 635414.4932 | 3459116.3538 | 211804.8311 | 3183770.0734 | 2101288.2485 | 93617.7353 | 2194905.9838 | 0.1978 | 434152.4036 | 0.0082 | 17998.2291 | 0.001 | 2194.906 | 0.0001 | 219.4906 |  |  |  | 0.0451 | 98990.2599 |  | 552630.0406 | 184210.0135 |  |  |  |  | 82784.4526 | 27594.8175 | [5 empty] | 8e-06 | 17.5592 | 1e-06 | 2.1949 | 2e-07 | 0.43898 |  |  |  | 3e-08 | 0.065847
18 |  | 423609.6621 | 3459116.3538 | 211804.8311 | 3204950.5565 | 2115267.3673 | 86416.3711 | 2201683.7384 | 0.1799 | 396082.9045 | 0.0045 | 9907.5768 | 0.0007 | 1541.1786 | 7e-05 | 154.1179 |  |  |  | 0.0376 | 82783.3086 |  | 368420.0271 | 184210.0135 |  |  |  |  | 55189.6351 | 27594.8175 | [5 empty] | 4e-06 | 8.8067 | 5e-07 | 1.1008 | 1e-07 | 0.22017 |  |  |  | 1e-08 | 0.022017
19 |  | 211804.8311 | 3459116.3538 | 211804.8311 | 3226131.0397 | 2129246.4862 | 79215.0068 | 2208461.493 | 0.1635 | 361083.4541 | 0.0033 | 7287.9229 | 0.0005 | 1104.2307 | 2e-05 | 44.1692 |  |  |  | 0.0313 | 69124.8447 |  | 184210.0135 | 184210.0135 |  |  |  |  | 27594.8175 | 27594.8175 | [5 empty] | 2e-07 | 0.44169 | 2e-07 | 0.44169 | 3e-08 | 0.066254 |  |  |  | 0 | 0
20 |  | 0 | 3459116.3538 | 211804.8311 | 3247311.5228 | 2143225.605 | 72013.6426 | 2215239.2476 | 0.1486 | 329184.5522 | 0.0025 | 5538.0981 | 0.0003 | 664.5718 | 1e-05 | 22.1524 |  |  |  | 0.0261 | 57817.7444 |  | 0 | 184210.0135 |  |  |  |  | 0 | 27594.8175 | [5 empty] | 1e-07 | 0.22152 | 1e-07 | 0.22152 | 1e-08 | 0.022152 |  |  |  | 0 | 0
| -5704155.0922 |  | 69182327.0765 |  | 59411504.0297 | 39211592.6596 | 3322079.8359 | 36829517.4033 |  | 12339001.2047 |  | 762358.5169 |  | -1039713.4378 |  | -2600872.3712 | 0.36646 | 0.41346 | 0.3335 |  | 4677399.3248 | [9 empty] | -5704155.0922 |  | 0 |  |  |  | -3292550.4954 |  | -3767261.5087 |  | -4249144.3618 | -0.19006 | -0.73398 | -0.70445 |  | -4794214.1446 | -0.4489
Alternative 10 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -5283091.5922 | [6 empty] | -5283091.5922 | 1 | -5283091.5922 | 1 | -5283091.5922 | 1 | -5283091.5922 | 1 | -5283091.5922 |  |  |  | 1 | -5283091.5922 | -5283091.5922 | [8 empty] | -5283091.5922 |  |  |  |  | 1 | -5283091.5922 | 1 | -5283091.5922 | 1 | -5283091.5922 |  |  |  | 1 | -5283091.5922
1 |  | 4754782.433 | 4095924.0637 | 528309.1592 | 3092136.6611 | 2040810.1964 | 341287.7169 | 2382097.9132 | 0.9091 | 2165565.2129 | 0.7407 | 1764419.9243 | 0.6667 | 1588144.6787 | 0.5714 | 1361130.7476 |  |  |  | 0.8333 | 1985002.1911 |  | 4754782.433 | 528309.1592 |  | 0 | 0 | [8 empty] | 0.5 | 1191048.9566 | 0.4444 | 1058604.3126 | 0.4 | 952839.1653 |  |  |  | 0.03636 | 86613.0801
2 |  | 4279304.1897 | 4095924.0637 | 475478.2433 | 3192515.4014 | 2107060.1649 | 307158.9452 | 2414219.1101 | 0.8264 | 1995110.6726 | 0.6669 | 1610042.7245 | 0.4444 | 1072878.9725 | 0.3265 | 788242.5394 |  |  |  | 0.6944 | 1676433.75 |  | 4279304.1897 | 475478.2433 |  | 0 | 0 | [8 empty] | 0.25 | 603554.7775 | 0.1613 | 389413.5425 | 0.016 | 38627.5058 |  |  |  | 0.13223 | 319232.1929
3 |  | 3851373.7707 | 4095924.0637 | 427930.419 | 3282856.2676 | 2166685.1366 | 276443.0507 | 2443128.1873 | 0.7513 | 1835522.2071 | 0.4046 | 988489.6646 | 0.2963 | 723898.8819 | 0.1866 | 455887.7197 |  |  |  | 0.5787 | 1413838.282 |  | 3851373.7707 | 427930.419 |  | 0 | 0 | [8 empty] | 0.125 | 305391.0234 | 0.0878 | 214506.6548 | 0.064 | 156360.204 |  |  |  | 0.04808 | 117465.6032
4 |  | 3466236.3937 | 4095924.0637 | 385137.3771 | 3364163.0472 | 2220347.6112 | 248798.7456 | 2469146.3568 | 0.683 | 1686426.9617 | 0.3011 | 743459.968 | 0.1975 | 487656.4055 | 0.1066 | 263211.0016 |  |  |  | 0.4823 | 1190869.2879 |  | 3466236.3937 | 385137.3771 |  | 0 | 0 | [8 empty] | 0.0625 | 154321.6473 | 0.039 | 96296.7079 | 0.0256 | 63210.1467 |  |  |  | 0.01749 | 43184.1352
5 |  | 3119612.7543 | 4095924.0637 | 346623.6394 | 3437339.1489 | 2268643.8382 | 223918.871 | 2492562.7093 | 0.6209 | 1547632.1862 | 0.223 | 555841.4842 | 0.1317 | 328270.5088 | 0.0609 | 151797.069 |  |  |  | 0.4019 | 1001760.9529 |  | 3119612.7543 | 346623.6394 |  | 0 | 0 | [8 empty] | 0.03125 | 77892.5847 | 0.0173 | 43121.3349 | 0.0102 | 25424.1396 |  |  |  | 0.00636 | 15852.6988
6 |  | 2807651.4789 | 4095924.0637 | 311961.2754 | 3503197.6403 | 2312110.4426 | 201526.9839 | 2513637.4266 | 0.5645 | 1418948.3273 | 0.1652 | 415252.9029 | 0.0878 | 220697.3661 | 0.0348 | 87474.5824 |  |  |  | 0.3349 | 841817.1742 |  | 2807651.4789 | 311961.2754 |  | 0 | 0 | [8 empty] | 0.01563 | 39288.153 | 0.0077 | 19355.0082 | 0.0041 | 10305.9134 |  |  |  | 0.00231 | 5806.5025
7 |  | 2526886.331 | 4095924.0637 | 280765.1479 | 3562470.2827 | 2351230.3866 | 181374.2855 | 2532604.6721 | 0.5132 | 1299732.7177 | 0.1224 | 309990.8119 | 0.0585 | 148157.3733 | 0.0199 | 50398.833 |  |  |  | 0.2791 | 706849.964 |  | 2526886.331 | 280765.1479 |  | 0 | 0 | [8 empty] | 0.00781 | 19779.6425 | 0.0034 | 8610.8559 | 0.0016 | 4052.1675 |  |  |  | 0.00084 | 2127.3879
8 |  | 2274197.6979 | 4095924.0637 | 252688.6331 | 3615815.6608 | 2386438.3361 | 163236.857 | 2549675.1931 | 0.4665 | 1189423.4776 | 0.0906 | 231000.5725 | 0.039 | 99437.3325 | 0.0199 | 50738.5363 |  |  |  | 0.2326 | 593054.4499 |  | 2274197.6979 | 252688.6331 |  | 0 | 0 | [8 empty] | 0.00391 | 9969.23 | 0.0015 | 3824.5128 | 0.000665 | 1695.534 |  |  |  | 0.000306 | 780.2006
9 |  | 2046777.9281 | 4095924.0637 | 227419.7698 | 3663826.5011 | 2418125.4907 | 146913.1713 | 2565038.662 | 0.4241 | 1087832.8965 | 0.0671 | 172114.0942 | 0.026 | 66691.0052 | 0.0065 | 16672.7513 |  |  |  | 0.1938 | 497104.4927 |  | 2046777.9281 | 227419.7698 |  | 0 | 0 | [8 empty] | 0.00195 | 5001.8254 | 0.0007 | 1795.5271 | 0.000262 | 672.0401 |  |  |  | 0.000111 | 284.7193
10 | -421063.5 | 1842100.1353 | 4095924.0637 | 204677.7928 | 3707036.2573 | 2446643.9298 | 132221.8542 | 2157802.284 | 0.3855 | 831832.7805 | 0.0497 | 107242.7735 | 0.0173 | 37329.9795 | 0.0037 | 7983.8685 |  |  |  | 0.1615 | 348485.0689 |  | 1842100.1353 | 204677.7928 |  | 0 | 0 | -421063.5 |  |  | -421063.5 |  |  |  |  | 0.00098 | 2114.6462 | 0.0003 | 647.3407 | 0.000105 | 226.5692 |  |  |  | 4e-05 | 86.3121
11 |  | 1994740.9218 | 4095924.0637 | 268422.7135 | 3628027.258 | 2394497.9902 | 159084.9139 | 2553582.9042 | 0.3505 | 895030.8079 | 0.0368 | 93971.8509 | 0.116 | 296215.6169 | 0.0021 | 5362.5241 |  |  |  | 0.1346 | 343712.2589 |  | 1657890.1218 | 184210.0135 |  |  |  |  | 336850.8 | 84212.7 | [5 empty] | 0.00049 | 1251.2556 | 0.00013 | 331.9658 | 4.2e-05 | 107.2505 |  |  |  | 1.47e-05 | 37.5377
12 |  | 1743160.7482 | 4095924.0637 | 251580.1735 | 3670027.8153 | 2422218.3581 | 144804.7244 | 2567023.0825 | 0.3186 | 817853.5541 | 0.0273 | 70079.7302 | 0.0077 | 19766.0777 | 0.0012 | 3080.4277 |  |  |  | 0.1122 | 288019.9899 |  | 1473680.1082 | 184210.0135 |  |  |  |  | 269480.64 | 67370.16 | [5 empty] | 0.00024 | 616.0855 | 5.9e-05 | 151.4544 | 1.7e-05 | 43.6394 |  |  |  | 5.3e-06 | 13.6052
13 |  | 1505054.6067 | 4095924.0637 | 238106.1415 | 3707312.4615 | 2446826.2246 | 132127.9447 | 2578954.1693 | 0.2897 | 747123.0228 | 0.0273 | 70405.4488 | 0.0051 | 13152.6663 | 0.0007 | 1805.2679 |  |  |  | 0.0935 | 241132.2148 |  | 1289470.0947 | 184210.0135 |  |  |  |  | 215584.512 | 53896.128 | [5 empty] | 0.00012 | 309.4745 | 2.6e-05 | 67.0528 | 6.7e-06 | 17.279 |  |  |  | 1.9e-06 | 4.9
14 |  | 1277727.6908 | 4095924.0637 | 227326.9159 | 3740824.3787 | 2468944.0899 | 120733.8929 | 2589677.9828 | 0.2633 | 681862.2129 | 0.0202 | 52311.4953 | 0.0034 | 8804.9051 | 0.0004 | 1035.8712 |  |  |  | 0.0779 | 201735.9149 |  | 1105260.0812 | 184210.0135 |  |  |  |  | 172467.6096 | 43116.9024 | [5 empty] | 6e-05 | 155.3807 | 1.2e-05 | 31.0761 | 2.7e-06 | 6.9921 |  |  |  | 7e-07 | 1.8128
15 |  | 1059024.1553 | 4095924.0637 | 218703.5354 | 3771318.1127 | 2489069.9544 | 110366.0233 | 2599435.9777 | 0.2394 | 622304.9731 | 0.015 | 38991.5397 | 0.0023 | 5978.7027 | 0.0002 | 519.8872 |  |  |  | 0.0649 | 168703.395 |  | 921050.0676 | 184210.0135 |  |  |  |  | 137974.0877 | 34493.5219 | [5 empty] | 3e-05 | 77.9831 | 5e-06 | 12.9972 | 1.1e-06 | 2.8594 |  |  |  | 3e-07 | 0.77983
16 |  | 847219.3243 | 4095924.0637 | 211804.8311 | 3799397.3002 | 2507602.2181 | 100819.0996 | 2608421.3177 | 0.2176 | 567592.4787 | 0.0111 | 28953.4766 | 0.0015 | 3912.632 | 0.0001 | 260.8421 |  |  |  | 0.0541 | 141115.5933 |  | 736840.0541 | 184210.0135 |  |  |  |  | 110379.2701 | 27594.8175 | [5 empty] | 1e-05 | 26.0842 | 2.3e-06 | 5.9994 | 4e-07 | 1.0434 |  |  |  | 9e-08 | 0.23476
17 |  | 635414.4932 | 4095924.0637 | 211804.8311 | 3820577.7833 | 2521581.337 | 93617.7353 | 2615199.0723 | 0.1978 | 517286.3765 | 0.0082 | 21444.6324 | 0.001 | 2615.1991 | 0.0001 | 261.5199 |  |  |  | 0.0451 | 117945.4782 |  | 552630.0406 | 184210.0135 |  |  |  |  | 82784.4526 | 27594.8175 | [5 empty] | 8e-06 | 20.9216 | 1e-06 | 2.6152 | 2e-07 | 0.52304 |  |  |  | 3e-08 | 0.078456
18 |  | 423609.6621 | 4095924.0637 | 211804.8311 | 3841758.2664 | 2535560.4558 | 86416.3711 | 2621976.8269 | 0.1799 | 471693.6312 | 0.0045 | 11798.8957 | 0.0007 | 1835.3838 | 7e-05 | 183.5384 |  |  |  | 0.0376 | 98586.3287 |  | 368420.0271 | 184210.0135 |  |  |  |  | 55189.6351 | 27594.8175 | [5 empty] | 4e-06 | 10.4879 | 5e-07 | 1.311 | 1e-07 | 0.2622 |  |  |  | 1e-08 | 0.02622
19 |  | 211804.8311 | 4095924.0637 | 211804.8311 | 3862938.7495 | 2549539.5747 | 79215.0068 | 2628754.5815 | 0.1635 | 429801.3741 | 0.0033 | 8674.8901 | 0.0005 | 1314.3773 | 2e-05 | 52.5751 |  |  |  | 0.0313 | 82280.0184 |  | 184210.0135 | 184210.0135 |  |  |  |  | 27594.8175 | 27594.8175 | [5 empty] | 2e-07 | 0.52575 | 2e-07 | 0.52575 | 3e-08 | 0.078863 |  |  |  | 0 | 0
20 |  | 0 | 4095924.0637 | 211804.8311 | 3884119.2326 | 2563518.6935 | 72013.6426 | 2635532.3361 | 0.1486 | 391640.1051 | 0.0025 | 6588.8308 | 0.0003 | 790.6597 | 1e-05 | 26.3553 |  |  |  | 0.0261 | 68787.394 |  | 0 | 184210.0135 |  |  |  |  | 0 | 27594.8175 | [5 empty] | 1e-07 | 0.26355 | 1e-07 | 0.26355 | 1e-08 | 0.026355 |  |  |  | 0 | 0
| -5704155.0922 |  | 81918481.2731 |  | 72147658.2263 | 47617454.4294 | 3322079.8359 | 45235379.1731 |  | 15917124.3842 |  | 2017984.1188 |  | -155542.8676 |  | -2036965.1343 | 0.3863 | 0.48927 | 0.47933 |  | 6724142.6071 | [9 empty] | -5704155.0922 |  | 0 |  |  |  | -2872260.6432 |  | -3446310.5338 |  | -4029498.2523 | 0.14035 | -0.25088 | -0.22736 |  | -4691599.7846 | -0.02148
Alternative 11 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR | 175% | NPV | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150% | Discount | at 175% | 150-175%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor |  |  |  |  | Rate
0 | -8998894.8063 | [6 empty] | -8998894.8063 | 1 | -8998894.8063 | 1 | -8998894.8063 | 1 | -8998894.8063 | 1 | -8998894.8063 |  |  |  | 1 | -8998894.8063 | -8998894.8063 |  |  | 0 | [5 empty] | -8998894.8063 |  |  |  |  | 1 | -8998894.8063 | 1 | -8998894.8063 | 1 | -8998894.8063 |  |  |  | 1 | -8998894.8063
1 |  | 8099005.3256 | 4380412.9759 | 899889.4806 | 2670622.9627 | 1762611.1554 | 581328.6045 | 2343939.7599 | 0.9091 | 2130875.6357 | 0.7407 | 1736156.1801 | 0.6667 | 1562704.6379 | 0.5714 | 1339327.1788 |  |  |  | 0.8333 | 1953205.0019 |  | 8099005.3256 | 899889.4806 |  | 0 | 0 | [6 empty] | 8099005.3256 | 899889.4806 | 0.5 | 1171969.8799 | 0.4444 | 1041646.8293 | 0.4 | 937575.9039 |  |  |  | 0.03636 | 85225.6497
2 |  | 7289104.7931 | 4380412.9759 | 809900.5326 | 2841601.964 | 1875457.2962 | 523195.744 | 2398653.0403 | 0.8264 | 1982246.8725 | 0.6669 | 1599661.7126 | 0.4444 | 1065961.4111 | 0.3265 | 783160.2176 |  |  |  | 0.6944 | 1665624.6712 |  | 7289104.7931 | 809900.5326 |  | 0 | 0 | [6 empty] | 7289104.7931 | 809900.5326 | 0.25 | 599663.2601 | 0.1613 | 386902.7354 | 0.016 | 38378.4486 |  |  |  | 0.13223 | 317173.8915
3 |  | 6560194.3138 | 4380412.9759 | 728910.4793 | 2995483.0652 | 1977018.823 | 470876.1696 | 2447894.9927 | 0.7513 | 1839103.508 | 0.4046 | 990418.314 | 0.2963 | 725311.2863 | 0.1866 | 456777.2056 |  |  |  | 0.5787 | 1416596.8322 |  | 6560194.3138 | 728910.4793 |  | 0 | 0 | [6 empty] | 6560194.3138 | 728910.4793 | 0.125 | 305986.8741 | 0.0878 | 214925.1804 | 0.064 | 156665.2795 |  |  |  | 0.04808 | 117694.7912
4 |  | 5904174.8824 | 4380412.9759 | 656019.4314 | 3133976.0563 | 2068424.1971 | 423788.5527 | 2492212.7498 | 0.683 | 1702181.3081 | 0.3011 | 750405.259 | 0.1975 | 492212.0181 | 0.1066 | 265669.8791 |  |  |  | 0.4823 | 1201994.2092 |  | 5904174.8824 | 656019.4314 |  | 0 | 0 | [6 empty] | 5904174.8824 | 656019.4314 | 0.0625 | 155763.2969 | 0.039 | 97196.2972 | 0.0256 | 63800.6464 |  |  |  | 0.01749 | 43587.5549
5 |  | 5313757.3941 | 4380412.9759 | 590417.4882 | 3258619.7482 | 2150689.0338 | 381409.6974 | 2532098.7312 | 0.6209 | 1572180.1022 | 0.223 | 564658.0171 | 0.1317 | 333477.4029 | 0.0609 | 154204.8127 |  |  |  | 0.4019 | 1017650.4801 |  | 5313757.3941 | 590417.4882 |  | 0 | 0 | [6 empty] | 5313757.3941 | 590417.4882 | 0.03125 | 79128.0854 | 0.0173 | 43805.3081 | 0.0102 | 25827.4071 |  |  |  | 0.00636 | 16104.1479
6 |  | 4782381.6547 | 4380412.9759 | 531375.7394 | 3370799.071 | 2224727.3868 | 343268.7277 | 2567996.1145 | 0.5645 | 1449633.8066 | 0.1652 | 424232.9581 | 0.0878 | 225470.0589 | 0.0348 | 89366.2648 |  |  |  | 0.3349 | 860021.8987 |  | 4782381.6547 | 531375.7394 |  | 0 | 0 | [6 empty] | 4782381.6547 | 531375.7394 | 0.01563 | 40137.7793 | 0.0077 | 19773.5701 | 0.0041 | 10528.7841 |  |  |  | 0.00231 | 5932.071
7 |  | 4304143.4893 | 4380412.9759 | 478238.1655 | 3471760.4615 | 2291361.9046 | 308941.8549 | 2600303.7595 | 0.5132 | 1334475.8894 | 0.1224 | 318277.1802 | 0.0585 | 152117.7699 | 0.0199 | 51746.0448 |  |  |  | 0.2791 | 725744.7793 |  | 4304143.4893 | 478238.1655 |  | 0 | 0 | [6 empty] | 4304143.4893 | 478238.1655 | 0.00781 | 20308.3724 | 0.0034 | 8841.0328 | 0.0016 | 4160.486 |  |  |  | 0.00084 | 2184.2552
8 |  | 3873729.1403 | 4380412.9759 | 430414.3489 | 3562625.7129 | 2351332.9705 | 278047.6694 | 2629380.6399 | 0.4665 | 1226606.0685 | 0.0906 | 238221.886 | 0.039 | 102545.845 | 0.0199 | 52324.6747 |  |  |  | 0.2326 | 611593.9368 |  | 3873729.1403 | 430414.3489 |  | 0 | 0 | [6 empty] | 3873729.1403 | 430414.3489 | 0.00391 | 10280.8783 | 0.0015 | 3944.071 | 0.000665 | 1748.5381 |  |  |  | 0.000306 | 804.5905
9 |  | 3486356.2263 | 4380412.9759 | 387372.914 | 3644404.4392 | 2405306.9299 | 250242.9025 | 2655549.8323 | 0.4241 | 1126218.6839 | 0.0671 | 178187.3938 | 0.026 | 69044.2956 | 0.0065 | 17261.0739 |  |  |  | 0.1938 | 514645.5575 |  | 3486356.2263 | 387372.914 |  | 0 | 0 | [6 empty] | 3486356.2263 | 387372.914 | 0.00195 | 5178.3222 | 0.0007 | 1858.8849 | 0.000262 | 695.7541 |  |  |  | 0.000111 | 294.766
10 | 1491750 | 3137720.6037 | 4380412.9759 | 348635.6226 | 3718005.2929 | 2453883.4933 | 225218.6122 | 4170852.1055 | 0.3855 | 1607863.4867 | 0.0497 | 207291.3496 | 0.0173 | 72155.7414 | 0.0037 | 15432.1528 |  |  |  | 0.1615 | 673592.615 |  | 3137720.6037 | 348635.6226 |  | 0 | 0 | 0 |  |  | 0 |  |  | 3137720.6037 | 348635.6226 | 0.00098 | 4087.4351 | 0.0003 | 1251.2556 | 0.000105 | 437.9395 |  |  |  | 4e-05 | 166.8341
11 |  | 2823948.5433 | 4380412.9759 | 313772.0604 | 3784246.0612 | 2497602.4004 | 202696.751 | 2700299.1514 | 0.3505 | 946454.8526 | 0.0368 | 99371.0088 | 0.116 | 313234.7016 | 0.0021 | 5670.6282 |  |  |  | 0.1346 | 363460.2658 |  | 2823948.5433 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 2823948.5433 | 313772.0604 | 0.00049 | 1323.1466 | 0.00013 | 351.0389 | 4.2e-05 | 113.4126 |  |  |  | 1.47e-05 | 39.6944
12 |  | 2510176.4829 | 4380412.9759 | 313772.0604 | 3815623.2672 | 2518311.3564 | 192028.5009 | 2710339.8573 | 0.3186 | 863514.2785 | 0.0273 | 73992.2781 | 0.0077 | 20869.6169 | 0.0012 | 3252.4078 |  |  |  | 0.1122 | 304100.132 |  | 2510176.4829 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 2510176.4829 | 313772.0604 | 0.00024 | 650.4816 | 5.9e-05 | 159.9101 | 1.7e-05 | 46.0758 |  |  |  | 5.3e-06 | 14.3648
13 |  | 2196404.4226 | 4380412.9759 | 313772.0604 | 3847000.4732 | 2539020.3123 | 181360.2509 | 2720380.5632 | 0.2897 | 788094.2492 | 0.0273 | 74266.3894 | 0.0051 | 13873.9409 | 0.0007 | 1904.2664 |  |  |  | 0.0935 | 254355.5827 |  | 2196404.4226 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 2196404.4226 | 313772.0604 | 0.00012 | 326.4457 | 2.6e-05 | 70.7299 | 6.7e-06 | 18.2265 |  |  |  | 1.9e-06 | 5.1687
14 |  | 1882632.3622 | 4380412.9759 | 313772.0604 | 3878377.6793 | 2559729.2683 | 170692.0008 | 2730421.2692 | 0.2633 | 718919.9202 | 0.0202 | 55154.5096 | 0.0034 | 9283.4323 | 0.0004 | 1092.1685 |  |  |  | 0.0779 | 212699.8169 |  | 1882632.3622 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 1882632.3622 | 313772.0604 | 6e-05 | 163.8253 | 1.2e-05 | 32.7651 | 2.7e-06 | 7.3721 |  |  |  | 7e-07 | 1.9113
15 |  | 1568860.3018 | 4380412.9759 | 313772.0604 | 3909754.8853 | 2580438.2243 | 160023.7508 | 2740461.9751 | 0.2394 | 656066.5968 | 0.015 | 41106.9296 | 0.0023 | 6303.0625 | 0.0002 | 548.0924 |  |  |  | 0.0649 | 177855.9822 |  | 1568860.3018 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 1568860.3018 | 313772.0604 | 3e-05 | 82.2139 | 5e-06 | 13.7023 | 1.1e-06 | 3.0145 |  |  |  | 3e-07 | 0.82214
16 |  | 1255088.2415 | 4380412.9759 | 313772.0604 | 3941132.0914 | 2601147.1803 | 149355.5007 | 2750502.681 | 0.2176 | 598509.3834 | 0.0111 | 30530.5798 | 0.0015 | 4125.754 | 0.0001 | 275.0503 |  |  |  | 0.0541 | 148802.195 |  | 1255088.2415 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 1255088.2415 | 313772.0604 | 1e-05 | 27.505 | 2.3e-06 | 6.3262 | 4e-07 | 1.1002 |  |  |  | 9e-08 | 0.24755
17 |  | 941316.1811 | 4380412.9759 | 313772.0604 | 3972509.2974 | 2621856.1363 | 138687.2507 | 2760543.387 | 0.1978 | 546035.4819 | 0.0082 | 22636.4558 | 0.001 | 2760.5434 | 0.0001 | 276.0543 |  |  |  | 0.0451 | 124500.5068 |  | 941316.1811 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 941316.1811 | 313772.0604 | 8e-06 | 22.0843 | 1e-06 | 2.7605 | 2e-07 | 0.55211 |  |  |  | 3e-08 | 0.082816
18 |  | 627544.1207 | 4380412.9759 | 313772.0604 | 4003886.5034 | 2642565.0923 | 128019.0006 | 2770584.0929 | 0.1799 | 498428.0783 | 0.0045 | 12467.6284 | 0.0007 | 1939.4089 | 7e-05 | 193.9409 |  |  |  | 0.0376 | 104173.9619 |  | 627544.1207 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 627544.1207 | 313772.0604 | 4e-06 | 11.0823 | 5e-07 | 1.3853 | 1e-07 | 0.27706 |  |  |  | 1e-08 | 0.027706
19 |  | 313772.0604 | 4380412.9759 | 313772.0604 | 4035263.7095 | 2663274.0482 | 117350.7506 | 2780624.7988 | 0.1635 | 454632.1546 | 0.0033 | 9176.0618 | 0.0005 | 1390.3124 | 2e-05 | 55.6125 |  |  |  | 0.0313 | 87033.5562 |  | 313772.0604 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | 313772.0604 | 313772.0604 | 2e-07 | 0.55612 | 2e-07 | 0.55612 | 3e-08 | 0.083419 |  |  |  | 0 | 0
20 |  | 0 | 4380412.9759 | 313772.0604 | 4066640.9155 | 2683983.0042 | 106682.5005 | 2790665.5048 | 0.1486 | 414692.894 | 0.0025 | 6976.6638 | 0.0003 | 837.1997 | 1e-05 | 27.9067 |  |  |  | 0.0261 | 72836.3697 |  | 0 | 313772.0604 |  |  |  |  | 0 | 0 |  |  |  | -9.3132e-10 | 313772.0604 | 1e-07 | 0.27907 | 1e-07 | 0.27907 | 1e-08 | 0.027907 |  |  |  | 0 | 0
| -7507144.8063 |  | 87608259.5174 |  | 71922333.6571 | 47468740.2137 | 5333214.7925 | 45294810.1999 |  | 13457838.4448 |  | -1565706.0508 |  | -3823276.3666 |  | -5760329.1733 | 0.32395 | 0.24597 | 0.0065601 |  | 3491593.5448 | [9 empty] | -8998894.8063 |  | 0 |  |  |  | -6603783.0029 |  | -7178110.1882 |  | -7758885.4767 | -0.95736 | -1.8746 | -1.8399 |  | -8409663.9348 | -1.4806
Alternative 12 Total Cost of Ownership
[9 empty] | 10% | NPV | 35% | NPV | 50% | NPV | 75% | NPV | IRR | IRR | IRR | 20% | NPV | [14 empty] | 100% | NPV | 125% | NPV | 150% | NPV | IRR | IRR | IRR
| Addl. | Capital | Energy&Maint | 200% DB | Before-Tax | After-Tax | Tax | Nominal | Discount | at 10% | Discount | at 35% | Discount | at 50% | Discount | at 75% | 10-35% | 35-50% | 50-75% | Discount | at 20% | [14 empty] | Discount | at 100% | Discount | at 125% | Discount | at 150% | 75-100% | 100-125% | 125-150%
Year | Capital | Balance | Savings | Depr. | Savings | Savings | Savings | Cash Flow | Factor |  | Factor |  | Factor |  | Factor |  |  |  |  | Factor |  | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr | Invest | Bal | Depr |  |  | Factor |  | Factor |  | Factor
0 | -8599353.6298 | [6 empty] | -8599353.6298 | 1 | -8599353.6298 | 1 | -8599353.6298 | 1 | -8599353.6298 | 1 | -8599353.6298 |  |  |  | 1 | -8599353.6298 | -8599353.6298 |  |  | 0 | [5 empty] | -8599353.6298 |  |  |  |  | 1 | -8599353.6298 | 1 | -8599353.6298 | 1 | -8599353.6298
1 |  | 7739418.2668 | 4728201.1252 | 859935.363 | 3094323.9356 | 2042253.7975 | 555518.2445 | 2597772.042 | 0.9091 | 2361634.5633 | 0.7407 | 1924169.7515 | 0.6667 | 1731934.6204 | 0.5714 | 1484366.9448 |  |  |  | 0.8333 | 2164723.4426 |  | 7739418.2668 | 859935.363 |  | 0 | 0 | [6 empty] | 7739418.2668 | 859935.363 | 0.5 | 1298886.021 | 0.4444 | 1154449.8954 | 0.4 | 1039108.8168
2 |  | 6965476.4401 | 4728201.1252 | 773941.8267 | 3257711.6545 | 2150089.692 | 499966.42 | 2650056.112 | 0.8264 | 2190006.371 | 0.6669 | 1767322.4211 | 0.4444 | 1177684.9362 | 0.3265 | 865243.3206 |  |  |  | 0.6944 | 1840198.9642 |  | 6965476.4401 | 773941.8267 |  | 0 | 0 | [6 empty] | 6965476.4401 | 773941.8267 | 0.25 | 662514.028 | 0.1613 | 427454.0509 | 0.016 | 42400.8978
3 |  | 6268928.7961 | 4728201.1252 | 696547.644 | 3404760.6016 | 2247141.9971 | 449969.778 | 2697111.7751 | 0.7513 | 2026340.0766 | 0.4046 | 1091251.4242 | 0.2963 | 799154.219 | 0.1866 | 503281.0572 |  |  |  | 0.5787 | 1560818.5842 |  | 6268928.7961 | 696547.644 |  | 0 | 0 | [6 empty] | 6268928.7961 | 696547.644 | 0.125 | 337138.9719 | 0.0878 | 236806.4139 | 0.064 | 172615.1536
4 |  | 5642035.9165 | 4728201.1252 | 626892.8796 | 3537104.654 | 2334489.0716 | 404972.8002 | 2739461.8718 | 0.683 | 1871052.4585 | 0.3011 | 824851.9696 | 0.1975 | 541043.7197 | 0.1066 | 292026.6355 |  |  |  | 0.4823 | 1321242.4608 |  | 5642035.9165 | 626892.8796 |  | 0 | 0 | [6 empty] | 5642035.9165 | 626892.8796 | 0.0625 | 171216.367 | 0.039 | 106839.013 | 0.0256 | 70130.2239
5 |  | 5077832.3249 | 4728201.1252 | 564203.5917 | 3656214.3011 | 2413101.4387 | 364475.5202 | 2777576.9589 | 0.6209 | 1724597.5338 | 0.223 | 619399.6618 | 0.1317 | 365806.8855 | 0.0609 | 169154.4368 |  |  |  | 0.4019 | 1116308.1798 |  | 5077832.3249 | 564203.5917 |  | 0 | 0 | [6 empty] | 5077832.3249 | 564203.5917 | 0.03125 | 86799.28 | 0.0173 | 48052.0814 | 0.0102 | 28331.285
6 |  | 4570049.0924 | 4728201.1252 | 507783.2325 | 3763412.9835 | 2483852.5691 | 328027.9682 | 2811880.5373 | 0.5645 | 1587306.5633 | 0.1652 | 464522.6648 | 0.0878 | 246883.1112 | 0.0348 | 97853.4427 |  |  |  | 0.3349 | 941698.7919 |  | 4570049.0924 | 507783.2325 |  | 0 | 0 | [6 empty] | 4570049.0924 | 507783.2325 | 0.01563 | 43949.6928 | 0.0077 | 21651.4801 | 0.0041 | 11528.7102
7 |  | 4113044.1831 | 4728201.1252 | 457004.9092 | 3859891.7977 | 2547528.5865 | 295225.1714 | 2842753.7578 | 0.5132 | 1458901.2285 | 0.1224 | 347953.06 | 0.0585 | 166301.0948 | 0.0199 | 56570.7998 |  |  |  | 0.2791 | 793412.5738 |  | 4113044.1831 | 457004.9092 |  | 0 | 0 | [6 empty] | 4113044.1831 | 457004.9092 | 0.00781 | 22201.9068 | 0.0034 | 9665.3628 | 0.0016 | 4548.406
8 |  | 3701739.7648 | 4728201.1252 | 411304.4183 | 3946722.7304 | 2604837.0021 | 265702.6542 | 2870539.6563 | 0.4665 | 1339106.7497 | 0.0906 | 260070.8929 | 0.039 | 111951.0466 | 0.0199 | 57123.7392 |  |  |  | 0.2326 | 667687.5241 |  | 3701739.7648 | 411304.4183 |  | 0 | 0 | [6 empty] | 3701739.7648 | 411304.4183 | 0.00391 | 11223.8101 | 0.0015 | 4305.8095 | 0.000665 | 1908.9089
9 |  | 3331565.7883 | 4728201.1252 | 370173.9765 | 4024870.5699 | 2656414.5761 | 239132.3888 | 2895546.9649 | 0.4241 | 1228001.4678 | 0.0671 | 194291.2013 | 0.026 | 75284.2211 | 0.0065 | 18821.0553 |  |  |  | 0.1938 | 561157.0018 |  | 3331565.7883 | 370173.9765 |  | 0 | 0 | [6 empty] | 3331565.7883 | 370173.9765 | 0.00195 | 5646.3166 | 0.0007 | 2026.8829 | 0.000262 | 758.6333
10 | 1491750 | 2998409.2095 | 4728201.1252 | 333156.5788 | 4095203.6254 | 2702834.3928 | 215219.1499 | 4409803.5427 | 0.3855 | 1699979.2657 | 0.0497 | 219167.2361 | 0.0173 | 76289.6013 | 0.0037 | 16316.2731 |  |  |  | 0.1615 | 712183.2721 |  | 2998409.2095 | 333156.5788 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2998409.2095 | 333156.5788 | 0.00098 | 4321.6075 | 0.0003 | 1322.9411 | 0.000105 | 463.0294
11 |  | 2698568.2886 | 4728201.1252 | 299840.921 | 4158503.3754 | 2744612.2278 | 193697.2349 | 2938309.4627 | 0.3505 | 1029877.4667 | 0.0368 | 108129.7882 | 0.116 | 340843.8977 | 0.0021 | 6170.4499 |  |  |  | 0.1346 | 395496.4537 |  | 2698568.2886 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 2698568.2886 | 299840.921 | 0.00049 | 1439.7716 | 0.00013 | 381.9802 | 4.2e-05 | 123.409
12 |  | 2398727.3676 | 4728201.1252 | 299840.921 | 4188487.4675 | 2764401.7286 | 183502.6436 | 2947904.3722 | 0.3186 | 939202.333 | 0.0273 | 80477.7894 | 0.0077 | 22698.8637 | 0.0012 | 3537.4852 |  |  |  | 0.1122 | 330754.8706 |  | 2398727.3676 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 2398727.3676 | 299840.921 | 0.00024 | 707.497 | 5.9e-05 | 173.9264 | 1.7e-05 | 50.1144
13 |  | 2098886.4467 | 4728201.1252 | 299840.921 | 4218471.5596 | 2784191.2293 | 173308.0523 | 2957499.2817 | 0.2897 | 856787.5419 | 0.0273 | 80739.7304 | 0.0051 | 15083.2463 | 0.0007 | 2070.2495 |  |  |  | 0.0935 | 276526.1828 |  | 2098886.4467 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 2098886.4467 | 299840.921 | 0.00012 | 354.8999 | 2.6e-05 | 76.895 | 6.7e-06 | 19.8152
14 |  | 1799045.5257 | 4728201.1252 | 299840.921 | 4248455.6517 | 2803980.7301 | 163113.461 | 2967094.1911 | 0.2633 | 781235.9005 | 0.0202 | 59935.3027 | 0.0034 | 10088.1202 | 0.0004 | 1186.8377 |  |  |  | 0.0779 | 231136.6375 |  | 1799045.5257 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 1799045.5257 | 299840.921 | 6e-05 | 178.0257 | 1.2e-05 | 35.6051 | 2.7e-06 | 8.0112
15 |  | 1499204.6048 | 4728201.1252 | 299840.921 | 4278439.7438 | 2823770.2309 | 152918.8697 | 2976689.1006 | 0.2394 | 712619.3707 | 0.015 | 44650.3365 | 0.0023 | 6846.3849 | 0.0002 | 595.3378 |  |  |  | 0.0649 | 193187.1226 |  | 1499204.6048 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 1499204.6048 | 299840.921 | 3e-05 | 89.3007 | 5e-06 | 14.8834 | 1.1e-06 | 3.2744
16 |  | 1199363.6838 | 4728201.1252 | 299840.921 | 4308423.8359 | 2843559.7317 | 142724.2784 | 2986284.0101 | 0.2176 | 649815.4006 | 0.0111 | 33147.7525 | 0.0015 | 4479.426 | 0.0001 | 298.6284 |  |  |  | 0.0541 | 161557.9649 |  | 1199363.6838 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 1199363.6838 | 299840.921 | 1e-05 | 29.8628 | 2.3e-06 | 6.8685 | 4e-07 | 1.1945
17 |  | 899522.7629 | 4728201.1252 | 299840.921 | 4338407.928 | 2863349.2325 | 132529.6871 | 2995878.9195 | 0.1978 | 592584.8503 | 0.0082 | 24566.2071 | 0.001 | 2995.8789 | 0.0001 | 299.5879 |  |  |  | 0.0451 | 135114.1393 |  | 899522.7629 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 899522.7629 | 299840.921 | 8e-06 | 23.967 | 1e-06 | 2.9959 | 2e-07 | 0.59918
18 |  | 599681.8419 | 4728201.1252 | 299840.921 | 4368392.0201 | 2883138.7333 | 122335.0957 | 3005473.829 | 0.1799 | 540684.7418 | 0.0045 | 13524.6322 | 0.0007 | 2103.8317 | 7e-05 | 210.3832 |  |  |  | 0.0376 | 113005.816 |  | 599681.8419 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 599681.8419 | 299840.921 | 4e-06 | 12.0219 | 5e-07 | 1.5027 | 1e-07 | 0.30055
19 |  | 299840.921 | 4728201.1252 | 299840.921 | 4398376.1122 | 2902928.234 | 112140.5044 | 3015068.7385 | 0.1635 | 492963.7387 | 0.0033 | 9949.7268 | 0.0005 | 1507.5344 | 2e-05 | 60.3014 |  |  |  | 0.0313 | 94371.6515 |  | 299840.921 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 299840.921 | 299840.921 | 2e-07 | 0.60301 | 2e-07 | 0.60301 | 3e-08 | 0.090452
20 |  | 0 | 4728201.1252 | 299840.921 | 4428360.2043 | 2922717.7348 | 101945.9131 | 3024663.6479 | 0.1486 | 449465.0181 | 0.0025 | 7561.6591 | 0.0003 | 907.3991 | 1e-05 | 30.2466 |  |  |  | 0.0261 | 78943.7212 |  | 0 | 299840.921 |  |  |  |  | 0 | 0 |  |  |  | 0 | 299840.921 | 1e-07 | 0.30247 | 1e-07 | 0.30247 | 1e-08 | 0.030247
| -7107603.6298 |  | 94564022.5045 |  | 79574534.7521 | 52519192.9364 | 5096425.8358 | 50508015.1424 |  | 15932809.0108 |  | -423670.4216 |  | -2899465.5912 |  | -5024136.4173 | 0.34352 | 0.32433 | 0.15883 |  | 5090171.7257 | [9 empty] | -8599353.6298 |  | 0 |  |  |  | -5952619.376 |  | -6586084.1362 |  | -7227352.7259 | -0.60278 | -1.3492 | -1.3176