## Summary
Lumberton & Elizabethtown O&M Summary
All Amounts in Year 2001 $
| 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008
Lumberton O&M | 574387.8 | 851703.3 | 962320.8 | 726165.3 | 728223.3 | 800767.8 | 789448.8 | 757035.3
Elizabethtown O&M | 434546.7 | 687783.6 | 1403504.55 | 518667.45 | 566567.4 | 596099.7 | 632732.1 | 706408.5
Total O&M | 1008934.5 | 1539486.9 | 2365825.35 | 1244832.75 | 1294790.7 | 1396867.5 | 1422180.9 | 1463443.8
Total O&M | 11736362.4
Salary | 1563962.68 | 1563962.68 | 1563962.68 | 1563962.68 | 1563962.68 | 1563962.68 | 1563962.68 | 1563962.68
Burden | 509026.5648 | 509026.5648 | 509026.5648 | 509026.5648 | 509026.5648 | 509026.5648 | 509026.5648 | 509026.5648
Total Salary | 2072989.2448 | 2072989.2448 | 2072989.2448 | 2072989.2448 | 2072989.2448 | 2072989.2448 | 2072989.2448 | 2072989.2448
Total Salary | 16583913.9584
Total O&M and Salary | 28320276.3584

## Lumberton O&M
Lumberton | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008
Rev 4 01/11/00
Building | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
Painting | 15000 | 15000 | 15000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Landscaping | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
Yard equipment | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
Ex Lights | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | F
Hvac | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | F
Elevator | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
Pest control | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | F
Rolling equipment | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | F
Structures maint | 29400 | 29400 | 29400 | 19400 | 19400 | 19400 | 19400 | 19400 | F
Boiler gas & gas inj | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | V | Full Load 7 x24
Main Stack | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | F
Boiler water walls | 0 | 0 | 200000 | 0 | 0 | 0 | 0 | 200000 | V | more we cycle the sooner we'll have spend
Superheaters | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Boiler blowdown | 0 | 1000 | 0 | 1000 | 0 | 1000 | 0 | 1000 | F
Chemical injection pumps | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | F
Traveling grates | 0 | 105000 | 0 | 0 | 0 | 105000 | 0 | 0 | V | function of hours used => 5 to 5 1/2 years
Feeders | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | F
Ash Handling | 10000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | F
Fuel handling | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | F
Boiler feed pumps | 2500 | 5000 | 62500 | 5000 | 5000 | 62500 | 62500 | 5000 | V
Boiler feed system | 0 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | F
Main steam piping | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | F
Turbine extraction | 1000 | 1000 | 20000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
LP steam | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
IP team | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
HP Steam | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
Export steam | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Demineralizer | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | V | Periodic Maintenance
Economizer | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Insulation repair | 10000 | 5000 | 15000 | 5000 | 5000 | 5000 | 5000 | 5000 | V | Periodic Maintenance
Boiler chem wash | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | V | Periodic Maintenance every 10 years
Ash silo repair | 5000 | 5000 | 10000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Airheater replace | 0 | 0 | 0 | 75000 | 0 | 0 | 0 | 0 | V | Periodic Maintenance
Gas duct inlet | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | V
Gas duct outlet | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | V
Bag house replace | 0 | 100000 | 0 | 0 | 0 | 0 | 100000 | 0 | F | Every 4 years
Penthouse casing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
Boiler inspection | 15000 | 15000 | 0 | 15000 | 15000 | 15000 | 15000 | 0 | F
Boiler maintenance | 131500 | 357000 | 427500 | 237000 | 151000 | 314500 | 308500 | 337000
Air testing | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Licensing air | 20000 | 20000 | 20000 | 20000 | 20000 | 20000 | 20000 | 20000 | F
Fuel testing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water monitoring | 12500 | 12500 | 12500 | 12500 | 12500 | 12500 | 12500 | 12500 | F
Waste disposal | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
CEMS Installation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CEMS Gas & Maintenance | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
Emission monitoring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 190000 | CEMS when we become subject to Title IV
Enironmental | 43500 | 43500 | 43500 | 43500 | 43500 | 43500 | 43500 | 43500
Travel expenses | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Meals | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Refreshments | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Employee relations | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | F
Community dontation | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | F
PR | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000 | 19000
Training development | 1000 | 40000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
Training travel | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Training meals | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Safety programs | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | F
Professional dues | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
Training | 7500 | 46500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | F
Phone& fax | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | F
Cell phone | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | F
Office equipment maint | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | F
Copier replacement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
Utilities | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | F
Janitorial | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | F
Office supplies | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | F
Postage meter | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Overnight mail | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | F
Computer S/Hardware | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
Computer support | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Office Expenes | 53400 | 53400 | 53400 | 53400 | 53400 | 53400 | 53400 | 53400 | F
Cooling tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | Periodic Maintenance
Cooling tower box re | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | Periodic Maintenance
Cool tower gear rep | 0 | 0 | 10000 | 0 | 10000 | 0 | 10000 | 0 | F | Periodic Maintenance
Cooling tower repair | 0 | 0 | 10000 | 0 | 10000 | 0 | 10000 | 0 | F | Periodic Maintenance
Generator inspect | 10000 | 0 | 10000 | 0 | 10000 | 10000 | 0 | 10000 | F | Every "x" hours
Generator repair | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | V | Every "x" hours
| 10000 | 0 | 10000 | 60000 | 10000 | 10000 | 0 | 10000
Turbine inspection | 10000 | 10000 | 0 | 10000 | 10000 | 10000 | 10000 | 10000 | F
Turbine repairs | 0 | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | V | Every "y" hours, good for 3 more years
Vacuum pumps | 0 | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | V
Hot well pumps | 0 | 0 | 15000 | 0 | 0 | 0 | 0 | 15000 | V
Turbine repairs | 10000 | 10000 | 622000 | 10000 | 10000 | 10000 | 10000 | 25000
Inst air | 8000 | 0 | 0 | 0 | 8000 | 0 | 0 | 0 | F | Periodic Maintenance
Electrotest 2yrs | 0 | 0 | 25000 | 0 | 25000 | 0 | 25000 | 0 | F | Periodic Maintenance
Electrotest 5yrs | 0 | 0 |  | 0 | 0 | 60000 | 0 | 0 | F | Periodic Maintenance
| 0 | 0 | 25000 | 0 | 25000 | 60000 | 25000 | 0
Fire pump | 5000 | 0 | 5000 | 0 | 5000 | 0 | 5000 | 0 | F | Periodic Maintenance
DA Tank NDT Testing | 5000 | 0 | 0 | 0 | 0 | 5000 | 0 | 0 | F | Periodic Maintenance
Front end loader repair | 2000 | 10000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | V | By Hours
Boiler safety checks | 5000 | 5000 | 35000 | 5000 | 5000 | 5000 | 5000 | 5000 | F | Every Year Hydrostatic Test, Every 8 years Take them off the boiler and be dismantled and tested
L.C. Transformer | 0 | 0 | 15000 | 0 | 15000 | 0 | 15000 | 0 | F | Tested Every 2 years
ID fan motors | 0 | 15000 | 0 | 0 | 0 | 0 | 15000 | 0 | V | Every "z" hours
Hours Generating Power & Steam | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Hours Generating Steam Only | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost Generating Power & Steam | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Cost Generating Steam Only | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Boiler chems | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | V
Demin chems | 30000 | 30000 | 33000 | 30000 | 30000 | 30000 | 30000 | 30000 | V | This would go away with an econo-chem trailer plus one 18 hour man-day 3 times per week. Cost of a trailer is ?
Cooling tower chems | 7000 | 7000 | 8000 | 7000 | 7000 | 7000 | 7000 | 7000 | V
Waste water chems | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | V
Water pretreatment | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | V
Lab supplies | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | F
Chem supplies | 68900 | 68900 | 72900 | 68900 | 68900 | 68900 | 68900 | 68900
Coal Distribution chute GF | 0 | 0 | 0 | 20000 | 0 | 0 | 0 | 0 | F/V | Depends on type of coal and usage
Conveyors belts GF | 0 | 0 | 0 | 0 | 30000 | 0 | 0 | 0 | V | Every 10 years more or less
Coal underfeed GF | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | V | Every 5 years
Coal loadout CCHF | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | V | Based on Usage
Rail Maintenance CCHF | 10000 | 20000 | 10000 | 10000 | 50000 | 10000 | 10000 | 10000 | V | Based on Usage
Coal systems | 20000 | 30000 | 30000 | 40000 | 90000 | 20000 | 20000 | 20000
Co truck | 0 | 0 | 0 | 0 | 25000 | 0 | 0 | 0 |  | 2 trucks - 3/4 ton pick ups
City water | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | V
Total Operations & Maintenance in 2000 $ | 558200 | 827700 | 935200 | 705700 | 707700 | 778200 | 767200 | 735700
Total Operations & Maintenance in Nominal $ | 574387.8 | 874878.9 | 1015627.2 | 786502.65 | 808547.25 | 910260.54 | 917878.08 | 899466.82
Total Fixed Operating Expenses in Nominal $ | 503489.7 | 802051.6 | 936457.8 | 709713.6 | 729829 | 829668.21 | 835446.12 | 815229.68
Maintenance Reserve Accrual Adjustment to Insure There is Never a Negative Balance | 1982.6633
Maintenance Reserve Accrual | 772218.3771 | 772218.3771 | 772218.3771 | 772218.3771 | 772218.3771 | 772218.3771 | 772218.3771 | 772218.3771
Total Variable Operating Expenses | 70898.1 | 72827.3 | 79169.4 | 76789.05 | 78718.25 | 80592.33 | 82431.96 | 84237.14
Upfront Capital Expenditures
Traveling grates | 0
Boiler feed pumps | 60000
Boiler feed system | 25000
Demineralizer | 0
Ash silo repair | 15000
Gas duct inlet | 25000
Gas duct outlet | 25000
CEMS Installation | 230000
Training development | 43000
Copier replacement | 15000
Cooling tower | 150000
Cooling tower box re | 20000
Cool tower gear rep | 10000
Electrotest 5yrs | 60000
L.C. Transformer | 15000
Co truck | 25000
718000
a. We need to O/H both boiler feed pumps to get max flow to bring units to 37.5 MW
b. Every year the feed water control valve on both boiler wash out because of high differantal pressure on these valves we
need to look at adding a variable pressure pump payback should be in 4 years
c. Economizer were replaced to a larger design and have had no tube leakes
d. We need to replace all the fill in the cooling tower to get 37.5
e. We need to replace bad metal in the frames before we add new fill
Note on E17: dbeach: Note a
Note on B27: dbeach: Note b
Note on B35: dbeach: Note c
Note on B50: dbeach: Tested at Elizabethtown
Note on B63: dbeach: Senior Citizen Golf Tournament
Note on B128: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on C128: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on D128: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on E128: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on F128: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on G128: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on H128: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on I128: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating

## Elizabethtown O&M
Elizabethtown | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008
Rev 4 01/11/00
Building | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
Painting | 0 | 15000 | 15000 | 2000 | 2000 | 2000 | 2000 | 2000 | F
Landscaping | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
Yard equipment | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
Ex & Int Lights | 0 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | F
Hvac | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | F
Elevator | 2500 | 2500 | 4000 | 2500 | 2500 | 2500 | 2500 | 2500 | F
Pest control | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | F
Rolling equipment | 1200 | 1200 | 1200 | 1200 | 1250 | 1250 | 1250 | 1250 | F
Structures maint | 13900 | 30900 | 32400 | 17900 | 17950 | 17950 | 17950 | 17950
Boiler gas & gas inj | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | V | Based on Hours run could go as low as 25k
Main Stack | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | F | Periodic Inspection / Mainteneance if we have to replace a stack lliner its 100k
Boiler water walls | 0 | 0 | 200000 | 0 | 0 | 0 | 0 | 200000 | V | Periodic Maintenance based on inspections
Superheaters | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | F
Boiler blowdown | 0 | 1000 | 0 | 1000 | 0 | 1000 | 0 | 1000 | F
Chemical injection | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | F
Traveling grates | 0 | 105000 | 0 | 0 | 0 | 0 | 110000 | 0 | F
Feeders | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F | Feeders take two people, and we don't have good boiler feed control - 3 year pay-back
Ash Handling | 10000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | F
Fuel handling | 5000 | 5000 | 5000 | 5000 | 50000 | 5000 | 5000 | 5000 | F
Boiler feed pumps | 5000 | 5000 | 65000 | 5000 | 5000 | 65000 | 65000 | 5000 | F
Boiler feed system | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | F
Main steam piping | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | F
Turbine extraction | 1000 | 1000 | 5000 | 0 | 0 | 0 | 0 | 0 | F
LP steam | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
IP team | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
HP Steam | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
Export steam | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Demineralizer | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | F | Beads probably need to be replaced, but we son't know until they are inspected
Economizer | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Boiler inspection | 15000 | 15000 | 0 | 15000 | 15000 | 15000 | 15000 | 0 | F
Boiler chem wash | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | V | Depends on the boiler tube samples that are pulled
Plugmill | 0 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Airheater replace | 0 | 0 | 0 | 75000 | 0 | 0 | 0 | 0 | V | Depends on the boiler tube samples that are pulled
Gas duct inlet | 0 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | V | They need to be repaired
Gas duct outlet | 0 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | V | They need to be repaired
Bag house replace | 0 | 100000 | 0 | 0 | 0 | 0 | 0 | 0 | V | Due again in 2003 to 2005
Penthouse casing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
Penthouse roof repair | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
Boiler maintenance | 125500 | 343500 | 386500 | 222500 | 181500 | 197500 | 306500 | 322500
Air testing | 0 | 0 | 5000 | 0 | 0 | 0 | 0 | 5000 | F
Licensing air | 20000 | 20000 | 20000 | 20000 | 20000 | 20000 | 20000 | 20000 | V
Fuel testing | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | V
Water monitoring | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | V
Waste disposal | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
CEMS Installation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
CEMS Gas & Maintenance | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
Emission monitoring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | V
Enironmental | 39000 | 39000 | 44000 | 39000 | 39000 | 39000 | 39000 | 44000
Travel expenses | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | F
Meals | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Refreshments | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Employee relations | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | F
Community dontation | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | F
PR | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000
Training development | 1000 | 40000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
Training travel | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | F
Training meals | 1500 | 1500 | 750 | 750 | 750 | 750 | 750 | 750 | F
Safety programs | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | F
Professional dues | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | F
Training | 7500 | 46500 | 6750 | 6750 | 6750 | 6750 | 6750 | 6750
Phone& fax | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | F
Cell phone | 3000 | 3000 | 3200 | 3300 | 3400 | 3500 | 3600 | 3700 | F
Office equipment maint 3,000 |  | 3000 | 3200 | 3300 | 3300 | 3400 | 3500 | 3500 | F
Copier replacement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
Utilities | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | F
Janitorial | 6000 | 6000 | 6000 | 6300 | 6300 | 6600 | 6600 | 6900 | F
Office supplies | 3000 | 3100 | 3200 | 3300 | 3400 | 3500 | 3600 | 3700 | F
Postage meter | 1000 | 1000 | 1000 | 1000 | 1000 | 1100 | 1100 | 1100 | F
Overnight mail | 2000 | 2000 | 2200 | 2200 | 2400 | 2400 | 2400 | 2500 | F
Computer S/Hardware | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1200 | 1200 | F
Computer support | 1500 | 1500 | 1600 | 1600 | 1700 | 1700 | 1800 | 1800 | F
Office Expenes | 48500 | 51600 | 52400 | 53000 | 53500 | 54200 | 54800 | 55400
Cooling tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | Periodic Maintenance
Cooling tower box re | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | Periodic Maintenance
Cool tower gear rep | 0 | 0 | 10000 | 0 | 10000 | 0 | 10000 | 0 | F | Periodic Maintenance
Tower Repair | 0 | 0 | 10000 | 0 | 10000 | 0 | 10000 | 0
Generator inspection | 10000 | 0 | 10000 | 10000 | 0 | 10000 | 10000 | 0 | F | Periodic Maintenance
Generator repair | 0 | 10000 | 0 | 0 | 60000 | 0 | 0 | 60000 | V
| 10000 | 10000 | 10000 | 10000 | 60000 | 10000 | 10000 | 60000
Turbine inspection | 10000 | 10000 | 0 | 10000 | 10000 | 10000 | 10000 | 10000 | F | Periodic Maintenance
Turbine repairs | 0 | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | V
Vacuum pumps | 0 | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | V
Hot well pumps | 0 | 0 | 15000 | 0 | 0 | 0 | 0 | 0 | V
Steam jet ejt | 0 | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | V
Turbine repairs | 10000 | 10000 | 625000 | 10000 | 10000 | 10000 | 10000 | 10000
Inst air | 8000 | 0 | 0 | 8000 | 0 | 0 | 0 | 8000
Electrotest 2yrs | 0 | 0 | 25000 | 0 | 25000 | 0 | 0 | 25000
Electrotest 5yrs | 0 | 0 | 0 | 0 | 0 | 60000 | 0 | 0
| 0 | 0 | 25000 | 0 | 25000 | 60000 | 0 | 25000
Well PP repair/Acid trmt | 5000 | 0 | 0 | 0 | 5000 | 0 | 0 | 0 | F | Periodic Maintenance
Fire pump | 5000 | 0 | 5000 | 0 | 5000 | 0 | 5000 | 0 | F | Periodic Maintenance
DA Tank NDT Testing | 5000 | 0 | 0 | 0 | 0 | 5000 | 0 | 0 | F | Periodic Maintenance
Neuralization tank | 0 | 0 | 0 | 0 | 0 | 12000 | 0 | 0 | F | Periodic Maintenance
Front end loader repair | 10000 | 2000 | 2000 | 2000 | 2000 | 2000 | 10000 | 2000 | V | Periodic Maintenance
Boiler safety checks | 5000 | 5000 | 35000 | 5000 | 5000 | 5000 | 15000 | 5000
L.C. Transformer | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0
ID fan motors | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0 | V
Hours Generating Power & Steam | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Hours Generating Steam Only | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost Generating Power & Steam | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Cost Generating Steam Only | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Boiler chems | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | V
Demin chems | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | V | Well Water - Candidate for the econo-chem trailer
cooling tower chems | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | V
Waste water chems | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | V
Water pretrearment | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | V
Lab chems | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | F
| 108900 | 108900 | 108900 | 108900 | 108900 | 108900 | 108900 | 108900
Total Operations & Maintenance in 2000 $ | 422300 | 668400 | 1363950 | 504050 | 550600 | 579300 | 614900 | 686500
Total Operations & Maintenance in Nominal $ | 434546.7 | 706498.8 | 1481249.7 | 561763.725 | 629060.5 | 677607.21 | 735666.36 | 839314.9
Total Fixed Operating Expenses in Nominal $ | 322488.6 | 591391.5 | 1362984.3 | 440394.675 | 504642.25 | 550226.88 | 605378.4 | 706173.76
Maintenance Reserve Accrual Adjustment to Insure There is Never a Negative Balance | 184562.2523
Maintenance Reserve Accrual | 820022.2979 | 820022.2979 | 820022.2979 | 820022.2979 | 820022.2979 | 820022.2979 | 820022.2979 | 820022.2979
Total Variable Operating Expenses in Nominal $ | 112058.1 | 115107.3 | 118265.4 | 121369.05 | 124418.25 | 127380.33 | 130287.96 | 133141.14
Upfront Capital Expenditures
Painting | 30000
Ex & Int Lights | 4000
Traveling grates | 0
Feeders | 212000
Boiler feed pumps | 60000
Demineralizer | 0
Plugmill | 10000
Gas duct inlet | 15000
Gas duct outlet | 15000
Penthouse casing | 0
Penthouse roof repair | 18000
CEMS Installation | 230000
Training development | 43000
Copier replacement | 15000
Cooling tower | 150000
Cooling tower box re | 60000
Cool tower gear rep | 10000
Electrotest 5yrs | 60000
L.C. Transformer | 15000
ID fan motors | 15000
962000
a. Need to install new feeders to smooth out operation and inprove control to boilers also with the old feeder it takes 2 men to
start 1 up and put it in service , the new style can be started from the control room
b. We need to O/H both boiler feed pumps to get to max flow to reach 37.5 MW
c. Every year the feed water control valves on both boilers wash out because og high differantal pressure, we need to look at
adding a variable pressure pump.
d. The 2" condensate line to steam host needs to be replaced
e. Demin need a new PLC system
f. We need to replace all fill in the cooling tower to get to full load of 37.5 MW
g. Structure in very poor shape
Note on B26: dbeach: Note c
Note on B32: dbeach: Note d
Note on B41: dbeach: replaced in 1998
Note on B132: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on C132: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on D132: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on E132: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on F132: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on G132: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on H132: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating
Note on I132: dbeach: Per Jerry Campbell on 12/19/00 Boiler Chemicals $2.30/hr when supplying steam only $2.50 when generating

## Power Plant Payroll
Lumberton & Elizabethtown Power Plant Payroll
|  | 1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 2001 |  | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008
Escalation |  | 0% |  | 2.8% | 2.9% | 2.85% | 2.8% | 2.72% | 2.67% | 2.62%
Cumulative escalation |  | 0% |  | 2.8% | 5.7% | 8.55% | 11.35% | 14.07% | 16.74% | 19.36%
Payroll Expense |  | 1563962.68 |  | 1607753.635 | 1654378.4905 | 1701528.2774 | 1749171.0692 | 1796748.5223 | 1844721.7078 | 1893053.4166
Burden |  | 509026.5648 |  | 524791.2985 | 541576.236 | 558550.1491 | 575701.5441 | 592829.4174 | 610099.7546 | 627499.1603
Bonus Expense |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2072989.2448 |  | 2132544.9336 | 2195954.7265 | 2260078.4265 | 2324872.6133 | 2389577.9397 | 2454821.4624 | 2520552.5768
[13 empty] | Regular | Overtime | Total | Total
[13 empty] | Wage | Wage | Regular | Overtime | Total | Burden | Burden | Total
Salaries and Wage Rates in 2001 $ | [8 empty] | Regular | Regular | Overtime | Overtime | Cost | Cost | Wage | Wage | Wage | Rate | Cost | Payroll | Expected | Expected
|  | Position | Name | Salary | Hourly Rate | Overtime Rate |  | Weeks | Hours/Week | Hours/Year | Percentage | Hours | per Person | per Person | Cost | Cost | Cost |  |  | Cost | Bonus Rate | Bonus
Salary | 1 | Plant Manager | Jerry Campbell | 150000 | [12 empty] | 150000 | 0% | 0 | 150000 | 0 | 0
Salary | 1 | Opns Supervisor | Randy Musselwhite | 76811 | [12 empty] | 76811 | 36% | 27651.96 | 104462.96 | 0 | 0
Salary | 1 | Maint Supervisor | Open | 66592 | [12 empty] | 66592 | 36% | 23973.12 | 90565.12 | 0 | 0
Salary Plus Overtime | 1 | Shift Supervisors | Stan Bailey |  | 36.22 | 36.22 |  | 52 | 40 | 2080 | 10% | 208 | 75337.6 | 7533.76 | 75337.6 | 7533.76 | 82871.36 | 36% | 29833.6896 | 112705.0496 | 0 | 0
Salary Plus Overtime | 1 | Shift Supervisors | Eric Pait |  | 30.69 | 30.69 |  | 52 | 40 | 2080 | 10% | 208 | 63835.2 | 6383.52 | 63835.2 | 6383.52 | 70218.72 | 36% | 25278.7392 | 95497.4592 | 0 | 0
Hourly | 1 | Tech 1 | David Jackson |  | 25.44 | 38.16 |  | 52 | 40 | 2080 | 10% | 208 | 52915.2 | 7937.28 | 52915.2 | 7937.28 | 60852.48 | 36% | 21906.8928 | 82759.3728 | 0 | 0
Hourly | 1 | Tech 1 | Bill Huggins |  | 24.64 | 36.96 |  | 52 | 40 | 2080 | 10% | 208 | 51251.2 | 7687.68 | 51251.2 | 7687.68 | 58938.88 | 36% | 21217.9968 | 80156.8768 | 0 | 0
Hourly | 1 | Tech 1 | Frank Melvin |  | 24.95 | 37.425 |  | 52 | 40 | 2080 | 10% | 208 | 51896 | 7784.4 | 51896 | 7784.4 | 59680.4 | 36% | 21484.944 | 81165.344 | 0 | 0
Hourly | 1 | Tech 1 | David Evers |  | 24.82 | 37.23 |  | 52 | 40 | 2080 | 10% | 208 | 51625.6 | 7743.84 | 51625.6 | 7743.84 | 59369.44 | 36% | 21372.9984 | 80742.4384 | 0 | 0
Hourly | 1 | Tech 1 | Greg Boykin |  | 22.3 | 33.45 |  | 52 | 40 | 2080 | 10% | 208 | 46384 | 6957.6 | 46384 | 6957.6 | 53341.6 | 36% | 19202.976 | 72544.576 | 0 | 0
Hourly | 1 | Tech 1 | Donnie Todd |  | 20.56 | 30.84 |  | 52 | 40 | 2080 | 10% | 208 | 42764.8 | 6414.72 | 42764.8 | 6414.72 | 49179.52 | 36% | 17704.6272 | 66884.1472 | 0 | 0
Hourly | 1 | Tech 1 | Terrence Lesane |  | 19.77 | 29.655 |  | 52 | 40 | 2080 | 10% | 208 | 41121.6 | 6168.24 | 41121.6 | 6168.24 | 47289.84 | 36% | 17024.3424 | 64314.1824 | 0 | 0
Hourly | 1 | Tech 1 | Brian Wilkerson |  | 20.84 | 31.26 |  | 52 | 40 | 2080 | 10% | 208 | 43347.2 | 6502.08 | 43347.2 | 6502.08 | 49849.28 | 36% | 17945.7408 | 67795.0208 | 0 | 0
Hourly | 1 | Tech 1 | Terry Nealy |  | 21.94 | 32.91 |  | 52 | 40 | 2080 | 10% | 208 | 45635.2 | 6845.28 | 45635.2 | 6845.28 | 52480.48 | 36% | 18892.9728 | 71373.4528 | 0 | 0
Hourly | 1 | Tech 1 | Randy Coates |  | 19.34 | 29.01 |  | 52 | 40 | 2080 | 10% | 208 | 40227.2 | 6034.08 | 40227.2 | 6034.08 | 46261.28 | 36% | 16654.0608 | 62915.3408 | 0 | 0
Hourly | 1 | Tech 1 | Rick Houser |  | 20 | 30 |  | 52 | 40 | 2080 | 10% | 208 | 41600 | 6240 | 41600 | 6240 | 47840 | 36% | 17222.4 | 65062.4 | 0 | 0
Hourly | 1 | Tech 2 | Billy Gerald |  | 16.29 | 24.435 |  | 52 | 40 | 2080 | 10% | 208 | 33883.2 | 5082.48 | 33883.2 | 5082.48 | 38965.68 | 36% | 14027.6448 | 52993.3248 | 0 | 0
Hourly | 1 | Tech 2 | Cleveland Oxendine |  | 17.17 | 25.755 |  | 52 | 40 | 2080 | 10% | 208 | 35713.6 | 5357.04 | 35713.6 | 5357.04 | 41070.64 | 36% | 14785.4304 | 55856.0704 | 0 | 0
Hourly | 1 | Tech 2 | Chris Munns |  | 19.68 | 29.52 |  | 52 | 40 | 2080 | 10% | 208 | 40934.4 | 6140.16 | 40934.4 | 6140.16 | 47074.56 | 36% | 16946.8416 | 64021.4016 | 0 | 0
Hourly | 1 | Tech 2 | Leon Shaw |  | 18.95 | 28.425 |  | 52 | 40 | 2080 | 10% | 208 | 39416 | 5912.4 | 39416 | 5912.4 | 45328.4 | 36% | 16318.224 | 61646.624 | 0 | 0
Hourly | 1 | Tech 2 | Open |  | 14.28 | 21.42 |  | 52 | 40 | 2080 | 10% | 208 | 29702.4 | 4455.36 | 29702.4 | 4455.36 | 34157.76 | 36% | 12296.7936 | 46454.5536 | 0 | 0
Hourly | 1 | Tech 2 | Open |  | 14.28 | 21.42 |  | 52 | 40 | 2080 | 10% | 208 | 29702.4 | 4455.36 | 29702.4 | 4455.36 | 34157.76 | 36% | 12296.7936 | 46454.5536 | 0 | 0
Hourly | 1 | Tech 3 | Michael Floyd |  | 12.61 | 18.915 |  | 52 | 40 | 2080 | 10% | 208 | 26228.8 | 3934.32 | 26228.8 | 3934.32 | 30163.12 | 36% | 10858.7232 | 41021.8432 | 0 | 0
Hourly | 1 | Tech 3 | Joe Bivens |  | 12.01 | 18.015 |  | 52 | 40 | 2080 | 10% | 208 | 24980.8 | 3747.12 | 24980.8 | 3747.12 | 28727.92 | 36% | 10342.0512 | 39069.9712 | 0 | 0
Hourly | 1 | Tech 3 | Ed Dailey |  | 12.01 | 18.015 |  | 52 | 40 | 2080 | 10% | 208 | 24980.8 | 3747.12 | 24980.8 | 3747.12 | 28727.92 | 36% | 10342.0512 | 39069.9712 | 0 | 0
Hourly | 1 | Tech 3 | Open |  | 12.01 | 18.015 |  | 52 | 40 | 2080 | 10% | 208 | 24980.8 | 3747.12 | 24980.8 | 3747.12 | 28727.92 | 36% | 10342.0512 | 39069.9712 | 0 | 0
Hourly | 1 | Tech 3 | Open |  | 12.01 | 18.015 |  | 52 | 40 | 2080 | 10% | 208 | 24980.8 | 3747.12 | 24980.8 | 3747.12 | 28727.92 | 36% | 10342.0512 | 39069.9712 | 0 | 0
| 27 | [15 empty] | 1417405.88 |  | 456266.1168 | 1873671.9968 |  | 0
Salary | 1 | Comptroller |  | 72800 | [12 empty] | 72800 | 36% | 26208 | 99008 | 0 | 0
Hourly | 1 | Office Secretary | Judy Walters |  | 18.46 | 27.69 |  | 52 | 40 | 2080 | 0% | 0 | 38396.8 | 0 | 38396.8 | 0 | 38396.8 | 36% | 13822.848 | 52219.648 | 0 | 0
Hourly | 1 | Purchasing/Invoicing Clerk | Vicky Williamson |  | 17 | 25.5 |  | 52 | 40 | 2080 | 0% | 0 | 35360 | 0 | 35360 | 0 | 35360 | 36% | 12729.6 | 48089.6 | 0 | 0
| 3 | [15 empty] | 146556.8 |  | 52760.448 | 199317.248 |  | 0
Total Personnel | 30 | [15 empty] | 1563962.68 |  | 509026.5648 | 2072989.2448 |  | 0
Benefits
Sick time
401(k) w/ 6% Contribution
PPO for Medical
Vacation based on Seniority
|  | 5 |  | yrs | 2 | wks
|  | 15 |  | yrs | 3 | wks
|  | Over 15 |  | yrs | 4 | wks
|  | Uniforms |  | ?
Bonus
|  | Plant Mgr |  | 20000
|  | Opns Supv |  | 12000
|  | Shift Supv |  | 8000
|  | Tech 1 |  | 7000
|  | Tech 2 |  | 6000
|  | Tech 3 |  | 4000
Other Assumptions
10% Overtime
They will receive a salary increase to match inflation every year
Note on V18: dbeach: This is purely my assumption
Note on V19: dbeach: This is purely my assumption
Note on F40: dbeach: Rate is between $11.50 and $17.00
Note on F41: dbeach: Rate is between $11.50 and $17.00
Note on F42: dbeach: Rate is between $11.50 and $17.00
Note on F43: dbeach: Rate is between $11.50 and $17.00
Note on F44: dbeach: Rate is between $11.50 and $17.00

## Inflation
US Inflation Rates |  | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008
Annual Inflation Rates | % | 2.9% | 2.8% | 2.9% | 2.85% | 2.8% | 2.72% | 2.67% | 2.62%
Cumulative Inflation Rates | % | 2.9% | 5.7% | 8.6% | 11.45% | 14.25% | 16.97% | 19.64% | 22.26%