## COVER
TRENT MESA
MONTHLY REPORT
FOR
2002-01-02
**ALL TIMES ARE GMT**

## WTG Down
CLEAR SKY
SIGNIFICANT WTG DOWN TIME
Month: |  |  |  |  | Reason: F=fault, U=unscheduled maint. S= scheduled maint. C=curtail
WTG # | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
91 | 2002-03-14 | 0800 | 2002-03-15 | 0930 | 25.5 | F | MS-3 failed.
121 | 2002-03-07 | 700 | 2002-03-13 | 830 | 144 | F | MS-3 failed.
74 | 2002-03-11 | 1240 | 2002-03-12 | 1400 | 26 | F | Battery charging voltage not ok.
105 | 2002-03-08 | 1150 | 2002-03-08 | 1545 | 27.5 | F | 10F3 and 3F1 in top box blown.
88 | 2002-03-19 | 500 | 2002-03-20 | 1630 | 35 | F | PMT tripped, commisioning lost, MS3 defective. Had to wait for part
81 | 2002-03-12 | 1000 | 3/14 | 1500 | 53 | F | Closeout on blade one fixed, let Sikaflex dry.
63 | 2002-03-08 | 0149 | 2002-03-09 | 2239 | 42 | F | Battery charging voltage not ok.
41 | 2002-03-08 | 0745 | 2002-03-12 | 950 | 38 | F | Encoder cable cold solder joint on CSC3-LG-60. Replaced component.
47 | 2002-03-04 | 1000 | 2002-03-05 | 2236 | 36 | F | Repaired torn insulation on 3 generator cables.
35 | 2002-03-25 | 1930 | 2002-03-25 | 1900 | 23.5 | F | Axis 3 lost zero and axis 1 had broken sight glass.
38 | 2002-03-24 | 0645 | 2002-03-25 | 1345 | 31 | F | Motor protection top cabinet. Checked circuit.
114 | 2002-03-27 | 0530 | 2002-03-29 | 1100 | 53.5 | F | DC link voltage too high.
63 | 2002-03-26 | 0130 | 2002-03-27 | 1215 | 35.25 | F | Battery charging voltage not ok.
78 | 2002-03-25 | 0500 | 2002-03-26 | 1300 | 32 | F | Lost commissioning.
80 | 2002-03-25 | 0800 | 2002-03-26 | 1400 | 30 | F | Lost commissioning and ratio gen/rotor speed.
13 | 2002-03-28 | 0500 | 2002-03-31 | 2400 | 91 | F | Broken piece inside CB-1 breaker.
100 | 2002-03-03 | 1500 | 2002-03-04 | 830 | 17.5 | F | CSC HUR had bad connection.
64 | 2002-03-03 | 1900 | 2002-03-04 | 930 | 14.5 | F | SEG lost commissioning
105 | 2002-03-03 | 2000 | 2002-03-04 | 900 | 13 | F | SEG lost commissioning
82 | 2002-03-03 | 2030 | 2002-03-04 | 830 | 12 | F | SEG lost commissioning
116 | 2002-03-20 | 2300 | 2002-03-21 | 1445 | 15.75 | F | Axis 2 lost zero
84 | 2002-03-18 | 0400 | 2002-03-23 | 1200 | 128 | F | Current asymmetry caused by burned wire.
108 | 2002-03-18 | 0500 | 2002-03-23 | 1330 | 128.5 | F | Axis 2 pitch problem caused by loose wire at thyristor driver
58 | 2002-03-25 | 0400 | 2002-03-27 | 1030 | 54.5 | F | Safety chain problem
59 | 2002-03-24 | 0500 | 2002-03-27 | 1130 | 78.5 | F | Brake sensor shorting out on reset
91 | 2002-03-24 | 0900 | 2002-03-25 | 1800 | 33 | F | Axis 1 lost zero
70 | 2002-03-24 | 0700 | 2002-03-25 | 1600 | 33 | F | SEG lost commissioning
88 | 2002-03-19 | 1015 | 2002-03-22 | 2000 | 81.75 | F | DC link voltage too high.
4 | 2002-03-25 | 0130 | 2002-03-26 | 1100 | 33.5 | F | Various converter faults. Replaced CSC HUR
4 | 2002-03-30 | 1230 | 2002-03-31 | 2400 | 35.5 | F | Battery charging voltage not ok.
116 | 2002-03-20 | 2300 | 2002-03-21 | 1600 | 17 | F | Axis 1 lost zero
4 | 2002-03-25 | 0500 | 2002-03-28 | 0900 | 76 | F | Replaced CSC HUR.
103 | 2002-03-30 | 1030 | 2002-03-31 | 2400 | 37.5 | F | SEG lost commissioning
70 | 2002-03-30 | 1800 | 2002-03-31 | 2400 | 30 | F | Generator fan motor shaft broke.
108 | 2002-03-30 | 0300 | 2002-03-31 | 1130 | 32.5 | F | CCU collective faults
70 | 2002-03-30 | 0600 | 2002-03-31 | 1030 | 28.5 | F | Faulted on Overload top box due to broken fan motor shaft on gen cooling fan.
100 | 2002-03-18 | 2245 | 2002-03-23 | 0900 | 106.25 | F | Safety chain problem
67 | 2002-03-01 | 0000 | 2002-03-31 | 2400 | 744 | F | Tower cables are burned.
59 | 2002-03-28 | 2200 | 2002-03-29 | 1030 | 12.5 | F | Feedback CCU
118 | 2002-03-28 | 1200 | 2002-03-29 | 1130 | 23.5 | F | MS-3 failed.
61 | 2002-03-28 | 1700 | 2002-03-29 | 1330 | 20.5 | F | MS-3 failed.
4 | 2002-03-28 | 1600 | 2002-03-31 | 1515 | 71.25 | F | Converter faults
105 | 2002-03-29 | 2345 | 2002-03-31 | 2400 | 48.25 | F | Axis 1 pitch problems
61 | 2002-03-01 | 0000 | 2002-03-04 | 1830 | 90.5 | F | Replaced slipring on gearbox. Had to wait for part to come in.
76 | 2002-03-01 | 0000 | 2002-03-04 | 1230 | 84.5 | F | Intermittent ground fault in hub.
51 | 2002-03-03 | 1730 | 2002-03-04 | 1400 | 20.5 | F | Collective disturbiance pitch controller
53 | 2002-03-04 | 1430 | 2002-03-05 | 1200 | 21.5 | F | PMT and CB-1 tripped.
70 | 2002-03-06 | 1200 | 2002-03-07 | 1500 | 27 | F | SEG lost commissioning
41 | 2002-03-07 | 0530 | 2002-03-11 | 1200 | 102.5 | F | Replaced damaged generator encoder cable and rotor cable in generator j-box
81 | 2002-03-11 | 1300 | 2002-03-15 | 1500 | 98 | F | Blade closeout came loose
86 | 2002-03-11 | 1230 | 2002-03-18 | 1900 | 174.5 | F | Top IGBT rack had bad filter. Had to wait for part
121 | 2002-03-11 | 1730 | 2002-03-13 | 1230 | 43 | F | MS-3 failed. Had to wait for part
91 | 2002-03-14 | 0900 | 2002-03-14 | 830 | 23.5 | F | MS-3 failed.
105 | 2002-03-16 | 0230 | 2002-03-18 | 1145 | 57.25 | F | Battery charging voltage not ok.
61 | 2002-03-17 | 0330 | 2002-03-21 | 1200 | 104.5 | F | Blade closeout bolt fell out and broke sight glass
41 | 2002-03-16 | 0645 | 2002-03-18 | 0745 | 49 | F | PMT tripped.
15 | 2002-03-18 | 1430 | 2002-03-31 | 2400 | 321.5 | F | Top IGBT rack went out.
53 | 2002-03-20 | 0800 | 2002-03-24 | 1445 | 102.75 | F | Engineering was repairing some test equipment in the gearbox.
102 | 2002-03-19 | 1330 | 2002-03-21 | 1000 | 44.5 | F | MS-3 failed.

## GRID
CLEAR SKY
GRID VARIANCE
Chargeable to: A=AEP, N=Force Majeure, E=Enron, T= TXU
Month: |  |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
E | 2002-03-20 | 0750 | 2002-03-20 | 1430 | 7.16 | S | Scheduled power outage on 69kV line for moving arrestors to the correct side of gang switch and repairing damaged gang switch blade.

## WEATHER
CLEAR SKY
WEATHER EVENTS
Month:
Date | Time | Event | Comments
N/A | N/A | N/A | No weather events

## RECALL
CLEAR SKY
CREW CALL-OUTS
Month:
Date | Time | Who | Reason
N/A | N/A | N/A | No crew call-outs.

## PARTS
CLEAR SKY
PARTS USAGE
Month: | 2002-03-01
Date | WTG # | EW Part # | Description | Qty. | Comments
2002-03-06 | 57 | T56631000630 | power protection switch 4-6.3 | 1
2002-03-06 | 57 |  | nacelle latch | 3
2002-03-06 | 59 |  | nacelle latch | 1
2002-03-06 | 88 | UX5670030070 |  | 1
2002-03-06 | 57 |  | A10 288 | 1
2002-03-06 | 61 | T56910153102 | Assy, slipring,60Hz,TZ1.5 | 1
2002-03-06 | 109 | T56031020396 | MS3 | 1
2002-03-06 | 61 | UX56137094800 | Cable, fiber optic, assy 2 channel, EW1.5 | 1
2002-03-06 | 61 | T56137049800 | PLC Fast Bus Slave | 1
2002-03-06 | 61 | T56137049500 | PLC Fast Busmaster | 1
2002-03-06 | 19 | T56031155076 | IGBT | 1
2002-03-06 | 51 | T56031155076 | IGBT | 1
2002-03-06 | 51 | T56031155076 | IGBT | 1
2002-03-06 | 88 | T56031031646 | Air Contactor 3 pole | 1
2002-03-06 | 88 | UX59901000001 | 3hp CAP,600V,30KVAR,indoor | 1
2002-03-06 | 107 |  | keyboard | 1
2002-03-06 | 61 |  | Ethernet cable | 250ft
2002-03-06 | 61 | T56137900200 | PLC digital input | 1
2002-03-06 | 61 | T83701043518 | anemometer/low wind transducer | 1
2002-03-06 | 61 | T56137991800 | PLC COM 1-4 Interface | 1
2002-03-06 | 61 | T56137900300 | PLC digital output 32-times | 1
2002-03-06 | 57 | T56779400916 |  | 1
2002-03-06 | 73 | T56636211354 | circuit breaker 3-polig | 1
2002-03-06 | 93 | T83706043128 | wind vane | 1
2002-03-06 | 90 | UX5620100004 | switch assembly,micro, circuit breaker | 1
2002-03-06 | 90 | T56114798844 | Overvoltage protection | 1
2002-03-06 | 81 |  | nacelle latch | 2
2002-03-06 | 2 | T56031020396 | MS3 | 1
2002-03-06 | 53 | T56031020396 | MS3 | 1
2002-03-06 | 81 | T56870000204 |  | 1
2002-03-06 | 93 | T92980850022 | Arretierungsbock, Bresscheibe,TW1.5 | 1
2002-03-11 | 92 | T56031019936 | Control system for main converter | 1
2002-03-11 | 51 | T56137900400 | PLC digital output 16x | 1
2002-03-11 | 51 | T56137899700 | PLC digital Input 32x | 1
2002-03-11 | 51 | T56137965000 | PLC COM 1-4 Interface | 1
2002-03-11 | 51 | T56137909700 | PLC analog In/Out | 2
2002-03-11 | 51 | T56137932300 | PLC power supply Bachmann | 1
2002-03-11 | 51 | T56137049500 | PLC Fast Busmaster | 1
2002-03-11 | 105 | UX5990100063 | Fuse 10A | 2
2002-03-11 | 30 | UX59901000045 | Grill/Fliter Kit 7" | 1
2002-03-11 | 20 | T56137899700 | PLC digital Input 32x | 1
2002-03-11 | 20 | T56137909700 | PLC analog In/Out | 2
2002-03-11 | 20 | T56137900400 | PLC digital output 16x | 1
2002-03-11 | 20 | T56137932300 | PLC power supply Bachmann | 1
2002-03-11 | 20 | T56137049500 | PLC Fast Busmaster | 1
2002-03-11 | 20 | T56137965000 | PLC COM 1-4 Interface | 1
2002-03-11 | 38 | UX59901000128 | PITCH MOTOR ENCODER | 1
2002-03-11 | 119 | T56137070900 | PLC INC 1 INC 2 | 1
2002-03-11 | 105 | T56114798844 | Overvoltage protection | 1
2002-03-11 | 92 | T56031021337 | Display and Control unit for Concycle-Generator | 1
2002-03-11 | 119 | T56137049800 | PLC Fast Bus Slave | 1
2002-03-11 | 119 | UX56137094800 | Cable, fiber optic, assy 2 channel, EW1.5 | 1
2002-03-11 | 17 | T56137899700 | PLC digital Input 32x | 1
2002-03-11 | 17 | T56137909700 | PLC analog In/Out | 2
2002-03-11 | 17 | T56137900400 | PLC digital output 16x | 1
2002-03-11 | 17 | T56137932300 | PLC power supply Bachmann | 1
2002-03-11 | 17 | T56137049500 | PLC Fast Busmaster | 1
2002-03-11 | 17 | T56137965000 | PLC COM 1-4 Interface | 1
2002-03-11 | 44 | T56137049500 | PLC Fast Busmaster | 1
2002-03-11 | 44 | T56137049800 | PLC Fast Bus Slave | 1
2002-03-18 | 44 | T56266000080 | d.c. supply 230/24v-8A | 1
2002-03-18 | 47 | T56137965000 | PLC COM 1-4 Interface | 1
2002-03-18 | 44 | UX56137094800 | Cable, fiber optic, assy 2 channel, EW1.5 | 2
2002-03-18 | 119 | T56137070800 | PLC analog In/Out | 1
2002-03-18 | 54 | T56114798682 | Overvoltage protection | 1
2002-03-18 | 54 | T56225827250 | Battery monitor S1UM 1U 1V-500V/AC/DC | 1
2002-03-18 | 105 | T56836060333 | COMPUTER 60Hz, TZ1.5, S#PC-DTD(1) | 1
2002-03-18 | 28 | T56137899700 | PLC digital Input 32x | 1
2002-03-18 | 70 | T56031020396 | MS3 | 1
2002-03-18 | 46 | T56225827250 | Battery monitor S1UM 1U 1V-500V/AC/DC | 1
2002-03-18 | 45 | T56137909700 | PLC analog In/Out | 1
2002-03-18 | 61 | UX59901000103 | OIL SITE GLASS M22 | 1
2002-03-18 | scada | T5603152543 | Terminal, Ring, 1.52MM2, Type 630/4 | 1
2002-03-21 | 86 | GSC-F12U | SEG DU/DT filter | 1
2002-03-25 | 43 | T56031020396 | MS3 | 1
2002-03-25 | 116 | UX59901000128 | PITCH MOTOR ENCODER | 1
2002-03-25 | 47 | T92980850022 | ROTOR LOCK | 1
2002-03-25 | 41 | T56031020396 | MS3 | 1
2002-03-25 | 45 | UX59901000005 | ELEC OPER 100-130VAC/DC E1/E6 | 1
2002-03-25 | 23 | T56226072012 | Batteries hub panel | 2
2002-03-25 | 100 | T56137049500 | PLC Fast Busmaster | 1
2002-03-25 | 100 | T56137899700 | PLC digital Input 32x | 1
2002-03-25 | 100 | T56137932300 | PLC power supply Bachmann | 1
2002-03-25 | 100 | T56137900400 | PLC digital output 16x | 1
2002-03-25 | 100 | UX59901000145 | PLC "Can"Bus Master, in main cabinet | 1
2002-03-25 | 100 | T56137965000 | PLC COM 1-4 Interface | 1
2002-03-25 | 70 | T56031153405 | Interference suppression filter MS3 | 1
2002-03-25 | 53 | T92980850022 | ROTOR LOCK | 1
2002-03-25 | 47 | T56836060333 | COMPUTER 60Hz, TZ1.5, S#PC-DTD(1) | 1
2002-03-25 | 100 | UX59901000135 | PLC BACKBOARD FOR OLC MOD | 1
2002-03-25 | 58 | UX59901000076 | CONTACT ELEMENT EC11 CONTACT BLOCK | 2
2002-03-25 | 116 | UX59901000128 | PITCH MOTOR ENCODER | 1
2002-03-25 | 68 | T56031153405 | Interference suppression filter MS3 | 1
2002-03-25 | 70 | T56031153405 | Interference suppression filter MS3 | 1
2002-03-25 | 52 | t566031020396 | MS3 | 1
2002-03-25 | 105 | UX59901000063 | Fuse 10A | 8
2002-03-28 | 91 | T56137965000 | PLC COM 1-4 Interface | 1
2002-03-28 | 30 | UX59901000029 | Fuse 50A Class J | 3
2002-03-28 | 51 | T56031020396 | Module to DC voltage measuring | 1
2002-03-28 | 59 | T56137049500 | PLC Fast Busmaster | 1
2002-03-28 | 105 | UX59901000063 | Fuse 10A | 2
2002-03-28 | 59 | T56137909700 | PLC analog In/Out | 1
2002-03-28 | 59 | T56137899700 | PLC digital Input 32x | 1
2002-03-28 | 59 | T56137900400 | PLC digital output 16x | 1
2002-03-28 | 59 | T56137965000 | PLC COM 1-4 Interface | 1
2002-03-28 | 4 | T56137049500 | PLC Fast Busmaster | 1
2002-03-25 | 22 |  | CB3 | 1
2002-03-25 | 22 |  | DIGITRIP RMS 310 | 1
2002-03-28 | 4 | T56137899700 | PLC digital Input 32x | 1
2002-03-28 | 4 | T56137900400 | PLC digital output 16x | 1
2002-03-28 | 4 | T56137909700 | PLC analog In/Out | 2
2002-03-28 | 59 | T56137049800 | PLC Fast Bus Slave | 1
2002-03-28 | 70 | T56604010213 | auxillary relay 3 pole | 1
2002-03-28 | 107 | T56604010213 | auxillary relay 3 pole | 1
2002-03-28 | 58 | T56260102001 | Rotor -overspeed monitor | 1
2002-03-28 | 58 | UX56750030070 | Sensor, Prox, 7M cable | 1
2002-03-28 | 58 | UX59901000112 | Indicator ON/OFF pad wear | 1
2002-03-28 | 4 | T56031019947 | Control system for main converter | 1
2002-03-28 | 67 | T56137899700 | PLC digital Input 32x | 1
2002-03-28 | 67 | T56137900200 | PLC digital Input | 1
2002-03-28 | 4 |  | HUR CSC rev 3.5.3 | 1
2002-03-28 | 78 |  | PCH 1026 Vibration Monitor | 1
2002-03-28 | 82 | T56604010213 | DILEM-10-A Relay | 1
2002-03-28 | 68 | T56604031882 | ETRY-11-A | 3
2002-03-28 | 59 | UX5901000004 | Close Coil | 1
2002-03-28 | 59 | UX59901000008 | UV TRIP COIL | 1
2002-03-28 | 59 | UX56201000004 | MICROSWITCH | 1
2002-03-28 | 68 | T56602069718 | SNUBBER / AC | 1

## LOW PRODUCERS
CLEAR SKY
BOTTOM FIVE PRODUCERS
WTG | kW Hours | Sys. Avl | Mach. Avl | Line Avl | Reason

## CURTAILMENTS
CLEAR SKY
CURTAILMENTS
Month: | March
WTG | Date off | Time off | Date on | Time on | Hours off | Name | CPS operator | Comments
68 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
76 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
78 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
79 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
80 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
81 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
82 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
83 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
84 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
86 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
87 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
88 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
89 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
90 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
91 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
92 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
93 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
96 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
100 | 2002-03-29 | 14:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
102 | 2002-03-29 | 14:30 | 2002-03-29 | 17:30 |  | Bryan | Gilbert
103 | 2002-03-29 | 14:30 | 2002-03-29 | 17:30 |  | Bryan | Gilbert
57 | 2002-03-29 | 15:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
56 | 2002-03-29 | 15:00 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
54 | 2002-03-29 | 15:15 | 2002-03-30 | 2400 |  | Bryan | Gilbert
46 | 2002-03-29 | 15:15 | 2002-03-30 | 2400 |  | Bryan | Gilbert
47 | 2002-03-29 | 15:15 | 2002-03-30 | 2400 |  | Bryan | Gilbert
51 | 2002-03-29 | 15:15 | 2002-03-30 | 2400 |  | Bryan | Gilbert
52 | 2002-03-29 | 15:15 | 2002-03-30 | 2400 |  | Bryan | Gilbert
104 | 2002-03-29 | 15:15 | 2002-03-29 | 16:40 |  | Bryan | Gilbert
105 | 2002-03-29 | 15:15 | 2002-03-29 | 16:20 |  | Bryan | Gilbert
106 | 2002-03-29 | 15:15 | 2002-03-29 | 16:20 |  | Bryan | Gilbert
60 | 2002-03-30 | 15:45 | 2002-03-30 | 20:00 |  | Jason | Johnny | CPS wanted 20MW on each line
61 | 2002-03-30 | 15:45 | 2002-03-30 | 20:00 |  | Jason | Johnny
62 | 2002-03-30 | 15:45 | 2002-03-30 | 20:00 |  | Jason | Johnny
36 | 2002-03-30 | 15:45 | 2002-03-30 | 20:00 |  | Jason | Johnny
37 | 2002-03-30 | 15:45 | 2002-03-30 | 20:00 |  | Jason | Johnny
38 | 2002-03-30 | 15:45 | 2002-03-30 | 20:00 |  | Jason | Johnny
39 | 2002-03-30 | 15:45 | 2002-03-30 | 20:00 |  | Jason | Johnny
40 | 2002-03-30 | 15:45 | 2002-03-30 | 20:00 |  | Jason | Johnny
86 | 2002-03-30 | 16:00 | 2002-03-30 | 20:00 |  | Jason | Johnny
87 | 2002-03-30 | 16:00 | 2002-03-30 | 20:00 |  | Jason | Johnny
88 | 2002-03-30 | 16:00 | 2002-03-30 | 20:00 |  | Jason | Johnny
89 | 2002-03-30 | 16:00 | 2002-03-30 | 20:00 |  | Jason | Johnny
90 | 2002-03-30 | 16:00 | 2002-03-30 | 20:00 |  | Jason | Johnny
91 | 2002-03-30 | 16:00 | 2002-03-30 | 20:00 |  | Jason | Johnny
92 | 2002-03-30 | 16:00 | 2002-03-30 | 20:00 |  | Jason | Johnny
93 | 2002-03-30 | 16:00 | 2002-03-30 | 20:00 |  | Jason | Johnny
96 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
100 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
66 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
36 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
37 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
38 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
39 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
40 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
68 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
69 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
31 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
32 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
33 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
34 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
26 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
27 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
28 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
29 | 2002-03-30 | 16:15 | 2002-03-30 | 20:00 |  | Jason | Johnny
18 | 2002-03-01 | 5:00 | 2002-03-01 | 7:15 |  | Tootie | Gilbert | To High Buss 1
17 | 2002-03-01 | 5:00 | 2002-03-01 | 7:15 |  | Tootie | Gilbert | To High Buss 1
15 | 2002-03-01 | 5:00 | 2002-03-01 | 7:15 |  | Tootie | Gilbert | To High Buss 1
14 | 2002-03-01 | 5:00 | 2002-03-01 | 7:15 |  | Tootie | Gilbert | To High Buss 1
79 | 2002-03-01 | 6:00 | 2002-03-01 | 9:16 |  | Tootie | Gilbert | To High Buss 2
21 | 2002-03-01 | 21:45 | 2002-03-01 | 22:00 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
22 | 2002-03-01 | 21:45 | 2002-03-01 | 22:00 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
23 | 2002-03-01 | 21:45 | 2002-03-01 | 22:00 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
24 | 2002-03-01 | 21:45 | 2002-03-01 | 22:00 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
19 | 2002-03-01 | 21:45 | 2002-03-01 | 22:00 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
20 | 2002-03-01 | 21:45 | 2002-03-01 | 22:00 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
1 | 2002-03-01 | 22:25 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
2 | 2002-03-01 | 22:25 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
3 | 2002-03-01 | 22:25 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
4 | 2002-03-01 | 22:25 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
5 | 2002-03-01 | 22:25 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
7 | 2002-03-01 | 22:30 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
18 | 2002-03-01 | 22:30 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
14 | 2002-03-01 | 22:50 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
27 | 2002-03-01 | 22:50 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
28 | 2002-03-01 | 22:50 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
31 | 2002-03-01 | 22:50 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
33 | 2002-03-01 | 22:50 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
35 | 2002-03-01 | 22:50 | 2002-03-01 | 23:25 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
37 | 2002-03-01 | 23:50 | 2002-03-02 | 8:50 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
39 | 2002-03-01 | 23:50 | 2002-03-02 | 8:51 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
41 | 2002-03-01 | 23:50 | 2002-03-02 | 16:50 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
43 | 2002-03-01 | 23:50 | 2002-03-02 | 16:50 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
46 | 2002-03-01 | 23:50 | 2002-03-02 | 16:50 |  | Tootie | Ben | Curtailed to 36 MW Buss 1
47 | 2002-03-01 | 23:50 | 2002-03-02 | 15:15 |  | Gabe | Dale | Curtailed to 36 MW Buss 1
49 | 2002-03-01 | 23:50 | 2002-03-02 | 15:15 |  | Gabe | Dale | Curtailed to 36 MW Buss 1
50 | 2002-03-01 | 23:50 | 2002-03-02 | 15:15 |  | Gabe | Dale | Curtailed to 36 MW Buss 1
51 | 2002-03-01 | 23:50 | 2002-03-02 | 15:15 |  | Gabe | Dale | Curtailed to 36 MW Buss 1
52 | 2002-03-01 | 23:50 | 2002-03-02 | 15:15 |  | Gabe | Dale | Curtailed to 36 MW Buss 1
53 | 2002-03-01 | 23:50 | 2002-03-02 | 14:45 |  | Gabe | Dale | Curtailed to 30 MW Buss 1&2
54 | 2002-03-01 | 23:50 | 2002-03-02 | 14:45 |  | Gabe | Dale | Curtailed to 30 MW Buss 1&2
55 | 2002-03-01 | 23:50 | 2002-03-02 | 14:45 |  | Gabe | Dale | Curtailed to 30 MW Buss 1&2
56 | 2002-03-01 | 23:50 | 2002-03-02 | 14:45 |  | Gabe | Dale | Curtailed to 30 MW Buss 1&2
57 | 2002-03-01 | 23:50 | 2002-03-02 | 14:45 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
58 | 2002-03-01 | 23:50 | 2002-03-02 | 14:45 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
59 | 2002-03-01 | 23:50 | 2002-03-02 | 14:45 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
19 | 2002-03-01 | 23:50 | 2002-03-02 | 1:58 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
27 | 2002-03-02 | 0:25 | 2002-03-02 | 2:10 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
28 | 2002-03-02 | 0:25 | 2002-03-02 | 8:50 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
30 | 2002-03-02 | 0:25 | 2002-03-02 | 8:48 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
31 | 2002-03-02 | 0:25 | 2002-03-02 | 8:48 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
60 | 2002-03-02 | 0:50 | 2002-03-02 | 8:50 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
62 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
63 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
647 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
65 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
66 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
68 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
69 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
70 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
71 | 2002-03-02 | 0:50 | 2002-03-02 | 8:52 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
72 | 2002-03-02 | 0:50 | 2002-03-02 | 1:55 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
73 | 2002-03-02 | 0:50 | 2002-03-02 | 1:55 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
74 | 2002-03-02 | 0:50 | 2002-03-02 | 1:55 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
75 | 2002-03-02 | 0:50 | 2002-03-02 | 1:40 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
76 | 2002-03-02 | 0:50 | 2002-03-02 | 1:40 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
77 | 2002-03-02 | 0:50 | 2002-03-02 | 1:40 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
78 | 2002-03-02 | 0:50 | 2002-03-02 | 1:40 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
79 | 2002-03-02 | 0:50 | 2002-03-02 | 1:30 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
80 | 2002-03-02 | 0:50 | 2002-03-02 | 1:30 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
81 | 2002-03-02 | 0:50 | 2002-03-02 | 13:30 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
24 | 2002-03-02 | 1:15 | 2002-03-02 | 2:10 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
85 | 2002-03-02 | 2:13 | 2002-03-02 | 13:30 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
86 | 2002-03-02 | 2:13 | 2002-03-02 | 13:30 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
87 | 2002-03-02 | 2:13 | 2002-03-02 | 13:25 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
88 | 2002-03-02 | 2:13 | 2002-03-02 | 13:25 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
108 | 2002-03-02 | 2:23 | 2002-03-02 | 6:35 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
100 | 2002-03-02 | 2:23 | 2002-03-02 | 6:40 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
102 | 2002-03-02 | 2:23 | 2002-03-02 | 6:40 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
116 | 2002-03-02 | 3:08 | 2002-03-02 | 11:58 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
115 | 2002-03-02 | 3:20 | 2002-03-02 | 11:58 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
120 | 2002-03-02 | 3:34 | 2002-03-02 | 4:40 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
27 | 2002-03-02 | 3:50 | 2002-03-02 | 8:45 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
24 | 2002-03-02 | 3:50 | 2002-03-02 | 8:47 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
23 | 2002-03-02 | 3:50 | 2002-03-02 | 8:47 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
118 | 2002-03-02 | 1:54 | 2002-03-02 | 4:40 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
105 | 2002-03-02 | 4:55 | 2002-03-02 | 6:35 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
104 | 2002-03-02 | 5:05 | 2002-03-02 | 6:35 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
44 | 2002-03-02 | 5:55 | 2002-03-02 | 16:50 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
28 | 2002-03-02 | 6:03 | 2002-03-02 | 8:47 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
27 | 2002-03-02 | 6:03 | 2002-03-02 | 16:50 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
122 | 2002-03-02 | 6:03 | 2002-03-02 | 6:31 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
22 | 2002-03-02 | 6:03 | 2002-03-02 | 8:10 |  | Tootie | Ben | Curtailed to 30 MW Buss 1&2
105 | 2002-03-02 | 7:45 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
104 | 2002-03-02 | 7:45 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
103 | 2002-03-02 | 7:45 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
72 | 2002-03-02 | 7:45 | 2002-03-02 | 11:56 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
73 | 2002-03-02 | 7:45 | 2002-03-02 | 11:56 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
74 | 2002-03-02 | 7:45 | 2002-03-02 | 11:56 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
75 | 2002-03-02 | 7:45 | 2002-03-02 | 11:56 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
77 | 2002-03-02 | 7:45 | 2002-03-02 | 11:56 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
76 | 2002-03-02 | 7:45 | 2002-03-02 | 11:56 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
78 | 2002-03-02 | 8:05 | 2002-03-02 | 11:56 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
1 | 2002-03-02 | 9:20 | 2002-03-02 | 11:56 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
2 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
3 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
4 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
5 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
7 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
23 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
14 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
15 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
18 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
102 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
100 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
96 | 2002-03-02 | 9:20 | 2002-03-02 | 16:50 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
93 | 2002-03-02 | 9:25 | 2002-03-02 | 14:45 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
92 | 2002-03-02 | 9:25 | 2002-03-02 | 14:45 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
90 | 2002-03-02 | 9:25 | 2002-03-02 | 14:45 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
89 | 2002-03-02 | 9:25 | 2002-03-02 | 14:45 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
88 | 2002-03-02 | 9:25 | 2002-03-02 | 13:30 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
87 | 2002-03-02 | 19:50 | 2002-03-02 | 13:30 |  | Kevin | Doyle | Curtailed to 30 MW Buss 1&2
1 | 2002-03-04 | 19:50 | 2002-03-05 | 2:00 |  | Justin | Buckley | Need Buss 1 to 40 & Buss2 to 35
2 | 2002-03-04 | 19:50 | 2002-03-05 | 2:00 |  | Justin | Buckley | Need Buss 1 to 40 & Buss2 to 35
3 | 2002-03-04 | 19:50 | 2002-03-05 | 2:30 |  | Justin | Buckley | Bring Buss 1 to 50 & Buss 2 to 45
4 | 2002-03-04 | 19:50 | 2002-03-05 | 2:30 |  | Justin | Buckley
5 | 2002-03-04 | 19:50 | 2002-03-05 | 11:45 |  | Justin | Buckley
7 | 2002-03-04 | 19:50 | 2002-03-05 | 11:45 |  | Justin | Buckley
8 | 2002-03-04 | 19:50 | 2002-03-05 | 11:45 |  | Justin | Buckley
9 | 2002-03-04 | 19:50 | 2002-03-05 | 11:45 |  | Justin | Buckley
14 | 2002-03-04 | 19:50 | 2002-03-05 | 11:45 |  | Justin | Buckley
15 | 2002-03-04 | 19:50 | 2002-03-05 | 11:45 |  | Justin | Buckley
17 | 2002-03-04 | 19:50 | 2002-03-05 | 11:45 |  | Justin | Buckley
109 | 2002-03-04 | 19:50 | 2002-03-05 | 2:30 |  | Justin | Buckley
114 | 2002-03-04 | 19:50 | 2002-03-05 | 11:46 |  | Justin | Buckley
115 | 2002-03-04 | 19:50 | 2002-03-05 | 2:30 |  | Justin | Buckley
116 | 2002-03-04 | 19:50 | 2002-03-05 | 2:00 |  | Justin | Buckley
117 | 2002-03-04 | 19:50 | 2002-03-05 | 2:00 |  | Justin | Buckley
118 | 2002-03-04 | 19:50 | 2002-03-05 | 2:00 |  | Justin | Buckley
119 | 2002-03-04 | 19:50 | 2002-03-05 | 2:00 |  | Justin | Buckley
120 | 2002-03-04 | 19:50 | 2002-03-05 | 2:30 |  | Justin | Buckley
121 | 2002-03-04 | 19:50 | 2002-03-05 | 2:00 |  | Justin | Buckley
122 | 2002-03-04 | 19:50 | 2002-03-05 | 2:00 |  | Justin | Buckley
18 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
19 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
20 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
21 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
23 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
24 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
96 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
100 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
102 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
103 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
104 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
105 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
106 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
107 | 2002-03-04 | 20:00 | 2002-03-05 | 10:00 |  | Justin | Buckley
27 | 2002-03-04 | 23:25 | 2002-03-05 | 10:00 |  | Justin | Buckley
28 | 2002-03-04 | 23:25 | 2002-03-05 | 10:00 |  | Justin | Buckley
29 | 2002-03-04 | 23:25 | 2002-03-05 | 10:00 |  | Justin | Buckley | Need Buss 1 to 40 & Buss2 to 35
91 | 2002-03-04 | 23:25 | 2002-03-05 | 10:00 |  | Justin | Buckley
92 | 2002-03-04 | 23:25 | 2002-03-05 | 10:00 |  | Justin | Buckley
93 | 2002-03-04 | 23:25 | 2002-03-05 | 10:00 |  | Justin | Buckley
30 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey | Need Buss 1 to 35
31 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey
33 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey
35 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey
37 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey
39 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey
41 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey
43 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey
46 | 2002-03-05 | 7:16 | 2002-03-05 | 10:00 |  | Jason | Joey
19 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey | Confirmed 32 MW Buss1 and 43 MW on Buss 2
20 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
21 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
22 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
23 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
24 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
91 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
96 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
100 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
102 | 2002-03-05 | 7:16 | 2002-03-05 | 12:45 |  | Jason | Joey
103 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey | Confirmed 30 Mw on both Busses
104 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey | Turning on more to achieve 30 Buss 1 and 45 on Buss 2
105 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
106 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
107 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
41 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
43 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
46 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
32 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
34 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey | Buss 1 to High
35 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
36 | 2002-03-05 | 7:16 | 2002-03-05 | 13:45 |  | Jason | Joey
37 | 2002-03-05 | 16:10 | 2002-03-05 | 13:45 |  | Jason | Joey | Buss 1 to High
38 | 2002-03-05 | 16:10 | 2002-03-07 | 6:50 |  | Jason | Buckley
39 | 2002-03-05 | 16:10 | 2002-03-07 | 6:50 |  | Jason | Buckley
40 | 2002-03-05 | 16:10 | 2002-03-07 | 6:50 |  | Jason | Buckley
41 | 2002-03-05 | 16:10 | 2002-03-07 | 6:50 |  | Jason | Buckley
42 | 2002-03-05 | 16:10 | 2002-03-07 | 6:50 |  | Jason | Buckley
43 | 2002-03-05 | 16:10 | 2002-03-07 | 6:50 |  | Jason | Buckley
45 | 2002-03-05 | 16:10 | 2002-03-07 | 6:50 |  | Jason | Buckley
46 | 2002-03-05 | 16:10 | 2002-03-07 | 6:50 |  | Jason | Buckley | Buss 1 to High
60 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley | Need Buss 1 & 2 at 35 MW
61 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
62 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
63 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
64 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
64 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
66 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
67 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
68 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
76 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
82 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
56 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
57 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
58 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
59 | 2002-03-05 | 18:25 | 2002-03-06 | 6:00 |  | Justin | Buckley
83 | 2002-03-05 | 19:45 | 2002-03-06 | 6:00 |  | Justin | Buckley | Need Buss 1 & 2 at 35 MW
84 | 2002-03-05 | 19:45 | 2002-03-06 | 6:00 |  | Justin | Buckley
21 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben | Curtail lifted
23 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
24 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
25 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
27 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
28 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
29 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
30 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
31 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
32 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
33 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
34 | 2002-03-05 | 19:45 | 2002-03-06 | 7:22 |  | Jason | Ben
35 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
36 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
37 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
38 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
39 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
40 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
41 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
42 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
45 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
46 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
61 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
62 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
63 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
64 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
65 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
66 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
67 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
68 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
69 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
70 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
71 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
72 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
73 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
74 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
75 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
76 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
77 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
78 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
79 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
80 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
81 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
103 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
104 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
105 | 2002-03-05 | 19:45 | 2002-03-06 | 7:20 |  | Jason | Ben
1 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley | Buss 1 at 35 MW
2 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
3 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
4 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley | Need Buss 1 at 35 MW
5 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
7 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
8 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
9 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
14 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
15 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
17 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
18 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
19 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
21 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
23 | 2002-03-06 | 20:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
24 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
25 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
27 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
28 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
29 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
30 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
31 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
32 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
33 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
34 | 2002-03-06 | 20:30 | 2002-03-07 | 24:00 |  | Justin | Buckley
24 | 2002-03-07 | 2:30 | 2002-03-07 | 6:50 |  | Justin | Buckley | Need Buss 1 at 35 MW
25 | 2002-03-07 | 2:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
26 | 2002-03-07 | 2:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
27 | 2002-03-07 | 2:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
29 | 2002-03-07 | 2:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
105 | 2002-03-07 | 4:30 | 2002-03-07 | 6:50 |  | Justin | Buckley | Need Buss 2 at 30 MW
106 | 2002-03-07 | 4:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
107 | 2002-03-07 | 4:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
108 | 2002-03-07 | 4:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
109 | 2002-03-07 | 4:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
113 | 2002-03-07 | 4:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
115 | 2002-03-07 | 4:30 | 2002-03-07 | 6:50 |  | Justin | Buckley
116 | 2002-03-07 | 4:30 | 2002-03-07 | 6:30 |  | Justin | Buckley | Need Buss 2 at 30 MW
117 | 2002-03-07 | 4:30 | 2002-03-07 | 6:30 |  | Justin | Buckley
118 | 2002-03-07 | 4:30 | 2002-03-07 | 6:30 |  | Justin | Buckley
119 | 2002-03-07 | 4:30 | 2002-03-07 | 6:30 |  | Justin | Buckley
120 | 2002-03-07 | 4:30 | 2002-03-07 | 6:30 |  | Justin | Buckley
121 | 2002-03-07 | 4:30 | 2002-03-07 | 6:30 |  | Justin | Buckley
122 | 2002-03-07 | 4:30 | 2002-03-07 | 6:30 |  | Justin | Buckley
60 | 2002-03-07 | 4:30 | 2002-03-07 | 6:30 |  | Justin | Buckley
61 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny | Need Buss 2 at 30 MW
62 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
63 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
64 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
65 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
66 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
68 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
69 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
70 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
71 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
72 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
73 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
74 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
75 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
77 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
76 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
78 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
79 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
80 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
81 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
82 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
83 | 2002-03-07 | 7:20 | 2002-03-07 | 11:10 |  | Jason | Johnny
68 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben | Curtailed to 30 MW on Line 2
69 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
71 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
72 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
73 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
74 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
75 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
76 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
77 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
78 | 2002-03-07 | 11:30 | 2002-03-07 | 13:00 |  | Matt | Ben
79 | 2002-03-07 | 12:26 | 2002-03-07 | 13:00 |  | Matt | Ben | Line 2 at 36, Set to 30
80 | 2002-03-07 | 12:26 | 2002-03-07 | 13:00 |  | Matt | Ben
81 | 2002-03-07 | 12:26 | 2002-03-07 | 13:00 |  | Matt | Ben
82 | 2002-03-07 | 12:26 | 2002-03-07 | 13:00 |  | Matt | Ben
83 | 2002-03-07 | 12:26 | 2002-03-07 | 13:00 |  | Matt | Ben | Curtail lifted
117 | 2002-03-07 | 17:00 | 2002-03-07 | 17:30 |  | Justin | Ben | Need Line 2 at 35 MW
118 | 2002-03-07 | 17:00 | 2002-03-07 | 17:30 |  | Justin | Ben
119 | 2002-03-07 | 17:00 | 2002-03-07 | 17:30 |  | Justin | Ben
121 | 2002-03-07 | 17:00 | 2002-03-07 | 17:30 |  | Justin | Ben
122 | 2002-03-07 | 17:00 | 2002-03-07 | 17:30 |  | Justin | Ben
115 | 2002-03-07 | 17:00 | 2002-03-07 | 17:30 |  | Justin | Ben
116 | 2002-03-07 | 17:00 | 2002-03-07 | 17:30 |  | Justin | Ben
31 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben | Need Buss 1 at 35 MW
32 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
33 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
34 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
35 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
36 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
37 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
38 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
39 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
40 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
42 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
43 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
44 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
45 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
46 | 2002-03-07 | 18:00 | 2002-03-07 | 19:30 |  | Justin | Ben
47 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben | Need Buss 1 at 35 MW
48 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
49 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
50 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
52 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
53 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
54 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
55 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
56 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
57 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
58 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
59 | 2002-03-07 | 18:00 | 2002-03-08 | 0:30 |  | Justin | Ben
102 | 2002-03-07 | 18:15 | 2002-03-08 | 0:30 |  | Justin | Ben | Need Buss 2 at 40 MW
103 | 2002-03-07 | 18:15 | 2002-03-08 | 0:30 |  | Justin | Ben
104 | 2002-03-07 | 18:15 | 2002-03-08 | 0:30 |  | Justin | Ben
106 | 2002-03-07 | 18:15 | 2002-03-08 | 0:30 |  | Justin | Ben
107 | 2002-03-07 | 18:15 | 2002-03-08 | 0:30 |  | Justin | Ben | Need Buss 1 & 2 at 10MW
8 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
9 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
14 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
15 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
17 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
18 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
19 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
20 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
21 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
23 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
24 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
25 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
27 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
28 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
29 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
30 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
68 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
76 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
77 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
78 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
79 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
80 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
81 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
82 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
83 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
84 | 2002-03-08 | 24:00 | 2002-03-08 | 7:30 |  | Justin | Ben
85 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
86 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
87 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
88 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
89 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
90 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
91 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
92 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
93 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
96 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
100 | 2002-03-08 | 24:00 | 2002-03-08 | 0:30 |  | Justin | Ben
114 | 2002-03-08 | 24:00 | 2002-03-08 | 7:30 |  | Justin | Ben
3 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey | Need Buss 1 & 2 at 10MW
4 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Justin | Ben
5 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
75 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
76 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
77 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
79 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
8 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
9 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
14 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
15 | 2002-03-08 | 6:50 | 2002-03-08 | 7:30 |  | Jason | Joey
114 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey | Cleared Bus I and II for 15 MW ea.
78 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
79 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
80 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
81 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
82 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
83 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
84 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
7 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
8 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
9 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
13 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
14 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
15 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
16 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
17 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
18 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
19 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
20 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
21 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
22 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
23 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
24 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
25 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
26 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
68 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
87 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
88 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
89 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
27 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
91 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
92 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
93 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
51 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
85 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
86 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
87 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
88 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
89 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
90 | 2002-03-08 | 6:50 | 2002-03-08 | 8:00 |  | Jason | Joey
92 | 2002-03-08 | 7:10 | 2002-03-08 | 8:10 |  | Jason | Joey | Bus I too low
28 | 2002-03-08 | 7:10 | 2002-03-08 | 8:05 |  | Jason | Joey
29 | 2002-03-08 | 7:10 | 2002-03-08 | 8:10 |  | Jason | Joey
83 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey | Bus II too high
84 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
91 | 2002-03-08 | 7:10 | 2002-03-08 | 8:00 |  | Jason | Joey
29 | 2002-03-08 | 7:10 | 2002-03-08 | 8:10 |  | Jason | Joey | Bus I and II too high (winds gusting)
83 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
84 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
91 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey | Bus I and II too high (winds gusting)
29 | 2002-03-08 | 7:10 | 2002-03-08 | 8:10 |  | Jason | Joey
28 | 2002-03-08 | 7:10 | 2002-03-08 | 8:10 |  | Jason | Joey
27 | 2002-03-08 | 7:10 | 2002-03-08 | 8:00 |  | Jason | Joey
25 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
26 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
24 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
23 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
81 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
80 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
79 | 2002-03-08 | 7:10 | 2002-03-08 | 7:30 |  | Jason | Joey
23 | 2002-03-08 | 7:10 | 2002-03-08 | 8:25 |  | Jason | Joey | Cleared for 25 MW each Bus
24 | 2002-03-08 | 7:10 | 2002-03-08 | 8:35 |  | Jason | Joey
25 | 2002-03-08 | 7:10 | 2002-03-08 | 8:35 |  | Jason | Joey
78 | 2002-03-08 | 7:10 | 2002-03-08 | 8:35 |  | Jason | Joey
80 | 2002-03-08 | 7:10 | 2002-03-08 | 8:35 |  | Jason | Joey
81 | 2002-03-08 | 7:10 | 2002-03-08 | 8:47 |  | Jason | Joey | Bus II too low
82 | 2002-03-08 | 7:10 | 2002-03-08 | 8:47 |  | Jason | Joey
83 | 2002-03-08 | 7:10 | 2002-03-08 | 8:47 |  | Jason | Joey
84 | 2002-03-08 | 7:10 | 2002-03-08 | 8:47 |  | Jason | Joey
85 | 2002-03-08 | 7:10 | 2002-03-08 | 8:47 |  | Jason | Joey
86 | 2002-03-08 | 7:10 | 2002-03-08 | 8:47 |  | Jason | Joey
87 | 2002-03-08 | 7:10 | 2002-03-08 | 8:47 |  | Jason | Joey
25 | 2002-03-08 | 7:55 | 2002-03-08 | 8:35 |  | Jason | Joey | Bus I too high
38 | 2002-03-08 | 7:30 | 2002-03-08 | 9:13 |  | Jason | Joey | Bus I and II too low
89 | 2002-03-08 | 8:00 | 2002-03-08 | 9:13 |  | Jason | Joey
25 | 2002-03-08 | 8:55 | 2002-03-08 | 9:13 |  | Jason | Joey
26 | 2002-03-08 | 7:30 | 2002-03-08 | 9:13 |  | Jason | Joey
88 | 2002-03-08 | 8:00 | 2002-03-08 | 9:13 |  | Jason | Joey
89 | 2002-03-08 | 8:00 | 2002-03-08 | 9:13 |  | Jason | Joey
90 | 2002-03-08 | 8:00 | 2002-03-08 | 9:13 |  | Jason | Joey
91 | 2002-03-08 | 3:30 | 2002-03-08 | 9:13 |  | Jason | Joey | Bus I and II too low
92 | 2002-03-08 | 8:00 | 2002-03-08 | 9:30 |  | Jason | Joey
118 | 2002-03-07 | 5:00 | 2002-03-08 | 9:30 |  | Jason | Joey
119 | 2002-03-07 | 5:00 | 2002-03-08 | 9:30 |  | Jason | Joey
96 | 2002-03-07 | 18:00 | 2002-03-08 | 9:30 |  | Jason | Joey
93 | 2002-03-08 | 8:00 | 2002-03-08 | 9:30 |  | Jason | Joey
121 | 2002-03-07 | 5:00 | 2002-03-08 | 9:30 |  | Jason | Joey
115 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Jason | Joey
116 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Jason | Joey
9 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Jason | Joey
47 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Jason | Joey
100 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Jason | Joey
102 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Jason | Joey
103 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Jason | Joey
72 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert | Bus II up to 35 MW
73 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
82 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
83 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
84 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
85 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
86 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
87 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
88 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
89 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
90 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
91 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
92 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
93 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
117 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
45 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert | Bus I up to 35 MW
26 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
27 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
28 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
29 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
30 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
32 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
116 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
33 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
34 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
114 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
35 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
36 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
46 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
37 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
38 | 2002-03-08 | 8:55 | 2002-03-08 | 9:30 |  | Tom | Gilbert
108 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert | Bus II down to 25 MW
122 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
119 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
118 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
117 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
116 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
109 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
106 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
105 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
92 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
93 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
96 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
100 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
102 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
103 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
104 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
82 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
83 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
84 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
85 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
86 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
87 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
88 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
89 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
90 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
91 | 2002-03-09 | 5:45 | 2002-03-09 | 9:20 |  | Bryan | Gilbert
80 | 2002-03-09 | 5:45 | 2002-03-09 | 6:45 |  | Bryan | Gilbert
79 | 2002-03-09 | 5:45 | 2002-03-09 | 6:45 |  | Bryan | Gilbert
71 | 2002-03-09 | 5:45 | 2002-03-09 | 6:45 |  | Kevin | Gilbert
72 | 2002-03-09 | 5:45 | 2002-03-09 | 6:45 |  | Kevin | Gilbert
73 | 2002-03-09 | 5:45 | 2002-03-09 | 6:45 |  | Kevin | Gilbert
96 | 2002-03-09 | 5:45 | 2002-03-09 | 8:35 |  | Tom | Gilbert | Bus II up to 35 MW
100 | 2002-03-09 | 5:45 | 2002-03-09 | 8:35 |  | Tom | Gilbert
102 | 2002-03-09 | 5:45 | 2002-03-09 | 8:35 |  | Tom | Gilbert
103 | 2002-03-09 | 5:45 | 2002-03-09 | 8:35 |  | Tom | Gilbert
104 | 2002-03-09 | 5:45 | 2002-03-09 | 8:35 |  | Tom | Gilbert
106 | 2002-03-09 | 5:45 | 2002-03-09 | 8:35 |  | Tom | Gilbert
114 | 2002-03-09 | 5:00 | 2002-03-09 | 8:35 |  | Bryan | Art | Down to 25 MW on Bus I until 7:15
24 | 2002-03-09 | 5:00 | 2002-03-09 | 8:35 |  | Bryan | Art
26 | 2002-03-09 | 5:00 | 2002-03-09 | 8:35 |  | Bryan | Art
27 | 2002-03-09 | 5:00 | 2002-03-09 | 8:35 |  | Bryan | Art
28 | 2002-03-09 | 5:00 | 2002-03-09 | 8:35 |  | Bryan | Art
29 | 2002-03-09 | 5:00 | 2002-03-09 | 8:35 |  | Bryan | Art
30 | 2002-03-09 | 5:00 | 2002-03-09 | 8:35 |  | Bryan | Art
31 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
32 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
34 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
35 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
36 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
37 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
38 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
39 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
40 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
41 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
42 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
43 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
45 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
47 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
49 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
50 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
51 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
52 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
53 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
54 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
55 | 2002-03-09 | 5:00 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
56 | 2002-03-09 | 5:00 | 2002-03-09 | 6:45 |  | Kevin | Gilbert
57 | 2002-03-09 | 5:00 | 2002-03-09 | 6:45 |  | Kevin | Gilbert
23 | 2002-03-09 | 5:30 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
21 | 2002-03-09 | 5:30 | 2002-03-09 | 8:50 |  | Kevin | Gilbert
17 | 2002-03-09 | 5:30 | 2002-03-09 | 8:35 |  | Tom | Gilbert | Bus I up to 35 MW
20 | 2002-03-09 | 5:30 | 2002-03-09 | 8:35 |  | Tom | Gilbert
21 | 2002-03-09 | 5:30 | 2002-03-09 | 8:35 |  | Tom | Gilbert
24 | 2002-03-09 | 5:30 | 2002-03-09 | 8:35 |  | Tom | Gilbert
47 | 2002-03-09 | 5:30 | 2002-03-09 | 8:35 |  | Tom | Gilbert
122 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art | 35 MW
118 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art | Release to full power 00:30
91 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
92 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
93 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
96 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
100 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
102 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
103 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
104 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
105 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
106 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
107 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
108 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
109 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
90 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
89 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
88 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
87 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
85 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
84 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
83 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
82 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
80 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
1 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art | Bus I to 35 MW until 23:30
2 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art | Release to full power 00:30
3 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
4 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
5 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
7 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
8 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
9 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
13 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
49 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
50 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
51 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
52 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
53 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
54 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
55 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
56 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
57 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
58 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
59 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
40 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
42 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
43 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
45 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
46 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
47 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
39 | 2002-03-10 | 20:00 | 2002-03-11 | 0:30 |  | Bryan | Art
38 | 2002-03-10 | 21:45 | 2002-03-11 | 0:30 |  | Bryan | Art
113 | 2002-03-10 | 22:00 | 2002-03-11 | 0:30 |  | Bryan | Art
114 | 2002-03-10 | 22:00 | 2002-03-11 | 0:30 |  | Bryan | Art
115 | 2002-03-10 | 22:00 | 2002-03-11 | 0:30 |  | Bryan | Art
14 | 2002-03-10 | 22:00 | 2002-03-11 | 0:30 |  | Bryan | Art
91 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
92 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
93 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
96 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
100 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
102 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
103 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
104 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
105 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
106 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
107 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
108 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
109 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
75 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
122 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
121 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
119 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
118 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
117 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
68 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
69 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
70 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
71 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
72 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
73 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
74 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
103 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
104 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
105 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
87 | 2002-03-11 | 24:45 | 2002-03-11 | 9:00 |  | Tootie | Gilbert
88 | 2002-03-11 | 24:45 | 2002-03-11 | 9:00 |  | Tootie | Gilbert
89 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
90 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
85 | 2002-03-11 | 24:45 | 2002-03-11 | 9:00 |  | Tootie | Gilbert
84 | 2002-03-11 | 24:45 | 2002-03-11 | 9:00 |  | Tootie | Gilbert
22 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
59 | 2002-03-11 | 24:45 | 2002-03-11 | 11:05 |  | Tootie | Gilbert
58 | 2002-03-11 | 24:45 | 2002-03-11 | 11:05 |  | Tootie | Gilbert
57 | 2002-03-11 | 24:45 | 2002-03-11 | 11:05 |  | Tootie | Gilbert
56 | 2002-03-11 | 24:45 | 2002-03-11 | 11:05 |  | Tootie | Gilbert
55 | 2002-03-11 | 24:45 | 2002-03-11 | 11:05 |  | Tootie | Gilbert
54 | 2002-03-11 | 24:45 | 2002-03-11 | 11:05 |  | Tootie | Gilbert
53 | 2002-03-11 | 24:45 | 2002-03-11 | 11:05 |  | Tootie | Gilbert
52 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
51 | 2002-03-11 | 24:45 | 2002-03-11 | 6:15 |  | Tootie | Gilbert
50 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
49 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
47 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
46 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
45 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
43 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
42 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
41 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
40 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
39 | 2002-03-11 | 24:45 | 2002-03-11 | 10:55 |  | Tootie | Gilbert
38 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
37 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
36 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
35 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
34 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
33 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
32 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
31 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
30 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
113 | 2002-03-11 | 24:45 | 2002-03-11 | 10:30 |  | Tootie | Gilbert
29 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
28 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
27 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
26 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
21 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
22 | 2002-03-11 | 24:45 | 2002-03-11 | 6:00 |  | Tootie | Gilbert
23 | 2002-03-11 | 24:45 | 2002-03-11 | 10:10 |  | Tootie | Gilbert
24 | 2002-03-11 | 24:45 | 2002-03-11 | 10:45 |  | Tootie | Gilbert
19 | 2002-03-11 | 24:45 | 2002-03-11 | 9:00 |  | Tootie | Gilbert
17 | 2002-03-11 | 24:45 | 2002-03-11 | 6:25 |  | Tootie | Gilbert
4 | 2002-03-11 | 12:42 | 2002-03-11 | 16:54 |  | Tootie | Gilbert
5 | 2002-03-11 | 12:42 | 2002-03-11 | 16:54 |  | Tootie | Gilbert
7 | 2002-03-11 | 12:53 | 2002-03-11 | 15:58 |  | Tootie | Gilbert
43 | 2002-03-11 | 12:53 | 2002-03-11 | 14:00 |  | Tootie | Gilbert
45 | 2002-03-11 | 12:53 | 2002-03-11 | 14:00 |  | Tootie | Gilbert
50 | 2002-03-11 | 12:53 | 2002-03-11 | 14:00 |  | Tootie | Gilbert
33 | 2002-03-11 | 12:53 | 2002-03-11 | 14:00 |  | Tootie | Gilbert
34 | 2002-03-11 | 12:53 | 2002-03-11 | 14:00 |  | Tootie | Gilbert
35 | 2002-03-11 | 12:53 | 2002-03-11 | 14:00 |  | Tootie | Gilbert
36 | 2002-03-11 | 12:53 | 2002-03-11 | 14:00 |  | Tootie | Gilbert
79 | 2002-03-11 | 12:53 | 2002-03-11 | 14:00 |  | Tootie | Gilbert
122 | 2002-03-11 | 12:15 | 2002-03-11 | 14:00 |  | Tootie | Gilbert | Bus I at 25 MW Bus II at 35 MW
119 | 2002-03-11 | 12:15 | 2002-03-11 | 15:59 |  | Tootie | Gilbert
118 | 2002-03-11 | 12:15 | 2002-03-11 | 15:59 |  | Tootie | Gilbert
117 | 2002-03-11 | 12:15 | 2002-03-11 | 15:59 |  | Tootie | Gilbert
113 | 2002-03-11 | 12:15 | 2002-03-11 | 13:45 |  | Tootie | Gilbert
109 | 2002-03-11 | 12:15 | 2002-03-11 | 17:00 |  | Tootie | Gilbert
108 | 2002-03-11 | 12:15 | 2002-03-11 | 17:00 |  | Tootie | Gilbert
107 | 2002-03-11 | 12:15 | 2002-03-11 | 13:45 |  | Tootie | Gilbert
106 | 2002-03-11 | 12:15 | 2002-03-11 | 17:00 |  | Tootie | Gilbert
105 | 2002-03-11 | 12:15 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
100 | 2002-03-11 | 12:15 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
102 | 2002-03-11 | 12:15 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
103 | 2002-03-11 | 12:15 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
104 | 2002-03-11 | 12:15 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
88 | 2002-03-11 | 12:20 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
89 | 2002-03-11 | 12:20 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
90 | 2002-03-11 | 12:20 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
92 | 2002-03-11 | 12:20 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
93 | 2002-03-11 | 12:20 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
96 | 2002-03-11 | 12:20 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
18 | 2002-03-11 | 12:30 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
8 | 2002-03-11 | 12:30 | 2002-03-12 | 15:58 |  | Tootie | Gilbert
9 | 2002-03-11 | 12:30 | 2002-03-12 | 15:58 |  | Tootie | Gilbert
15 | 2002-03-11 | 12:30 | 2002-03-12 | 14:00 |  | Tootie | Gilbert
17 | 2002-03-11 | 12:30 | 2002-03-12 | 14:00 |  | Tootie | Gilbert
19 | 2002-03-11 | 12:30 | 2002-03-12 | 14:00 |  | Tootie | Gilbert
20 | 2002-03-11 | 12:30 | 2002-03-12 | 14:00 |  | Tootie | Gilbert
21 | 2002-03-11 | 12:30 | 2002-03-12 | 14:00 |  | Tootie | Gilbert
22 | 2002-03-11 | 12:30 | 2002-03-11 | 13:50 |  | Tootie | Gilbert
23 | 2002-03-11 | 12:30 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
24 | 2002-03-11 | 12:35 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
25 | 2002-03-11 | 12:35 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
26 | 2002-03-11 | 12:35 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
1 | 2002-03-11 | 12:42 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
2 | 2002-03-11 | 12:42 | 2002-03-12 | 19:00 |  | Tootie | Gilbert
3 | 2002-03-11 | 12:42 | 2002-03-12 | 16:54 |  | Tootie | Gilbert
59 | 2002-03-12 | 14:29 | 2002-03-11 | 14:45 |  | Tootie | Buck | Curtailed to 31 MW on each bus
58 | 2002-03-12 | 14:29 | 2002-03-11 | 14:45 |  | Tootie | Buck
1 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
2 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben | Bus I at 31 MW
3 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
4 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
5 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
6 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
7 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
8 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
9 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
14 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
15 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
17 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
18 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
19 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
20 | 2002-03-12 | 18:00 | 2002-03-13 | 0:30 |  | Justin | Ben
60 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben | Bus II at 31 MW
61 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
62 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
63 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
64 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
65 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
66 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
68 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
69 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
70 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
71 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
72 | 2002-03-12 | 19:00 | 2002-03-13 | 0:30 |  | Justin | Ben
73 | 2002-03-12 | 21:00 | 2002-03-13 | 0:30 |  | Justin | Ben | Bus I and II at 31 MW each
74 | 2002-03-12 | 21:00 | 2002-03-13 | 0:30 |  | Justin | Ben
75 | 2002-03-12 | 21:00 | 2002-03-13 | 0:30 |  | Justin | Ben
76 | 2002-03-12 | 21:00 | 2002-03-13 | 0:30 |  | Justin | Ben
77 | 2002-03-12 | 21:00 | 2002-03-13 | 0:30 |  | Justin | Ben
87 | 2002-03-13 | 24:00 | 2002-03-13 | 0:30 |  | Justin | Ben | Bus II at 31 MW
88 | 2002-03-13 | 24:00 | 2002-03-13 | 0:30 |  | Justin | Ben
89 | 2002-03-13 | 24:00 | 2002-03-13 | 0:30 |  | Justin | Ben
90 | 2002-03-13 | 24:00 | 2002-03-13 | 0:30 |  | Justin | Ben
91 | 2002-03-13 | 24:00 | 2002-03-13 | 0:30 |  | Justin | Ben
92 | 2002-03-13 | 24:00 | 2002-03-13 | 0:30 |  | Justin | Ben
93 | 2002-03-13 | 24:00 | 2002-03-13 | 0:30 |  | Justin | Ben
1 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben | Need 30 MW's Line I and II
2 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
3 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
4 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
5 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
7 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
9 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
14 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
15 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
18 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
21 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
22 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
23 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
24 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
25 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
26 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
28 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
29 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
30 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
31 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
32 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
33 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
34 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
35 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
36 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
38 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
39 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
60 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
61 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
62 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
63 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
64 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
60 | 2002-03-13 | 6:00 | 2002-03-13 | 9:52 |  | Kevin | Art
61 | 2002-03-13 | 6:00 | 2002-03-13 | 9:52 |  | Kevin | Art
62 | 2002-03-13 | 6:00 | 2002-03-13 | 9:52 |  | Kevin | Art
63 | 2002-03-13 | 6:00 | 2002-03-13 | 9:52 |  | Kevin | Art
64 | 2002-03-13 | 6:00 | 2002-03-13 | 9:52 |  | Kevin | Art
65 | 2002-03-13 | 6:00 | 2002-03-13 | 9:52 |  | Kevin | Art
66 | 2002-03-13 | 6:00 | 2002-03-13 | 9:52 |  | Kevin | Art
68 | 2002-03-13 | 6:00 | 2002-03-13 | 9:52 |  | Kevin | Art
72 | 2002-03-13 | 6:00 | 2002-03-13 | 9:45 |  | Kevin | Art
73 | 2002-03-13 | 6:00 | 2002-03-13 | 9:45 |  | Kevin | Art
74 | 2002-03-13 | 6:00 | 2002-03-13 | 9:44 |  | Kevin | Art
75 | 2002-03-13 | 6:00 | 2002-03-13 | 9:44 |  | Kevin | Art
76 | 2002-03-13 | 6:00 | 2002-03-13 | 9:40 |  | Kevin | Art
77 | 2002-03-13 | 6:00 | 2002-03-13 | 9:34 |  | Kevin | Art
84 | 2002-03-13 | 6:00 | 2002-03-13 | 9:34 |  | Kevin | Art
85 | 2002-03-13 | 6:00 | 2002-03-13 | 9:34 |  | Kevin | Art
87 | 2002-03-13 | 6:00 | 2002-03-13 | 9:34 |  | Kevin | Art
88 | 2002-03-13 | 6:00 | 2002-03-13 | 9:34 |  | Kevin | Art
89 | 2002-03-13 | 6:00 | 2002-03-13 | 9:34 |  | Kevin | Art
90 | 2002-03-13 | 6:00 | 2002-03-13 | 9:34 |  | Kevin | Art
91 | 2002-03-13 | 6:00 | 2002-03-13 | 9:34 |  | Kevin | Art
92 | 2002-03-13 | 6:00 | 2002-03-13 | 7:47 |  | Kevin | Art
38 | 2002-03-13 | 6:30 | 2002-03-13 | 8:20 |  | Kevin | Art | Bus I too High
40 | 2002-03-13 | 6:30 | 2002-03-13 | 8:20 |  | Kevin | Art
15 | 2002-03-13 | 6:30 | 2002-03-13 | 8:20 |  | Kevin | Art
34 | 2002-03-13 | 6:30 | 2002-03-13 | 8:24 |  | Kevin | Art
33 | 2002-03-13 | 6:30 | 2002-03-13 | 8:24 |  | Kevin | Art
32 | 2002-03-13 | 6:30 | 2002-03-13 | 8:42 |  | Kevin | Art
31 | 2002-03-13 | 6:30 | 2002-03-13 | 9:52 |  | Kevin | Art
30 | 2002-03-13 | 6:30 | 2002-03-13 | 9:52 |  | Kevin | Art
29 | 2002-03-13 | 6:30 | 2002-03-13 | 9:52 |  | Kevin | Art
28 | 2002-03-13 | 6:30 | 2002-03-13 | 9:52 |  | Kevin | Art
70 | 2002-03-13 | 6:30 | 2002-03-13 | 9:52 |  | Kevin | Art
43 | 2002-03-13 | 6:30 | 2002-03-13 | 7:45 |  | Kevin | Art
100 | 2002-03-13 | 6:30 | 2002-03-13 | 6:35 |  | Kevin | Art
102 | 2002-03-13 | 6:30 | 2002-03-13 | 6:35 |  | Kevin | Art
108 | 2002-03-13 | 6:30 | 2002-03-13 | 7:44 |  | Kevin | Art
104 | 2002-03-13 | 6:30 | 2002-03-13 | 7:36 |  | Kevin | Art
106 | 2002-03-13 | 6:30 | 2002-03-13 | 7:36 |  | Kevin | Art
107 | 2002-03-13 | 6:30 | 2002-03-13 | 6:41 |  | Kevin | Art
122 | 2002-03-13 | 6:30 | 2002-03-13 | 9:23 |  | Kevin | Art
116 | 2002-03-13 | 8:10 | 2002-03-13 | 9:23 |  | Kevin | Art
113 | 2002-03-13 | 8:14 | 2002-03-13 | 9:23 |  | Kevin | Art
120 | 2002-03-13 | 8:14 | 2002-03-13 | 9:23 |  | Kevin | Art
65 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
66 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
68 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
70 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
72 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
73 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
74 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
75 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
76 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
77 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
84 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
85 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
87 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
88 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
89 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
90 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
92 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
93 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
100 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
102 | 2002-03-13 | 12:45 | 2002-03-13 | 14:00 |  | Justin | Ben
1 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben | Need Line I and II at 30 MW's
2 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
3 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
4 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
5 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
7 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
9 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
14 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
18 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
21 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
22 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
23 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
24 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
25 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
26 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
27 | 2002-03-13 | 6:00 | 2002-03-13 | 14:00 |  | Justin | Ben
1 | 2002-03-13 | 13:47 | 2002-03-13 | 14:15 |  | Tootie | Art
2 | 2002-03-13 | 13:47 | 2002-03-13 | 14:15 |  | Tootie | Art
3 | 2002-03-13 | 13:47 | 2002-03-13 | 14:15 |  | Tootie | Art
4 | 2002-03-13 | 13:47 | 2002-03-13 | 14:15 |  | Tootie | Art
5 | 2002-03-13 | 13:47 | 2002-03-13 | 14:15 |  | Tootie | Art
7 | 2002-03-13 | 13:50 | 2002-03-13 | 14:15 |  | Tootie | Art
8 | 2002-03-13 | 13:50 | 2002-03-13 | 15:00 |  | Tootie | Art
9 | 2002-03-13 | 13:50 | 2002-03-13 | 15:00 |  | Tootie | Art
14 | 2002-03-13 | 13:50 | 2002-03-13 | 15:00 |  | Tootie | Art
15 | 2002-03-13 | 13:50 | 2002-03-13 | 19:00 |  | Tootie | Art
17 | 2002-03-13 | 13:50 | 2002-03-13 | 19:00 |  | Tootie | Art
18 | 2002-03-13 | 13:50 | 2002-03-13 | 19:00 |  | Tootie | Art
19 | 2002-03-13 | 13:55 | 2002-03-13 | 19:00 |  | Tootie | Art
20 | 2002-03-13 | 13:55 | 2002-03-13 | 19:00 |  | Tootie | Art
21 | 2002-03-13 | 13:58 | 2002-03-13 | 19:00 |  | Tootie | Art
23 | 2002-03-13 | 13:58 | 2002-03-13 | 19:00 |  | Tootie | Art
24 | 2002-03-13 | 13:58 | 2002-03-13 | 19:00 |  | Tootie | Art
25 | 2002-03-13 | 13:58 | 2002-03-13 | 19:00 |  | Tootie | Art
60 | 2002-03-13 | 14:00 | 2002-03-13 | 14:23 |  | Tootie | Art
61 | 2002-03-13 | 14:00 | 2002-03-13 | 14:23 |  | Tootie | Art
63 | 2002-03-13 | 14:00 | 2002-03-13 | 19:00 |  | Tootie | Art
64 | 2002-03-13 | 14:00 | 2002-03-13 | 19:00 |  | Tootie | Art
65 | 2002-03-13 | 14:00 | 2002-03-13 | 19:00 |  | Tootie | Art
66 | 2002-03-13 | 14:00 | 2002-03-13 | 19:00 |  | Tootie | Art
68 | 2002-03-13 | 14:00 | 2002-03-13 | 19:00 |  | Tootie | Art
70 | 2002-03-13 | 14:03 | 2002-03-13 | 19:00 |  | Tootie | Art
71 | 2002-03-13 | 14:03 | 2002-03-13 | 19:00 |  | Tootie | Art
27 | 2002-03-13 | 14:05 | 2002-03-13 | 19:00 |  | Tootie | Art
28 | 2002-03-13 | 14:05 | 2002-03-13 | 19:00 |  | Tootie | Art
29 | 2002-03-13 | 14:05 | 2002-03-13 | 19:00 |  | Tootie | Art
31 | 2002-03-13 | 14:05 | 2002-03-13 | 19:00 |  | Tootie | Art
33 | 2002-03-13 | 14:05 | 2002-03-13 | 19:00 |  | Tootie | Art
90 | 2002-03-13 | 14:12 | 2002-03-13 | 15:30 |  | Tootie | Art
92 | 2002-03-13 | 14:12 | 2002-03-13 | 15:30 |  | Tootie | Art
93 | 2002-03-13 | 14:12 | 2002-03-13 | 15:30 |  | Tootie | Art
96 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
100 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
34 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
35 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
36 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
72 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
37 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
38 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
39 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
73 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
74 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
40 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
41 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
42 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
43 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
44 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
75 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
76 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
77 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
78 | 2002-03-13 | 14:45 | 2002-03-13 | 19:00 |  | Justin | Ben
18 | 2002-03-13 | 15:08 | 2002-03-13 | 19:00 |  | Justin | Ben
17 | 2002-03-13 | 15:17 | 2002-03-13 | 19:00 |  | Justin | Ben
102 | 2002-03-13 | 15:17 | 2002-03-13 | 19:00 |  | Justin | Ben
103 | 2002-03-13 | 15:17 | 2002-03-13 | 19:00 |  | Justin | Ben
28 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben | Needs line I at 40 and II at 35 MW
29 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
30 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
31 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
32 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
33 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
96 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
83 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
82 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
80 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
79 | 2002-03-13 | 21:00 | 2002-03-14 | 7:00 |  | Justin | Ben
63 | 2002-03-14 | 2:00 | 2002-03-14 | 7:00 |  | Justin | Ben | Needs Bus I at 35 and Bus II at 30 MW
65 | 2002-03-14 | 2:00 | 2002-03-14 | 7:00 |  | Justin | Ben
100 | 2002-03-14 | 2:00 | 2002-03-14 | 19:00 |  | Justin | Ben | Need Line I at 35 and II at 30 MW's
102 | 2002-03-14 | 2:00 | 2002-03-14 | 19:00 |  | Justin | Ben
34 | 2002-03-14 | 2:00 | 2002-03-14 | 19:00 |  | Justin | Ben
36 | 2002-03-14 | 2:00 | 2002-03-14 | 19:00 |  | Justin | Ben
37 | 2002-03-14 | 2:00 | 2002-03-14 | 19:00 |  | Justin | Ben
38 | 2002-03-14 | 2:00 | 2002-03-14 | 19:00 |  | Justin | Ben
49 | 2002-03-14 | 2:00 | 2002-03-14 | 19:00 |  | Justin | Ben
1 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger | 20 MW
2 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger | 4AM lifted curtailment
3 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
4 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
5 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
7 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
8 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
9 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
13 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
14 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
15 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
17 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
18 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
19 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
20 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
21 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
23 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
24 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
25 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
26 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
27 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
28 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
29 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
30 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
31 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
32 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
33 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
34 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
36 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
37 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
40 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
42 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
43 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
113 | 2002-03-16 | 23:00 | 2002-03-17 | 1:30 |  | Bryan | Roger
114 | 2002-03-16 | 23:00 | 2002-03-17 | 1:30 |  | Bryan | Roger
44 | 2002-03-16 | 23:00 | 2002-03-17 | 1:30 |  | Bryan | Roger
45 | 2002-03-16 | 23:00 | 2002-03-17 | 1:30 |  | Bryan | Roger
60 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger | 20 MW
61 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger | 4AM lifted curtailment
62 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
63 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
66 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
68 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
69 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
70 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
71 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
72 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
73 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
74 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
75 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
76 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
77 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
78 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
79 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
80 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
81 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
82 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
83 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
85 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
87 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
88 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
89 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
90 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
91 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
92 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
93 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
96 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
100 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
102 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
104 | 2002-03-16 | 23:00 | 2002-03-17 | 4:00 |  | Bryan | Roger
1 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben | Bus I and Bus II at 30 MW each
2 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben
3 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben
4 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben
5 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben
7 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben
8 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben
9 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben
13 | 2002-03-18 | 21:30 | 2002-03-19 | 6:35 |  | Justin | Ben
14 | 2002-03-18 | 21:30 | 2002-03-19 | 6:20 |  | Justin | Ben
17 | 2002-03-18 | 21:30 | 2002-03-19 | 6:20 |  | Justin | Ben
18 | 2002-03-18 | 21:30 | 2002-03-19 | 6:20 |  | Justin | Ben
19 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
20 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
21 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
23 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
24 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
25 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
26 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
27 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
28 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
29 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
30 | 2002-03-18 | 21:30 | 2002-03-19 | 1:30 |  | Justin | Ben
31 | 2002-03-18 | 21:30 | 2002-03-19 | 1:30 |  | Justin | Ben
32 | 2002-03-18 | 21:30 | 2002-03-19 | 1:30 |  | Justin | Ben
33 | 2002-03-18 | 21:30 | 2002-03-19 | 1:30 |  | Justin | Ben
34 | 2002-03-18 | 21:30 | 2002-03-19 | 1:30 |  | Justin | Ben
35 | 2002-03-18 | 21:30 | 2002-03-19 | 1:30 |  | Justin | Ben
36 | 2002-03-18 | 21:30 | 2002-03-19 | 2:30 |  | Justin | Ben
37 | 2002-03-18 | 21:30 | 2002-03-19 | 1:30 |  | Justin | Ben
60 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
62 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
63 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
66 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
68 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
72 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
73 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Ben
74 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Art | Bus I and Bus II at 30 MW each
75 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Art
77 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Art
78 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Art
79 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Art
80 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Art
82 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Art
83 | 2002-03-18 | 21:30 | 2002-03-19 | 6:00 |  | Justin | Art
96 | 2002-03-18 | 21:30 | 2002-03-19 | 2:30 |  | Justin | Art
102 | 2002-03-18 | 21:30 | 2002-03-19 | 2:30 |  | Justin | Art
103 | 2002-03-18 | 21:30 | 2002-03-19 | 2:30 |  | Justin | Art
104 | 2002-03-18 | 21:30 | 2002-03-19 | 2:30 |  | Justin | Art
105 | 2002-03-18 | 21:30 | 2002-03-19 | 2:30 |  | Justin | Art
106 | 2002-03-18 | 21:30 | 2002-03-19 | 2:30 |  | Justin | Art
107 | 2002-03-18 | 21:30 | 2002-03-19 | 2:30 |  | Justin | Art
19 | 2002-03-19 | 6:30 | 2002-03-19 | 14:30 |  | Justin | Ben | Bus I and Bus II at 30 MW each
20 | 2002-03-19 | 6:30 | 2002-03-19 | 14:30 |  | Justin | Ben
21 | 2002-03-19 | 6:30 | 2002-03-19 | 14:30 |  | Justin | Ben
23 | 2002-03-19 | 6:30 | 2002-03-19 | 14:30 |  | Justin | Ben
24 | 2002-03-19 | 6:30 | 2002-03-19 | 14:30 |  | Justin | Ben
25 | 2002-03-19 | 6:30 | 2002-03-19 | 14:30 |  | Justin | Ben
36 | 2002-03-19 | 12:48 | 2002-03-19 | 13:06 |  | Tootie | Gilbert | Curtailed to 31 MW each bus
37 | 2002-03-19 | 12:48 | 2002-03-19 | 13:06 |  | Tootie | Gilbert
38 | 2002-03-19 | 12:50 | 2002-03-19 | 13:06 |  | Tootie | Gilbert
39 | 2002-03-19 | 12:50 | 2002-03-19 | 13:06 |  | Tootie | Gilbert
40 | 2002-03-19 | 12:50 | 2002-03-19 | 13:06 |  | Tootie | Gilbert
25 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
32 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
33 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
34 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
35 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
36 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
37 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
38 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
39 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
40 | 2002-03-19 | 13:20 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
62 | 2002-03-19 | 13:24 | 2002-03-19 | 14:41 |  | Tootie | Gilbert
63 | 2002-03-19 | 13:24 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
42 | 2002-03-19 | 13:25 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
43 | 2002-03-19 | 13:25 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
44 | 2002-03-19 | 13:25 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
66 | 2002-03-19 | 13:26 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
68 | 2002-03-19 | 13:26 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
69 | 2002-03-19 | 13:26 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
70 | 2002-03-19 | 13:26 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
17 | 2002-03-19 | 13:27 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
18 | 2002-03-19 | 13:27 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
19 | 2002-03-19 | 13:27 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
20 | 2002-03-19 | 13:27 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
14 | 2002-03-19 | 13:27 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
71 | 2002-03-19 | 13:29 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
72 | 2002-03-19 | 13:29 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
73 | 2002-03-19 | 13:29 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
59 | 2002-03-19 | 13:29 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
57 | 2002-03-19 | 13:29 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
56 | 2002-03-19 | 13:29 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
58 | 2002-03-19 | 13:29 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
74 | 2002-03-19 | 13:33 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
75 | 2002-03-19 | 13:36 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
76 | 2002-03-19 | 13:36 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
77 | 2002-03-19 | 13:36 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
78 | 2002-03-19 | 13:36 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
79 | 2002-03-19 | 13:36 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
80 | 2002-03-19 | 13:36 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
82 | 2002-03-19 | 13:36 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
83 | 2002-03-19 | 13:36 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
85 | 2002-03-19 | 13:37 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
87 | 2002-03-19 | 13:37 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
89 | 2002-03-19 | 13:38 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
90 | 2002-03-19 | 13:38 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
91 | 2002-03-19 | 13:38 | 2002-03-20 | 15:25 |  | Tootie | Gilbert
9 | 2002-03-19 | 13:39 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
8 | 2002-03-19 | 13:39 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
7 | 2002-03-19 | 13:39 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
5 | 2002-03-19 | 13:39 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
4 | 2002-03-19 | 13:41 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
92 | 2002-03-19 | 13:41 | 2002-03-20 | 15:23 |  | Tootie | Gilbert
104 | 2002-03-19 | 14:22 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
96 | 2002-03-19 | 14:54 | 2002-03-20 | 19:30 |  | Tootie | Gilbert
46 | 2002-03-19 | 15:39 | 2002-03-19 | 19:30 |  | Tootie | Gilbert
59 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art | Bus I at 45 MW
58 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
57 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
56 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
55 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
54 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
53 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
52 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
51 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
50 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
49 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
47 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
46 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
45 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
44 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
43 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art | Bus I at 45 MW
42 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
41 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
40 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
39 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
38 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Art
37 | 2002-03-20 | 3:30 | 2002-03-20 | 5:00 |  | Justin | Roger
3 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger | Bus I and bus II at 31 MW
4 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
7 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
8 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
13 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
19 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
20 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
18 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
24 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
26 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
23 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
28 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
9 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
14 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
17 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
21 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
22 | 2002-03-20 | 7:00 | 2002-03-20 | 9:00 |  | Kevin | Roger
26 | 2002-03-20 | 8:37 | 2002-03-20 | 9:00 |  | Jason | Roger | Bus I too high
27 | 2002-03-20 | 8:37 | 2002-03-20 | 9:00 |  | Jason | Roger
28 | 2002-03-20 | 8:37 | 2002-03-20 | 9:00 |  | Jason | Roger
29 | 2002-03-20 | 8:37 | 2002-03-20 | 9:00 |  | Jason | Roger
30 | 2002-03-20 | 8:37 | 2002-03-20 | 10:00 |  | Jason | Roger
1 | 2002-03-20 | 8:40 | 2002-03-20 | 10:00 |  | Jason | Roger | Bus I too high
2 | 2002-03-20 | 8:40 | 2002-03-20 | 10:00 |  | Jason | Roger
18 | 2002-03-20 | 8:40 | 2002-03-20 | 9:48 |  | Jason | Roger | Bus I too low
2 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
3 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
4 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
5 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
7 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
9 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
13 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
14 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
17 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
18 | 2002-03-20 | 8:40 | 2002-03-20 | 10:10 |  | Jason | Roger
8 | 2002-03-20 | 8:40 | 2002-03-20 | 10:25 |  | Jason | Roger
19 | 2002-03-20 | 8:40 | 2002-03-20 | 10:30 |  | Jason | Roger
20 | 2002-03-20 | 8:40 | 2002-03-20 | 10:30 |  | Jason | Roger
21 | 2002-03-20 | 8:40 | 2002-03-20 | 10:30 |  | Jason | Roger
22 | 2002-03-20 | 8:40 | 2002-03-20 | 10:30 |  | Jason | Roger
25 | 2002-03-20 | 8:40 | 2002-03-20 | 10:30 |  | Jason | Roger
26 | 2002-03-20 | 8:40 | 2002-03-20 | 10:30 |  | Jason | Roger
27 | 2002-03-20 | 8:40 | 2002-03-20 | 10:30 |  | Jason | Roger
24 | 2002-03-20 | 8:40 | 2002-03-20 | 10:30 |  | Jason | Roger
115 | 2002-03-20 | 9:40 | 2002-03-20 | 10:30 |  | Jason | Roger | Bus I too high
115 | 2002-03-20 | 11:33 | 2002-03-20 | 11:45 |  | Jason | Roger | Bus I too low
23 | 2002-03-20 | 11:33 | 2002-03-20 | 12:58 |  | Jason | Roger | Repair finished
1 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger | Bus I and Bus II at 31 MW each
2 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
3 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
4 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
5 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
7 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
8 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
9 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
13 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
14 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
17 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
18 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
19 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
20 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger | Bus I and bus II at 31 MW each
21 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
23 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
24 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
25 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
26 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
27 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
28 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
29 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
77 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
78 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
82 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
83 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
84 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
85 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
86 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
87 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
91 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
96 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
102 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
103 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
104 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
105 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
106 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
107 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
109 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
120 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
113 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
114 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
115 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
116 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
118 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
119 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
121 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
122 | 2002-03-21 | 12:45 | 2002-03-21 | 17:58 |  | Justin | Roger
39 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
38 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
37 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
1 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
2 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
3 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
4 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
5 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
7 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
8 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
9 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
13 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
14 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
17 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
18 | 2002-03-22 | 20:00 | 2002-03-23 | 6:55 |  | Bryan | Dale
19 | 2002-03-22 | 20:00 | 2002-03-23 | 7:17 |  | Bryan | Dale
20 | 2002-03-22 | 20:00 | 2002-03-23 | 7:15 |  | Bryan | Dale
19 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
20 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
39 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
102 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale | 30 MW
103 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
104 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
105 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
106 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
96 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
93 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
92 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
90 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
91 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
89 | 2002-03-23 | 20:00 | 2002-03-24 | 7:15 |  | Bryan | Dale
62 | 2002-03-23 | 20:00 | 2002-03-24 | 7:09 |  | Bryan | Dale
63 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
64 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
65 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
68 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
69 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
70 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
71 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
72 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
73 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
74 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
75 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
76 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
77 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
78 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
109 | 2002-03-23 | 20:00 | 2002-03-24 | 7:12 |  | Bryan | Dale
1 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
2 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
3 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
4 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
5 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
7 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
8 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
9 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
13 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
14 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
17 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
18 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
40 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
41 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
42 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
43 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
44 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
45 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
46 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
47 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
49 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
50 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
51 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
52 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
55 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
56 | 2002-03-24 | 20:00 | 2002-03-24 | 20:30 |  | Bryan | Dale
57 | 2002-03-24 | 20:00 | 2002-03-24 | 22:00 |  | Bryan | Dale
58 | 2002-03-24 | 20:00 | 2002-03-24 | 22:00 |  | Bryan | Dale
59 | 2002-03-24 | 20:00 | 2002-03-24 | 22:00 |  | Bryan | Dale
43 | 2002-03-27 | 17:15 | 2002-03-27 | 18:00 |  | Justin | Duvall
104 | 2002-03-27 | 17:15 | 2002-03-27 | 18:00 |  | Justin | Duvall
44 | 2002-03-27 | 17:15 | 2002-03-27 | 18:00 |  | Justin | Duvall
1 | 2002-03-27 | 17:15 | 2002-03-27 | 19:00 |  | Justin | Duvall
2 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
3 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
7 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
8 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
9 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
13 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
14 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
17 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
18 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
19 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
20 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
21 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
22 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
23 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
24 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
25 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
26 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
27 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
28 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
29 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
30 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
31 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
32 | 2002-03-27 | 18:30 | 2002-03-27 | 19:00 |  | Justin | Duvall
1 | 2002-03-27 | 0:45 | 2002-03-27 | 8:30 |  | Justin | Johnny | Bus I and bus II at 25 MW each
2 | 2002-03-27 | 0:45 | 2002-03-27 | 9:00 |  | Kenny | Johnny
3 | 2002-03-27 | 0:45 | 2002-03-27 | 9:00 |  | Kenny | Johnny
7 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
8 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
9 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
13 | 2002-03-27 | 0:45 | 2002-03-27 | 11:00 |  | Kenny | Johnny
14 | 2002-03-27 | 0:45 | 2002-03-27 | 11:00 |  | Kenny | Johnny
17 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
18 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
19 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
20 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
21 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
22 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
23 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
24 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
25 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
26 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
27 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
28 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
29 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
30 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
31 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
32 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
33 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
34 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
36 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
37 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
38 | 2002-03-27 | 0:45 | 2002-03-27 | 18:00 |  | Justin | Johnny
60 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
62 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
64 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
65 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
66 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
68 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
69 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
70 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
71 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny | Bus I and bus II at 25 MW each
72 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
73 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
74 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
75 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
76 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
77 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
78 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
79 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
80 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
82 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
83 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
84 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
85 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
86 | 2002-03-27 | 0:45 | 2002-03-28 | 1:00 |  | Justin | Johnny
87 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
88 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
89 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
90 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
91 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
92 | 2002-03-27 | 0:45 | 2002-03-27 | 12:00 |  | Kenny | Johnny
39 | 2002-03-27 | 1:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
40 | 2002-03-27 | 1:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
41 | 2002-03-27 | 1:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
93 | 2002-03-27 | 1:30 | 2002-03-27 | 12:00 |  | Kenny | Johnny
96 | 2002-03-27 | 1:30 | 2002-03-27 | 12:00 |  | Kenny | Johnny
100 | 2002-03-27 | 1:30 | 2002-03-27 | 9:20 |  | Kenny | Johnny
42 | 2002-03-27 | 9:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
87 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
88 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
89 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
90 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
91 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
7 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
8 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
9 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
13 | 2002-03-27 | 12:30 | 2002-03-27 | 18:00 |  | Kenny | Johnny
14 | 2002-03-27 | 12:30 | 2002-03-28 | 1:00 |  | Kenny | Johnny
92 | 2002-03-27 | 14:00 | 2002-03-28 | 1:00 |  | Kenny | Johnny
93 | 2002-03-27 | 14:00 | 2002-03-28 | 1:00 |  | Kenny | Johnny
96 | 2002-03-27 | 14:00 | 2002-03-28 | 1:00 |  | Kenny | Johnny
3 | 2002-03-27 | 14:00 | 2002-03-28 | 1:00 |  | Kenny | Johnny
102 | 2002-03-27 | 14:45 | 2002-03-28 | 1:00 |  | Kenny | Johnny
103 | 2002-03-27 | 14:45 | 2002-03-28 | 1:00 |  | Kenny | Johnny
1 | 2002-03-27 | 15:45 | 2002-03-28 | 1:00 |  | Kenny | Johnny
2 | 2002-03-27 | 15:45 | 2002-03-28 | 1:00 |  | Kenny | Johnny
43 | 2002-03-27 | 17:15 | 2002-03-27 | 18:00 |  | Justin | Duvall
104 | 2002-03-27 | 17:15 | 2002-03-27 | 18:00 |  | Justin | Duvall
44 | 2002-03-27 | 17:15 | 2002-03-27 | 18:00 |  | Justin | Duvall
122 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall | Bus I and bus II at 30 MW each
121 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
119 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
118 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
117 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
113 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
120 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
109 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
108 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
107 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
106 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
105 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
103 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
102 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
100 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
96 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
93 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
92 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
91 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
90 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
89 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
88 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
87 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
86 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
85 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
84 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall | Bus I and bus II at 30 MW each
83 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
82 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
81 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
44 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
43 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
42 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
41 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
40 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
39 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
38 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
37 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
36 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
34 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
33 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
32 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
31 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
30 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
29 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
28 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
27 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
26 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
25 | 2002-03-28 | 1:30 | 2002-03-28 | 4:00 |  | Justin | Duvall
122 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall | Bus I and bus II at 25 MW each
121 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
119 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
118 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
113 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
120 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
108 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
107 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
106 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
104 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
103 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
102 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
100 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
1 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
2 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
3 | 2002-03-28 | 7:00 | 2002-03-28 | 8:00 |  | Kenny | Duvall
3 | 2002-03-29 | 14:03 | 2002-03-29 | 16:17 |  | Tootie | Steve | Curtailed to 28MW Bus I and 26MW Bus II
4 | 2002-03-29 | 14:03 | 2002-03-29 | 16:17 |  | Tootie | Steve
5 | 2002-03-29 | 14:03 | 2002-03-29 | 16:17 |  | Tootie | Steve
7 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert | Curtailment lifted
8 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
9 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
13 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
14 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
15 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
16 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
17 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
18 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
19 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
20 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
21 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
22 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
24 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
25 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
26 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
27 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
28 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
29 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
30 | 2002-03-29 | 14:03 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
31 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
32 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
33 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
34 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
36 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
58 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
59 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
60 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
61 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
62 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
63 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
64 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
65 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
66 | 2002-03-29 | 14:04 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
68 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
76 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
78 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
79 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
80 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
81 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
82 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
83 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
84 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
86 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
87 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
88 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
89 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
90 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
91 | 2002-03-29 | 14:06 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
92 | 2002-03-29 | 14:14 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
93 | 2002-03-29 | 14:14 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
96 | 2002-03-29 | 14:14 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
100 | 2002-03-29 | 14:14 | 2002-03-30 | 24:00 |  | Bryan | Gilbert
102 | 2002-03-29 | 14:14 | 2002-03-29 | 17:35 |  | Bryan | Gilbert
103 | 2002-03-29 | 14:14 | 2002-03-29 | 17:35 |  | Bryan | Gilbert
57 | 2002-03-29 | 14:33 | 2002-03-30 | 0:00 |  | Bryan | Gilbert
56 | 2002-03-29 | 14:33 | 2002-03-30 | 0:00 |  | Bryan | Gilbert
54 | 2002-03-29 | 14:33 | 2002-03-30 | 0:00 |  | Bryan | Gilbert
46 | 2002-03-29 | 15:00 | 2002-03-30 | 0:00 |  | Bryan | Gilbert
42 | 2002-03-29 | 15:00 | 2002-03-30 | 0:00 |  | Bryan | Gilbert
51 | 2002-03-29 | 15:14 | 2002-03-30 | 0:00 |  | Bryan | Gilbert
52 | 2002-03-29 | 15:14 | 2002-03-30 | 0:00 |  | Bryan | Gilbert
104 | 2002-03-29 | 15:15 | 2002-03-29 | 16:40 |  | Bryan | Gilbert
105 | 2002-03-29 | 15:15 | 2002-03-29 | 16:19 |  | Bryan | Gilbert
106 | 2002-03-29 | 15:15 | 2002-03-29 | 16:19 |  | Bryan | Gilbert
42 | 2002-03-30 | 11:39 | 2002-03-30 | 16:19 |  | Bryan | Buck | Bus I to 10 MW and Bus II to 10 MW
32 | 2002-03-30 | 11:39 | 2002-03-30 | 16:19 |  | Bryan | Buck
25 | 2002-03-30 | 11:39 | 2002-03-30 | 16:19 |  | Bryan | Buck
24 | 2002-03-30 | 11:39 | 2002-03-30 | 16:19 |  | Bryan | Buck
22 | 2002-03-30 | 11:39 | 2002-03-30 | 16:19 |  | Bryan | Buck
21 | 2002-03-30 | 11:39 | 2002-03-30 | 16:19 |  | Bryan | Buck
60 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck | Bus II at 10 MW
62 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
63 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
64 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
65 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
66 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
68 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
73 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
74 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
75 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
76 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
77 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
78 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
79 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
80 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
81 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
82 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
83 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
84 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
85 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
96 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
100 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
102 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
103 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
104 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
106 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
107 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
113 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
116 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
120 | 2002-03-30 | 4:30 | 2002-03-30 | 16:19 |  | Bryan | Buck
20 | 2002-03-30 | 11:45 | 2002-03-30 | 16:19 |  | Jason | Buck | Bus I and Bus II at10MW
19 | 2002-03-30 | 11:45 | 2002-03-30 | 16:19 |  | Jason | Buck
18 | 2002-03-30 | 11:45 | 2002-03-30 | 16:19 |  | Jason | Buck
17 | 2002-03-30 | 11:45 | 2002-03-30 | 16:19 |  | Jason | Buck
115 | 2002-03-30 | 11:45 | 2002-03-30 | 16:19 |  | Jason | Buck
109 | 2002-03-30 | 11:45 | 2002-03-30 | 16:19 |  | Jason | Buck
117 | 2002-03-30 | 14:46 | 2002-03-30 | 16:19 |  | Jason | Buck
118 | 2002-03-30 | 14:46 | 2002-03-30 | 16:19 |  | Jason | Buck
119 | 2002-03-30 | 14:46 | 2002-03-30 | 16:19 |  | Jason | Buck
120 | 2002-03-30 | 14:46 | 2002-03-30 | 16:19 |  | Jason | Buck
114 | 2002-03-30 | 14:46 | 2002-03-30 | 16:19 |  | Jason | Buck
60 | 2002-03-30 | 14:46 | 2002-03-30 | 15:00 |  | Jason | Buck
61 | 2002-03-30 | 14:46 | 2002-03-30 | 15:00 |  | Jason | Buck
62 | 2002-03-30 | 14:46 | 2002-03-30 | 15:00 |  | Jason | Buck
66 | 2002-03-30 | 14:46 | 2002-03-30 | 15:00 |  | Jason | Buck
68 | 2002-03-30 | 14:46 | 2002-03-30 | 15:00 |  | Jason | Buck
73 | 2002-03-30 | 14:46 | 2002-03-30 | 15:00 |  | Jason | Buck
30 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
31 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
32 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
33 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
34 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
35 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
36 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
37 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
38 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
39 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
40 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
41 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
42 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
43 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
44 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
45 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
46 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
47 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
49 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
50 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
51 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
52 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
53 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
54 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
55 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
56 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
57 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
58 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
59 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
60 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
61 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
62 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
63 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
64 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
65 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
66 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
68 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
69 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
70 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
86 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
87 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
88 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
89 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
90 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
91 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny
92 | 2002-03-30 | 15:00 | 2002-03-30 | 20:00 |  | Bryan | Johnny

## PROJECTS
Clear Sky
SPECIAL PROJECTS
1. Completed installation of power supplies for Omnitron switches.
2. Pad #67 was inspected.
3. The burned fiber optic cables running into pad #67 were replaced.
4. The 575VAC cables running from the PMT to the controller on #67 were replaced.
5. Progress continued on the punch list.
6. Completed SEG training for maintenance and troubleshooting.
7. Started 1.5 turbine specific training.