## Weekly_US
 | time axis 2001-04-05 to 2002-04-04
EW 1.5mW Series |  | No. of | Hub | Tower | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD | MTD
Project Name | Location | Turbines | Height -m | Type | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability | Availability
Fenner | NY | 20 | 65 | Tube | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | 95.08% | 74.9% | 86.95% | 89.88% | 92.87% | 97.19% | 91.55% | 93.4% | 93.2% | 88.1%
Indian Mesa I | TX | N/A3 |  |  | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2
Indian Mesa II | TX | 90 | 65 | Tube | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A2 | N/A2 | N/A2 | N/A2 | 89.04% | 85.36% | 88.75% | 90.39% | 93.08%
Klondike | OR | 16 | 65 | Tube | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | N/A1 | N/A1 | N/A1 | N/A1 | N/A2 | N/A2 | 93.84% | 94.79% | 94.81% | 97.38% | 97.8% | 96.86% | 95.62% | 96.87%
Mill Run | PA | 10 | 65 | Tube | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | 82.2% | 89.4% | 93.99% | 94.42% | 95.18% | 91.7% | 93.28% | 94.35% | 96.05% | 90.45% | 93.89% | 93.28% | 93.93% | 98.9%
Montfort8 | WI | 20 | 65 | Tube | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | 0.89 | NA1 | NA1 | NA1 | 0.897 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | 0.9862 | 0.9778 | 0.9795 | 98.08% | 97.2% | 95.53% | 95.58% | 99.5% | 95.73% | 96.49% | 92% | 97.3% | 98.77% | 97.47% | 90.6% | 85.04% | N/A2 | N/A2 | 93.84% | 94.21% | 94.96% | 98% | 98.39% | 98.76% | 100% | 97.16% | 96.84% | 97.61% | 98% | 99.76%
Somerset | DE | 6 | 65 | Tube | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | N/A2 | N/A2 | N/A2 | N/A2 | 96.5% | 89.94% | 90.72% | 91.89% | 93.54% | 94.6% | 95.22% | 96.55% | 97.36% | 93.99% | 94.21% | 95.85% | 95.84% | 99.13%
Trent Mesa | TX | 100 | 65 | Tube | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | NA1 | N/A2 | N/A2 | N/A2 | N/A2 | 96.4% | 94.39% | 93.3% | 90.89% | 87.41% | 76.9% | 84.3% | 85.2% | 87.8% | 81% | 75% | 81.7% | N/A2 | 97.44%
Fleet Wide EW 1.5 |  | 262 | Weighted Average |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9862 | 0.978 | 0.9795 | 98.08% | 97.2% | 95.53% | 95.58% | 99.5% | 95.7% | 96.5% | 92% | 97.3% | 98.77% | 97.47% | 90.6% | 85.04% | 95.18% | 93.73% | 93.32% | 91.68% | 90.1% | 80.98% | 88.04% | 89.14% | 91.27% | 87.89% | 84.04% | 87.92% | 92.61% | 95.47%

## Monthly_US
Mechanical
| EW 1.5mW Series |  | No. of | Hub | Tower
| Project Name | Location | Turbines | Height -m | Type | 2001-04-01 | 2001-05-01 | 2001-06-01 | 2001-07-01 | 2001-08-29 | 2001-09-28 | 2001-10-28 | 2001-11-28 | 2001-12-28 | 2002-01-28 | 2002-02-28 | 2002-03-28
| Fenner | NY | 20 | 65 | Tube | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 95.08% | 86.15% | 93.84%
| Clear Sky | TX | 107 | 65 | Tube | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 88.39%
| Klondike | OR | 16 | 65 | Tube | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 94.48% | 96.91%
| Mill Run | PA | 10 | 65 | Tube | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 91.04% | 93.85% | 92.89%
| Montfort8 | WI | 20 | 65 | Tube | #DIV/0! | #DIV/0! | 89% | 89.7% | #DIV/0! | 98.12% | 96.6% | 96.2% | 92.97% | 94.34% | 98.79% | 97.4%
| Somerset | DE | 6 | 65 | Tube | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 92.52% | 95.93% | 94.97%
| Trent Mesa | TX | 100 | 65 | Tube | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 92.48% | 83.55% | 79.23%
| Fleet Wide EW 1.5 |  | 279 | Weighted Average |  | #DIV/0! | #DIV/0! | 89% | 89.7% | #DIV/0! | 98.12% | #DIV/0! | #DIV/0! | #DIV/0! | 92.96% | 87.67% | 86.93%
Contractual
| EW 1.5mW Series |  | No. of | Hub | Tower
| Project Name | Location | Turbines | Height -m | Type | 2001-04-01 | 2001-05-01 | 2001-06-01 | 2001-07-01 | 2001-08-29 | 2001-09-28 | 2001-10-28 | 2001-11-28 | 2001-12-28 | 2002-01-28 | 2002-02-28 | 2002-03-28
| Fenner | NY | 20 | 65 | Tube
| Clear Sky | TX | 107 | 65 | Tube | 2002-01-28: 81.1%; 2002-02-28: 85.1%
| Klondike | OR | 16 | 65 | Tube | 2002-02-28: 94%
| Mill Run | PA | 10 | 65 | Tube | 2001-10-28: 90.1%; 2001-11-28: 87.3%; 2001-12-28: 85.9%; 2002-01-28: 93.3%; 2002-02-28: 96%
| Montfort8 | WI | 20 | 65 | Tube | 90.2% | 89% | 89.7% | 89.4% | 93.8% | 97.8% | 94.6% | 91.9% | 87.9% | 93.6% | 98.5%
| Somerset | DE | 6 | 65 | Tube | 2001-10-28: 59.2%; 2001-11-28: 92.6%; 2001-12-28: 94.5%; 2002-01-28: 94%; 2002-02-28: 97.4%
| Trent Mesa | TX | 100 | 65 | Tube | 2001-12-28: 66.3%; 2002-01-28: 69.8%; 2002-02-28: 94.3%
| Fleet Wide EW 1.5 |  | 279 | Weighted Average |  | 90.2% | 89% | 89.7% | 89.4% | 93.8% | 97.8% | 87.45% | 90.74% | 72.16% | 78.3% | 90.94% | 0%
Mechanical | EW 1.5mW Series |  | No. of | Hub | Tower
| Project Name | Location | Turbines | Height -m | Type | 2001-04-01 | 2001-05-01 | 2001-06-01 | 2001-07-01 | 2001-08-29 | 2001-09-28 | 2001-10-28 | 2001-11-28 | 2001-12-28 | 2002-01-28 | 2002-02-28 | 2002-03-28
| Fenner | NY | 20 | 65 | Tube | 2002-01-28: 95.08%; 2002-02-28: 86.15%; 2002-03-28: 93.84% | (93% x 6 mo), then 97%+
| Clear Sky | TX | 107 | 65 | Tube | 2002-03-28: 88.39% | 65%, 75%, 85%
| Klondike | OR | 16 | 65 | Tube | 2002-02-28: 94.48%; 2002-03-28: 96.91% | 60%, 70%, 80%
| Mill Run | PA | 10 | 65 | Tube | 2002-01-28: 91.04%; 2002-02-28: 93.85%; 2002-03-28: 92.89% | (93% x 6 mo), then 97%+
| Montfort8 | WI | 20 | 65 | Tube |  |  | 89% | 89.7% |  | 98.12% | 96.6% | 96.2% | 92.97% | 94.34% | 98.79% | 97.4% | None
| Somerset | DE | 6 | 65 | Tube | 2002-01-28: 92.52%; 2002-02-28: 95.93%; 2002-03-28: 94.97% | (93% x 6 mo), then 97%+
| Trent Mesa | TX | 100 | 65 | Tube | 2002-01-28: 92.48%; 2002-02-28: 83.55%; 2002-03-28: 79.23% | 65%, 75%, 85%
| Fleet Wide EW 1.5 |  | 279 | Weighted Average
[8 empty] | = Construction |  |  | = Ramp-Up |  | = 93%, then 97%
Contractual | EW 1.5mW Series |  | No. of | Hub | Tower
| Project Name | Location | Turbines | Height -m | Type | 2001-04-01 | 2001-05-01 | 2001-06-01 | 2001-07-01 | 2001-08-29 | 2001-09-28 | 2001-10-28 | 2001-11-28 | 2001-12-28 | 2002-01-28 | 2002-02-28 | 2002-03-28
| Fenner | NY | 20 | 65 | Tube | bar: 2002-01-28 to 2002-03-28
| Clear Sky | TX | 107 | 65 | Tube | 2002-01-28: 81.1%; 2002-02-28: 85.1%
| Klondike | OR | 16 | 65 | Tube | 2002-02-28: 94%
| Mill Run | PA | 10 | 65 | Tube | 2001-10-28: 90.1%; 2001-11-28: 87.3%; 2001-12-28: 85.9%; 2002-01-28: 93.3%; 2002-02-28: 96%
| Montfort8 | WI | 20 | 65 | Tube | 90.2% | 89% | 89.7% | 89.4% | 93.8% | 97.8% | 94.6% | 91.9% | 87.9% | 93.6% | 98.5%
| Somerset | DE | 6 | 65 | Tube | 2001-10-28: 59.2%; 2001-11-28: 92.6%; 2001-12-28: 94.5%; 2002-01-28: 94%; 2002-02-28: 97.4%
| Trent Mesa | TX | 100 | 65 | Tube | 2001-12-28: 66.3%; 2002-01-28: 69.8%; 2002-02-28: 94.3%
| Fleet Wide EW 1.5 |  | 279 | Weighted Average |  | 90.2% | 89% | 89.7% | 89.4% | 93.8% | 97.8% | 87.45% | 90.74% | 72.16% | 78.3% | 90.94% | 0%
[8 empty] | = Construction |  |  | = Ramp-Up |  | = 93%, then 97%

## Summary
Mechanical | EW 1.5mW Series |  | No. of | Hub | Tower | [12 empty] | Ramp-Up Condition | Warranted Availability
| Project Name | Location | Turbines | Height -m | Type | 2001-04-01 | 2001-05-01 | 2001-06-01 | 2001-07-01 | 2001-08-29 | 2001-09-28 | 2001-10-28 | 2001-11-28 | 2001-12-28 | 2002-01-28 | 2002-02-28 | 2002-03-28
| Fenner | NY | 20 | 65 | Tube | 2002-01-28: 95.08%; 2002-02-28: 86.15%; 2002-03-28: 93.84% | (93% x 6 mo), then 97%+ | 97%
| Clear Sky | TX | 107 | 65 | Tube | 2002-03-28: 88.39% | 65%, 75%, 85% | 95%
| Klondike | OR | 16 | 65 | Tube | 2002-02-28: 94.48%; 2002-03-28: 96.91% | 60%, 70%, 80% | 95%
| Mill Run | PA | 10 | 65 | Tube | 2002-01-28: 91.04%; 2002-02-28: 93.85%; 2002-03-28: 92.89% | (93% x 6 mo), then 97%+ | 97%
| Montfort8 | WI | 20 | 65 | Tube |  |  | 89% | 89.7% |  | 98.12% | 96.6% | 96.2% | 92.97% | 94.34% | 98.79% | 97.4% | None | 95%
| Somerset | DE | 6 | 65 | Tube | 2002-01-28: 92.52%; 2002-02-28: 95.93%; 2002-03-28: 94.97% | (93% x 6 mo), then 97%+ | 97%
| Trent Mesa | TX | 100 | 65 | Tube | 2002-01-28: 92.48%; 2002-02-28: 83.55%; 2002-03-28: 79.23% | 65%, 75%, 85% | 95%
| Fleet Wide EW 1.5 |  | 279 | Weighted Average |  |  |  | 89% | 89.7% |  | 98.12% | 96.6% | 96.2% | 92.97% | 92.96% | 87.67% | 86.93%
[8 empty] | = Construction |  |  | = Ramp-Up |  | = 93%, then 97% |  |  | = Warranted Avail.
***Commissioing Date for Turbines not exact as this is a MTD and Turbines became operation throughout the month.***
Contractual | EW 1.5mW Series |  | No. of | Hub | Tower | [12 empty] | Ramp-Up Condition | Warranted Availability
| Project Name | Location | Turbines | Height -m | Type | 2001-04-01 | 2001-05-01 | 2001-06-01 | 2001-07-01 | 2001-08-29 | 2001-09-28 | 2001-10-28 | 2001-11-28 | 2001-12-28 | 2002-01-28 | 2002-02-28 | 2002-03-28
| Fenner | NY | 20 | 65 | Tube | [12 empty] | (93% x 6 mo), then 97%+ | 97% | bar: 2002-01-28 to 2002-03-28
| Clear Sky | TX | 107 | 65 | Tube | 2002-01-28: 81.1%; 2002-02-28: 85.1% | 65%, 75%, 85% | 95%
| Klondike | OR | 16 | 65 | Tube | 2002-02-28: 94% | 60%, 70%, 80% | 95%
| Mill Run | PA | 10 | 65 | Tube | 2001-10-28: 90.1%; 2001-11-28: 87.3%; 2001-12-28: 85.9%; 2002-01-28: 93.3%; 2002-02-28: 96% | (93% x 6 mo), then 97%+ | 97%
| Montfort8 | WI | 20 | 65 | Tube | 90.2% | 89% | 89.7% | 89.4% | 93.8% | 97.8% | 94.6% | 91.9% | 87.9% | 93.6% | 98.5% |  | None | 95%
| Somerset | DE | 6 | 65 | Tube | 2001-10-28: 59.2%; 2001-11-28: 92.6%; 2001-12-28: 94.5%; 2002-01-28: 94%; 2002-02-28: 97.4% | (93% x 6 mo), then 97%+ | 97%
| Trent Mesa | TX | 100 | 65 | Tube | 2001-12-28: 66.3%; 2002-01-28: 69.8%; 2002-02-28: 94.3% | 65%, 75%, 85% | 95%
| Fleet Wide EW 1.5 |  | 279 | Weighted Average |  | 90.2% | 89% | 89.7% | 89.4% | 93.8% | 97.8% | 87.45% | 90.74% | 72.16% | 78.3% | 90.94% | 0%
[8 empty] | = Construction |  |  | = Ramp-Up |  | = 93%, then 97% |  |  | = Warranted Avail.
***Commissioing Date for Turbines not exact as this is a MTD and Turbines became operation throughout the month.***
|  | Construction | Ramp-Up |  |  | 2001-04-01: Warranted Availability
|  |  | Month 1 | Month 2 | Month 3 | Month 1 | Month 2 | Month 3 | Month 4 | Month 5 | Month 6 | Month 7 | Month 8 | Month 9 | Average Warranted
| Mechanical | 89% | 94.48% | 96.91% | 90.43% | 89.44% | 85.97% | 94.73% | 95.14% | 94.55% | 92.97% | 94.34% | 98.79% | 97.4% | 93.24%
| Contractual | 85.13% | 87.55% | 75.7% | 69.8% | 91.38% | 91.23% | 96.17% | 95.3% | 91.9% | 87.9% | 93.6% | 98.5% | 0% | 93.25%