## ContractRef
Trent Mesa Contract / Warranty Reference
Executive Summary
This sheet provides data needed to compute contractually important metrics & cross references to Construction documents.
Due to Visupro data recording anomalies during the first 60 days the data 30 day and 60 day availabilities are based on the following logic:
If there is reliable SCADA data throughout the rampup period then compute the availability from the data. All 90 day rampup data is exact.
If there is no reliable SCADA data throughout the 30 or 60 day rampup periods then use the following:
For month m and the following month f
If 30 or 60 day rampup starts between m/1 and m/6 then rampup availability = availability for mth month.
m/1 is the first day of month m and m/6 is the sixth day of month m.
If 30 or 60 day rampup starts between m/7 and m/25 then rampup availability = Average the availability of months m and f.
If 30 or 60 day rampup starts between m/26 and End of Month then rampup availability = availability of fth month.
[5 empty] | Goal |  |  | Ramp up Goal | 65% | 75% | 85%
Site | Row | Pad | Construct ID | Start Date For Avail Warranty | Start Date Group | End of 30 day ramp up | End of 60 day ramp up | End of 90 day ramp up | 30 day Avg Contractual Availability | 60 day Avg Contractual Availability | 90 day Avg Contractual Availability
TrentMesa | 1 | 1 | 1 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 9.48% | 75.92% | 85.39%
TrentMesa | 1 | 2 | 2 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 76.74% | 87.92% | 65.95%
TrentMesa | 1 | 3 | 3 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 69.63% | 71.82% | 86.59%
TrentMesa | 1 | 4 | 4 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 87.47% | 74.73% | 99.06%
TrentMesa | 1 | 5 | 5 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 96.46% | 74.8% | 97%
TrentMesa | 1 | 6 | 6 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 89.76% | 68.3% | 99.33%
TrentMesa | 1 | 7 | 7 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 81.81% | 94.49% | 89.02%
TrentMesa | 1 | 8 | 8 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 99.99% | 75.62% | 92.31%
TrentMesa | 1 | 9 | 9 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 90.01% | 43.54% | 78.24%
TrentMesa | 1 | 10 | 10 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 96.62% | 74.19% | 85.14%
TrentMesa | 1 | 11 | 11 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 85.45% | 74.34% | 84.44%
TrentMesa | 1 | 12 | 12 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 74.52% | 96.62% | 99.69%
TrentMesa | 1 | 13 | 13 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 88.04% | 72.11% | 69.64%
TrentMesa | 1 | 14 | 14 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 89.45% | 73.81% | 88.2%
TrentMesa | 1 | 15 | 15 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 62.38% | 97.6% | 98.78%
TrentMesa | 1 | 16 | 16 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 89.32% | 49.58% | 81.85%
TrentMesa | 1 | 17 | 17 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 24.58% | 99.75% | 86.83%
TrentMesa | 1 | 18 | 18 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 52.25% | 45.5% | 97.26%
TrentMesa | 1 | 19 | 19 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 81.66% | 62.97% | 97.2%
TrentMesa | 1 | 20 | 20 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 73.43% | 72.3% | 96.97%
TrentMesa | 1 | 21 | 21 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 51.92% | 62.91% | 73.27%
TrentMesa | 1 | 22 | 22 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 95.13% | 86.28% | 89%
TrentMesa | 1 | 23 | 23 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 73.06% | 52.91% | 37.72%
TrentMesa | 1 | 24 | 24 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 83.4% | 88.35% | 98.89%
TrentMesa | 1 | 25 | 25 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 82.9% | 92.87% | 98.79%
TrentMesa | 1 | 26 | 26 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 92.81% | 92.87% | 97.19%
TrentMesa | 1 | 27 | 27 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 96.1% | 87.96% | 99.57%
TrentMesa | 1 | 28 | 28 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 78.76% | 68.41% | 84.06%
TrentMesa | 1 | 29 | 29 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 88.55% | 63.53% | 87.85%
TrentMesa | 1 | 30 | 30 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 92.78% | 61.52% | 91.15%
TrentMesa | 1 | 31 | 31 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 93.6% | 72.66% | 91.58%
TrentMesa | 1 | 32 | 32 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 48.83% | 61.91% | 94.63%
TrentMesa | 1 | 33 | 33 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 8.88% | 44.51% | 99.07%
TrentMesa | 1 | 34 | 34 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 13.34% | 43.64% | 27.94%
TrentMesa | 1 | 35 | 35 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 10.13% | 7.9% | 51.26%
TrentMesa | 1 | 36 | 36 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 15.6% | 56.86% | 68.38%
TrentMesa | 1 | 37 | 37 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 72.23% | 54.94% | 81.54%
TrentMesa | 1 | 38 | 38 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 96.03% | 83.09% | 95.51%
TrentMesa | 1 | 39 | 39 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 98.59% | 87.61% | 98.55%
TrentMesa | 1 | 40 | 40 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 96.46% | 34.85% | 92.31%
TrentMesa | 1 | 41 | 41 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 94.6% | 40.18% | 96.02%
TrentMesa | 1 | 42 | 42 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 45.65% | 71.57% | 97.4%
TrentMesa | 1 | 43 | 43 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 68.42% | 67.51% | 81.37%
TrentMesa | 1 | 44 | 44 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 67.55% | 94.57% | 95.49%
TrentMesa | 1 | 45 | 45 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 35.98% | 66.67% | 95.48%
TrentMesa | 1 | 46 | 46 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 45.8% | 51.66% | 91.8%
TrentMesa | 1 | 47 | 47 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 89.96% | 84.74% | 96.5%
TrentMesa | 1 | 48 | 48 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 88.64% | 87.05% | 91.31%
TrentMesa | 1 | 49 | 49 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 71.02% | 69.59% | 89.72%
TrentMesa | 1 | 50 | 50 | 2001-11-02 | 10 | 2001-12-02 | 2002-01-01 | 2002-01-31 | 84.2% | 85.51% |  | 90 days not yet complete
TrentMesa | 1 | 51 | 51 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 48.75% | 40.03% | 54.68%
TrentMesa | 1 | 52 | 52 | 2001-09-04 | 2 | 2001-10-04 | 2001-11-03 | 2001-12-03 | 99.69% | 85.15% | 93.47%
TrentMesa | 1 | 53 | 53 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 83.8% | 87% | 83.64%
TrentMesa | 1 | 54 | 54 | 2001-09-04 | 2 | 2001-10-04 | 2001-11-03 | 2001-12-03 | 74.32% | 78.19% | 95.07%
TrentMesa | 1 | 55 | 55 | 2001-09-01 | 1 | 2001-10-01 | 2001-10-31 | 2001-11-30 | 35.41% | 79% | 51.1%
TrentMesa | 1 | 56 | 56 | 2001-09-04 | 2 | 2001-10-04 | 2001-11-03 | 2001-12-03 | 16.37% | 28.65% | 84.74%
TrentMesa | 1 | 57 | 57 | 2001-09-04 | 2 | 2001-10-04 | 2001-11-03 | 2001-12-03 | 96.62% | 74.94% | 98.72%
TrentMesa | 1 | 58 | 58 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 67.4% | 37.61% | 20.6%
TrentMesa | 1 | 59 | 59 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 43.48% | 82.12% | 96.51%
TrentMesa | 1 | 60 | 60 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 75.33% | 61.97% | 88.48%
TrentMesa | 1 | 61 | 61 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 21.95% | 46.23% | 75.51%
TrentMesa | 1 | 62 | 62 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 64.26% | 61.56% | 97.6%
TrentMesa | 1 | 63 | 63 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 28.04% | 49.1% | 83.79%
TrentMesa | 1 | 64 | 64 | 2001-09-04 | 2 | 2001-10-04 | 2001-11-03 | 2001-12-03 | 89.28% | 76.25% | 87.04%
TrentMesa | 1 | 65 | 65 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 81.66% | 60.59% | 45.28%
TrentMesa | 1 | 66 | 66 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 76.83% | 76.98% | 99.57%
TrentMesa | 1 | 67 | 67 | 2001-11-02 | 10 | 2001-12-02 | 2002-01-01 | 2002-01-31 | 33.76% | 99.21% |  | 90 days not yet complete
TrentMesa | 1 | 68 | 68 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 64.55% | 62.18% | 93.74%
TrentMesa | 1 | 69 | 69 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 68.97% | 81.91% | 99.54%
TrentMesa | 1 | 70 | 70 | 2001-09-06 | 3 | 2001-10-06 | 2001-11-05 | 2001-12-05 | 88.9% | 45.72% | 74.42%
TrentMesa | 1 | 71 | 71 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 83.31% | 86.83% | 99.55%
TrentMesa | 1 | 72 | 72 | 2001-09-07 | 4 | 2001-10-07 | 2001-11-06 | 2001-12-06 | 54.72% | 69.49% | 88.73%
TrentMesa | 1 | 73 | 73 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 49.23% | 19.64% | 58.72%
TrentMesa | 1 | 74 | 74 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 76.35% | 87.7% | 99.36%
TrentMesa | 1 | 75 | B-5 | 2001-10-22 | 7 | 2001-11-21 | 2001-12-21 | 2002-01-20 |  | 84.33% |  | Comm problems in first & third 90 days.
TrentMesa | 1 | 76 | 76 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 76.58% | 53.55% | 57.44%
TrentMesa | 1 | 77 | 77 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 39.02% | 46.79% | 84.38%
TrentMesa | 1 | 78 | 78 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 76.2% | 71.01% | 89.79%
TrentMesa | 1 | 79 | 79 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 26.27% | 69.22% | 95.11%
TrentMesa | 1 | 80 | 80 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 80.66% | 79.86% | 97.18%
TrentMesa | 1 | 81 | 81 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 49.61% | 79.72% | 92.12%
TrentMesa | 1 | 82 | 82 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 53.15% | 72.79% | 92.51%
TrentMesa | 1 | 83 | 83 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 65.25% | 75.59% | 86.45%
TrentMesa | 1 | 84 | 84 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 64.03% | 78.27% | 98.57%
TrentMesa | 1 | 85 | 85 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 28.08% | 54.69% | 89.85%
TrentMesa | 1 | 86 | 86 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 61.75% | 89.85% | 88.21%
TrentMesa | 1 | 87 | 87 | 2001-09-07 | 4 | 2001-10-07 | 2001-11-06 | 2001-12-06 | 75.47% | 82.12% | 83.18%
TrentMesa | 1 | 88 | 88 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 72.85% | 53.28% | 68.6%
TrentMesa | 1 | 89 | 89 | 2001-09-07 | 4 | 2001-10-07 | 2001-11-06 | 2001-12-06 | 92.67% | 94.53% | 99.33%
TrentMesa | 1 | 90 | 90 | 2001-09-18 | 5 | 2001-10-18 | 2001-11-17 | 2001-12-17 | 83.48% | 58.67% | 83%
TrentMesa | 1 | 91 | 91 | 2001-11-02 | 10 | 2001-12-02 | 2002-01-01 | 2002-01-31 | 97.48% | 97.17% |  | 90 days not yet complete
TrentMesa | 1 | 92 | 92 | 2001-10-31 | 9 | 2001-11-30 | 2001-12-30 | 2002-01-29 | 60.87% | 98.54% |  | 90 days not yet complete
TrentMesa | 1 | 93 | 93 | 2001-11-02 | 10 | 2001-12-02 | 2002-01-01 | 2002-01-31 | 99.97% | 95.23% |  | 90 days not yet complete
TrentMesa | 1 | 94 | 94 | 2001-10-26 | 8 | 2001-11-25 | 2001-12-25 | 2002-01-24 | 72.81% | 85.55% | 99.99%
TrentMesa | 1 | 95 | 95 | 2001-11-06 | 11 | 2001-12-06 | 2002-01-05 | 2002-02-04 | 84.02% | 88.3% |  | 90 days not yet complete
TrentMesa | 1 | 96 | 96 | 2001-11-06 | 11 | 2001-12-06 | 2002-01-05 | 2002-02-04 | 59.9% | 97.79% |  | 90 days not yet complete
TrentMesa | 1 | 97 | B-6 | 2001-10-26 | 8 | 2001-11-25 | 2001-12-25 | 2002-01-24 | 8.4% | 50.32% | 100%
TrentMesa | 1 | 98 | B-7 | 2001-10-26 | 8 | 2001-11-25 | 2001-12-25 | 2002-01-24 | 57.27% | 70.97% | 76.78%
TrentMesa | 1 | 99 | B-8 | 2001-10-19 | 6 | 2001-11-18 | 2001-12-18 | 2002-01-17 | 34.67% | 66.47% |  | No comm in 3rd ramp up period
TrentMesa | 1 | 100 | B-9 | 2001-10-19 | 6 | 2001-11-18 | 2001-12-18 | 2002-01-17 | 12.9% | 55.58% | 66.55%
[5 empty] | Actual |  |  |  | 67.24% | 70.39% | 85.62%
[5 empty] | Goal |  |  | Ramp up Goal | 65% | 75% | 85%
[5 empty] | Variance |  |  |  | 2.235% | -4.612% | 0.6169%
Negative variances are undesirable.
Formulas:
End of 30 day ramp up = [Start Date For Avail Warranty]+30
End of 60 day ramp up = [End of 30 day ramp up]+30

## 0901
Trent Mesa Project Operational Report For September 2001
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
|  |  |  | Operational Parameters |  | Operational Parameters
Site | Row | Pad | Reporting Month | kWhGenerated | kWhConsumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs
TrentMesa | 1 | 1 | 2001-09-01 | 0 | 461 | -461 | 0% | 9.48% | 68.256
TrentMesa | 1 | 2 | 2001-09-01 | 217264 | 2148 | 215116 | 20.12% | 76.74% | 552.528
TrentMesa | 1 | 3 | 2001-09-01 | 310184 | 569 | 309615 | 28.72% | 69.63% | 501.336
TrentMesa | 1 | 4 | 2001-09-01 | 453231 | 875 | 452356 | 41.97% | 87.47% | 629.784
TrentMesa | 1 | 5 | 2001-09-01 | 402962 | 1279 | 401683 | 37.31% | 96.46% | 694.512
TrentMesa | 1 | 6 | 2001-09-01 | 193868 | 1886 | 191982 | 17.95% | 89.76% | 646.272
TrentMesa | 1 | 7 | 2001-09-01 | 148629 | 1169 | 147460 | 13.76% | 81.81% | 589.032
TrentMesa | 1 | 8 | 2001-09-01 | 166739 | 350 | 166389 | 15.44% | 99.99% | 719.928
TrentMesa | 1 | 9 | 2001-09-01 | 247783 | 972 | 246811 | 22.94% | 90.01% | 648.072
TrentMesa | 1 | 10 | 2001-09-01 | 314063 | 678 | 313385 | 29.08% | 96.62% | 695.664
TrentMesa | 1 | 11 | 2001-09-01 | 369257 | 810 | 368447 | 34.19% | 85.45% | 615.24
TrentMesa | 1 | 12 | 2001-09-01 | 331456 | 1746 | 329710 | 30.69% | 74.52% | 536.544
TrentMesa | 1 | 13 | 2001-09-01 | 103254 | 3078 | 100176 | 9.561% | 88.04% | 633.888
TrentMesa | 1 | 14 | 2001-09-01 | 238564 | 183 | 238381 | 22.09% | 89.45% | 644.04
TrentMesa | 1 | 15 | 2001-09-01 | 215194 | 4612 | 210582 | 19.93% | 62.38% | 449.136
TrentMesa | 1 | 16 | 2001-09-01 | 212630 | 1236 | 211394 | 19.69% | 89.32% | 643.104
TrentMesa | 1 | 17 | 2001-09-01 | 46535 | 1957 | 44578 | 4.309% | 24.58% | 176.976
TrentMesa | 1 | 18 | 2001-09-01 | 157944 | 1922 | 156022 | 14.62% | 52.25% | 376.2
TrentMesa | 1 | 19 | 2001-09-01 | 319062 | 550 | 318512 | 29.54% | 81.66% | 587.952
TrentMesa | 1 | 20 | 2001-09-01 | 183034 | 1705 | 181329 | 16.95% | 73.43% | 528.696
TrentMesa | 1 | 21 | 2001-09-01 | 281491 | 906 | 280585 | 26.06% | 51.92% | 373.824
TrentMesa | 1 | 22 | 2001-09-01 |  |  |  |  | 95.13% | 684.936
TrentMesa | 1 | 23 | 2001-09-01 |  |  |  |  | 73.06% | 526.032
TrentMesa | 1 | 24 | 2001-09-01 |  |  |  |  | 83.4% | 600.48
TrentMesa | 1 | 25 | 2001-09-01 | 546695 | 1156 | 545539 | 50.62% | 82.9% | 596.88
TrentMesa | 1 | 26 | 2001-09-01 | 708941 | 1249 | 707692 | 65.64% | 92.81% | 668.232
TrentMesa | 1 | 27 | 2001-09-01 | 486177 | 3962 | 482215 | 45.02% | 96.1% | 691.92
TrentMesa | 1 | 28 | 2001-09-01 | 364548 | 1770 | 362778 | 33.75% | 78.76% | 567.072
TrentMesa | 1 | 29 | 2001-09-01 | 463884 | 1359 | 462525 | 42.95% | 88.55% | 637.56
TrentMesa | 1 | 30 | 2001-09-01 | 376876 | 3035 | 373841 | 34.9% | 92.78% | 668.016
TrentMesa | 1 | 31 | 2001-09-01 | 522462 | 2022 | 520440 | 48.38% | 93.6% | 673.92
TrentMesa | 1 | 32 | 2001-09-01 | 45066 | 909 | 44157 | 4.173% | 46.63% | 335.736
TrentMesa | 1 | 33 | 2001-09-01 | 470 | 10117 | -9647 | 0% | 8.88% | 63.936
TrentMesa | 1 | 34 | 2001-09-01 | 340045 | 9086 | 330959 | 31.49% | 13.34% | 96.048
TrentMesa | 1 | 35 | 2001-09-01 | 984 | 13594 | -12610 | 0% | 10.13% | 72.936
TrentMesa | 1 | 36 | 2001-09-01 | 39575 | 6779 | 32796 | 3.664% | 15.6% | 112.32
TrentMesa | 1 | 37 | 2001-09-01 | 187774 | 3388 | 184386 | 17.39% | 72.23% | 520.056
TrentMesa | 1 | 38 | 2001-09-01 | 206198 | 1240 | 204958 | 19.09% | 96.03% | 691.416
TrentMesa | 1 | 39 | 2001-09-01 | 407462 | 1100 | 406362 | 37.73% | 98.59% | 709.848
TrentMesa | 1 | 40 | 2001-09-01 | 341468 | 1344 | 340124 | 31.62% | 96.46% | 694.512
TrentMesa | 1 | 41 | 2001-09-01 | 399568 | 966 | 398602 | 37% | 94.6% | 681.12
TrentMesa | 1 | 42 | 2001-09-01 | 256995 | 4991 | 252004 | 23.8% | 45.65% | 328.68
TrentMesa | 1 | 43 | 2001-09-01 | 140556 | 4596 | 135960 | 13.01% | 68.42% | 492.624
TrentMesa | 1 | 44 | 2001-09-01 | 352425 | 1798 | 350627 | 32.63% | 67.55% | 486.36
TrentMesa | 1 | 45 | 2001-09-01 | 33118 | 905 | 32213 | 3.066% | 35.98% | 259.056
TrentMesa | 1 | 46 | 2001-09-01 | 35665 | 1242 | 34423 | 3.302% | 61.13% | 440.136
TrentMesa | 1 | 47 | 2001-09-01 | 288001 | 971 | 287030 | 26.67% | 89.96% | 647.712
TrentMesa | 1 | 48 | 2001-09-01 | 257256 | 299 | 256957 | 23.82% | 88.64% | 638.208
TrentMesa | 1 | 49 | 2001-09-01 | 181341 | 838 | 180503 | 16.79% | 95.25% | 685.8
TrentMesa | 1 | 50 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 51 | 2001-09-01 | 9502 | 361 | 9141 | 0.8798% | 51.51% | 370.872
TrentMesa | 1 | 52 | 2001-09-01 | 62654 | 1529 | 61125 | 5.801% | 99.69% | 717.768
TrentMesa | 1 | 53 | 2001-09-01 | 113717 | 925 | 112792 | 10.53% | 71.07% | 511.704
TrentMesa | 1 | 54 | 2001-09-01 | 124873 | 760 | 124113 | 11.56% | 74.32% | 535.104
TrentMesa | 1 | 55 | 2001-09-01 | 48395 | 1303 | 47092 | 4.481% | 35.41% | 254.952
TrentMesa | 1 | 56 | 2001-09-01 | 250376 | 1321 | 249055 | 23.18% | 16.37% | 117.864
TrentMesa | 1 | 57 | 2001-09-01 | 232631 | 915 | 231716 | 21.54% | 96.62% | 695.664
TrentMesa | 1 | 58 | 2001-09-01 |  |  | 0 | 0% | 98.6% | 709.92
TrentMesa | 1 | 59 | 2001-09-01 | 6231 | 603 | 5628 | 0.5769% | 18.21% | 131.112
TrentMesa | 1 | 60 | 2001-09-01 | 55495 | 2657 | 52838 | 5.138% | 99.83% | 718.776
TrentMesa | 1 | 61 | 2001-09-01 | 10524 | 1185 | 9339 | 0.9744% | 27.14% | 195.408
TrentMesa | 1 | 62 | 2001-09-01 | 103812 | 1217 | 102595 | 9.612% | 84.52% | 608.544
TrentMesa | 1 | 63 | 2001-09-01 | 49558 | 1903 | 47655 | 4.589% | 33.39% | 240.408
TrentMesa | 1 | 64 | 2001-09-01 | 149751 | 553 | 149198 | 13.87% | 89.28% | 642.816
TrentMesa | 1 | 65 | 2001-09-01 | 58627 | 660 | 57967 | 5.428% | 87.54% | 630.288
TrentMesa | 1 | 66 | 2001-09-01 | 134531 | 735 | 133796 | 12.46% | 89.28% | 642.816
TrentMesa | 1 | 67 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 68 | 2001-09-01 | 106276 | 435 | 105841 | 9.84% | 90.07% | 648.504
TrentMesa | 1 | 69 | 2001-09-01 | 57910 | 1385 | 56525 | 5.362% | 65.81% | 473.832
TrentMesa | 1 | 70 | 2001-09-01 | 46586 | 472 | 46114 | 4.314% | 88.9% | 640.08
TrentMesa | 1 | 71 | 2001-09-01 | 79800 | 123 | 79677 | 7.389% | 86.37% | 621.864
TrentMesa | 1 | 72 | 2001-09-01 | 68144 | 1362 | 66782 | 6.31% | 58.9% | 424.08
TrentMesa | 1 | 73 | 2001-09-01 | 114500 | 650 | 113850 | 10.6% | 91.67% | 660.024
TrentMesa | 1 | 74 | 2001-09-01 | 78156 | 1705 | 76451 | 7.237% | 72.64% | 523.008
TrentMesa | 1 | 75 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 76 | 2001-09-01 | 48114 | 1494 | 46620 | 4.455% | 87.16% | 627.552
TrentMesa | 1 | 77 | 2001-09-01 | 19 | 580 | -561 | 0% | 31.26% | 225.072
TrentMesa | 1 | 78 | 2001-09-01 | 95693 | 453 | 95240 | 8.86% | 85.22% | 613.584
TrentMesa | 1 | 79 | 2001-09-01 | 3600 | 510 | 3090 | 0.3333% | 2.54% | 18.288
TrentMesa | 1 | 80 | 2001-09-01 | 86603 | 541 | 86062 | 8.019% | 95.18% | 685.296
TrentMesa | 1 | 81 | 2001-09-01 | 41477 | 808 | 40669 | 3.84% | 34.38% | 247.536
TrentMesa | 1 | 82 | 2001-09-01 | 32311 | 1196 | 31115 | 2.992% | 35.24% | 253.728
TrentMesa | 1 | 83 | 2001-09-01 | 49922 | 693 | 49229 | 4.622% | 56.91% | 409.752
TrentMesa | 1 | 84 | 2001-09-01 | 55559 | 186 | 55373 | 5.144% | 51.78% | 372.816
TrentMesa | 1 | 85 | 2001-09-01 | 67844 | 116 | 67728 | 6.282% | 37.5% | 270
TrentMesa | 1 | 86 | 2001-09-01 | 17977 | 978 | 16999 | 1.665% | 42.21% | 303.912
TrentMesa | 1 | 87 | 2001-09-01 | 52625 | 1534 | 51091 | 4.873% | 70.11% | 504.792
TrentMesa | 1 | 88 | 2001-09-01 | 108597 | 1437 | 107160 | 10.06% | 86.22% | 620.784
TrentMesa | 1 | 89 | 2001-09-01 | 91121 | 1644 | 89477 | 8.437% | 91.19% | 656.568
TrentMesa | 1 | 90 | 2001-09-01 | 128992 | 290 | 128702 | 11.94% | 88.65% | 638.28
TrentMesa | 1 | 91 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 92 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 93 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 94 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 95 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 96 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 97 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 98 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 99 | 2001-09-01 | [5 empty] | 0
TrentMesa | 1 | 100 | 2001-09-01 | [5 empty] | 0
|  | Project, Before line losses | 2001-09-01 | 14739197 | 143027 | 14596170 | 16.25% | 69.84% | 43745.904
|  | Assumed 2% Line Loss | 2001-09-01 | 294783.94 | 2860.54 | 291923.4
|  | Project, After line losses | 2001-09-01 | 14444413.06 | 140166.46 | 14304246.6 | 15.92% | 69.84% | 43745.904
|  | Project, After line losses | Year To Date3 | 14444413.06 | 140166.46 | 14304246.6 | 15.92% | 69.84% | 43745.904
Notes:
1) Current month availability is based on the Enron availability formula as provided by K. Holtel 06/22/2001. Year-to-date is based on data with two different definitions.
2) This is defined as (Turbine Net kWh - Substation Net kWh)/Turbine Net kWh
3) Year to date data is the same as September data. This is the first month of reporting.
4) Gray indicates that turbine data wasn't available in the field.
OUTAGES AND CURTAILMENTS IN SEPT 2001
Trent Mesa
Grid Availability= |  | 94.31%
Time Off |  | Time On | Machines Affected | Reason |  |  | Charge | Elapsed Hrs | No of WTG Affected | Lost WTGHrs
2001-09-17 08:00 |  | 2001-09-17 18:45 | 1-21, 38-58 | AEP(Sun) added air switch |  |  | AEP | 10.75 | 41 | 440.75
2001-09-18 08:30 |  | 2001-09-18 14:00 | 59-90, ex 67,75 | Down to tension towers, and clean under platform |  |  | Constructors | 5.5 | 34 | 187
2001-09-21 08:40 |  | 2001-09-21 16:25 | 22-37, 59-90, except 67, 75 | Down to tension towers, and clean under platform |  |  | Constructors | 7.75 | 49 | 379.75
2001-09-25 08:30 |  | 2001-09-27 17:00 | 1-21,38-58 | TXU doing work . Powered up at 1930 each night, |  |  | TXU | 56.5 | 41 | 2316.5
but were curtailed due to line restrictions
2001-09-29 07:00 |  | 2001-10-01 | All | Still off for new month. AEP(Sun) stringing new lines |  |  | AEP | 41 | 100 | 4100
[10 empty] | 4100 | Total Lost
[10 empty] | 72000 | Possible
[10 empty] | 0.94306 | Grid Avail

## 1001
Trent Mesa Project Operational Report For October 2001
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
|  |  |  | Operational Parameters |  | Operational Parameters
Site | Row | Pad | Reporting Month | kWh Generated | kWh Consumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs
TrentMesa | 1 | 1 | 2001-10-01 | 142519 | 1123 | 141396 | 12.77% | 75.92% | 564.8448
TrentMesa | 1 | 2 | 2001-10-01 | 370716 | 274 | 370442 | 33.22% | 87.92% | 654.1248
TrentMesa | 1 | 3 | 2001-10-01 | 215381 | 194 | 215187 | 19.3% | 71.82% | 534.3408
TrentMesa | 1 | 4 | 2001-10-01 | 372203 | 295 | 371908 | 33.35% | 74.73% | 555.9912
TrentMesa | 1 | 5 | 2001-10-01 | 400000 | 2657 | 397343 | 35.84% | 74.8% | 556.4862
TrentMesa | 1 | 6 | 2001-10-01 | 314758 | 710 | 314048 | 28.2% | 68.3% | 508.152
TrentMesa | 1 | 7 | 2001-10-01 | 327583 | 527 | 327056 | 29.35% | 94.49% | 703.0056
TrentMesa | 1 | 8 | 2001-10-01 | 227083 | 501 | 226582 | 20.35% | 75.62% | 562.6128
TrentMesa | 1 | 9 | 2001-10-01 | 116217 | 411 | 115806 | 10.41% | 43.54% | 323.9376
TrentMesa | 1 | 10 | 2001-10-01 | 187771 | 453 | 187318 | 16.83% | 74.19% | 551.9736
TrentMesa | 1 | 11 | 2001-10-01 | 248256 | 204 | 248052 | 22.25% | 74.34% | 553.0896
TrentMesa | 1 | 12 | 2001-10-01 | 370484 | 53 | 370431 | 33.2% | 96.62% | 718.8528
TrentMesa | 1 | 13 | 2001-10-01 | 42930 | 1967 | 40963 | 3.847% | 72.11% | 536.4984
TrentMesa | 1 | 14 | 2001-10-01 | 337433 | 29 | 337404 | 30.24% | 73.81% | 549.1464
TrentMesa | 1 | 15 | 2001-10-01 | 211924 | 1225 | 210699 | 18.99% | 97.6% | 726.144
TrentMesa | 1 | 16 | 2001-10-01 | 199236 | 792 | 198444 | 17.85% | 49.58% | 368.8752
TrentMesa | 1 | 17 | 2001-10-01 | 199236 | 908 | 198328 | 17.85% | 99.75% | 742.14
TrentMesa | 1 | 18 | 2001-10-01 | 188777 | 819 | 187958 | 16.92% | 45.5% | 338.52
TrentMesa | 1 | 19 | 2001-10-01 | 309575 | 496 | 309079 | 27.74% | 62.97% | 468.4968
TrentMesa | 1 | 20 | 2001-10-01 | 394382 | 408 | 393974 | 35.34% | 72.3% | 537.912
TrentMesa | 1 | 21 | 2001-10-01 | 344164 | 267 | 343897 | 30.84% | 62.91% | 468.0504
TrentMesa | 1 | 22 | 2001-10-01 | 461397 | 114 | 461283 | 41.34% | 86.28% | 641.9027
TrentMesa | 1 | 23 | 2001-10-01 | 292753 | 501 | 292252 | 26.23% | 52.91% | 393.6504
TrentMesa | 1 | 24 | 2001-10-01 | 472502 | 386 | 472116 | 42.34% | 88.35% | 657.3522
TrentMesa | 1 | 25 | 2001-10-01 | 499077 | 251 | 498826 | 44.72% | 92.87% | 690.9528
TrentMesa | 1 | 26 | 2001-10-01 | 496654 | 219 | 496435 | 44.5% | 92.87% | 690.9528
TrentMesa | 1 | 27 | 2001-10-01 | 470404 | 853 | 469551 | 42.15% | 87.96% | 654.4334
TrentMesa | 1 | 28 | 2001-10-01 | 297639 | 315 | 297324 | 26.67% | 68.41% | 508.9704
TrentMesa | 1 | 29 | 2001-10-01 | 253214 | 216 | 252998 | 22.69% | 63.53% | 472.6632
TrentMesa | 1 | 30 | 2001-10-01 | 305991 | 568 | 305423 | 27.42% | 61.52% | 457.7088
TrentMesa | 1 | 31 | 2001-10-01 | 388596 | 877 | 387719 | 34.82% | 72.66% | 540.6208
TrentMesa | 1 | 32 | 2001-10-01 | 272922 | 1525 | 271397 | 24.46% | 51.03% | 379.6933
TrentMesa | 1 | 33 | 2001-10-01 | 104836 | 1071 | 103765 | 9.394% | 44.51% | 331.1544
TrentMesa | 1 | 34 | 2001-10-01 | 210140 | 349 | 209791 | 18.83% | 43.64% | 324.6816
TrentMesa | 1 | 35 | 2001-10-01 | 162 | 3211 | -3049 | 0% | 7.9% | 58.776
TrentMesa | 1 | 36 | 2001-10-01 | 171683 | 1585 | 170098 | 15.38% | 56.86% | 423.0384
TrentMesa | 1 | 37 | 2001-10-01 | 315596 | 438 | 315158 | 28.28% | 54.94% | 408.7536
TrentMesa | 1 | 38 | 2001-10-01 | 330417 | 247 | 330170 | 29.61% | 83.09% | 618.1896
TrentMesa | 1 | 39 | 2001-10-01 | 320066 | 265 | 319801 | 28.68% | 87.61% | 651.8184
TrentMesa | 1 | 40 | 2001-10-01 | 186490 | 254 | 186236 | 16.71% | 34.85% | 259.284
TrentMesa | 1 | 41 | 2001-10-01 | 46250 | 506 | 45744 | 4.144% | 40.18% | 298.9392
TrentMesa | 1 | 42 | 2001-10-01 | 314182 | 1104 | 313078 | 28.15% | 71.57% | 532.4808
TrentMesa | 1 | 43 | 2001-10-01 | 339292 | 838 | 338454 | 30.4% | 67.51% | 502.2744
TrentMesa | 1 | 44 | 2001-10-01 | 357177 | 521 | 356656 | 32.01% | 94.57% | 703.6008
TrentMesa | 1 | 45 | 2001-10-01 |  | 778 | -778 | 0% | 66.67% | 496.0248
TrentMesa | 1 | 46 | 2001-10-01 | 128527 | 1334 | 127193 | 11.52% | 30.47% | 226.6968
TrentMesa | 1 | 47 | 2001-10-01 | 331524 | 682 | 330842 | 29.71% | 84.74% | 630.4656
TrentMesa | 1 | 48 | 2001-10-01 | 314375 | 242 | 314133 | 28.17% | 87.05% | 647.652
TrentMesa | 1 | 49 | 2001-10-01 | 60610 | 74 | 60536 | 5.431% | 46.79% | 348.1176
TrentMesa | 1 | 50 | 2001-10-01 | Non comm 3
TrentMesa | 1 | 51 | 2001-10-01 | 17214 | 672 | 16542 | 1.542% | 45.99% | 342.1656
TrentMesa | 1 | 52 | 2001-10-01 | 287181 | 650 | 286531 | 25.73% | 85.15% | 633.516
TrentMesa | 1 | 53 | 2001-10-01 | 93207 | 67 | 93140 | 8.352% | 96.53% | 718.1832
TrentMesa | 1 | 54 | 2001-10-01 | 268035 | 255 | 267780 | 24.02% | 78.19% | 581.7336
TrentMesa | 1 | 55 | 2001-10-01 | 44743 | 55 | 44688 | 4.009% | 79% | 587.76
TrentMesa | 1 | 56 | 2001-10-01 | 53479 | 470 | 53009 | 4.792% | 28.65% | 213.156
TrentMesa | 1 | 57 | 2001-10-01 | 250869 | 1285 | 249584 | 22.48% | 74.94% | 557.5536
TrentMesa | 1 | 58 | 2001-10-01 | 1948 | 1185 | 763 | 0.1746% | 36.2% | 269.328
TrentMesa | 1 | 59 | 2001-10-01 | 25584 | 639 | 24945 | 2.292% | 68.75% | 511.5
TrentMesa | 1 | 60 | 2001-10-01 | 26092 | 3082 | 23010 | 2.338% | 50.83% | 378.1752
TrentMesa | 1 | 61 | 2001-10-01 | 25451 | 2372 | 23079 | 2.281% | 16.76% | 124.6944
TrentMesa | 1 | 62 | 2001-10-01 | 170338 | 1845 | 168493 | 15.26% | 44% | 327.36
TrentMesa | 1 | 63 | 2001-10-01 | 102789 | 1704 | 101085 | 9.21% | 22.68% | 168.7392
TrentMesa | 1 | 64 | 2001-10-01 | 190950 | 1136 | 189814 | 17.11% | 76.25% | 567.3
TrentMesa | 1 | 65 | 2001-10-01 | 98362 | 813 | 97549 | 8.814% | 75.79% | 563.8776
TrentMesa | 1 | 66 | 2001-10-01 | 159062 | 1755 | 157307 | 14.25% | 64.37% | 478.9128
TrentMesa | 1 | 67 | 2001-10-01 | Non comm
TrentMesa | 1 | 68 | 2001-10-01 | 191803 | 652 | 191151 | 17.19% | 39.02% | 290.3088
TrentMesa | 1 | 69 | 2001-10-01 | 177215 | 1242 | 175973 | 15.88% | 72.12% | 536.5728
TrentMesa | 1 | 70 | 2001-10-01 | 46277 | 251 | 46026 | 4.147% | 45.72% | 340.1568
TrentMesa | 1 | 71 | 2001-10-01 | 168580 | 665 | 167915 | 15.11% | 80.24% | 596.9856
TrentMesa | 1 | 72 | 2001-10-01 | 176430 | 661 | 175769 | 15.81% | 50.54% | 376.0176
TrentMesa | 1 | 73 | 2001-10-01 | 13371 | 2575 | 10796 | 1.198% | 6.79% | 50.5176
TrentMesa | 1 | 74 | 2001-10-01 | 202928 | 1854 | 201074 | 18.18% | 80.07% | 595.7208
TrentMesa | 1 | 75 | 2001-10-01 | Non comm
TrentMesa | 1 | 76 | 2001-10-01 | 89156 | 2164 | 86992 | 7.989% | 66% | 491.04
TrentMesa | 1 | 77 | 2001-10-01 | 18467 | 758 | 17709 | 1.655% | 46.79% | 348.1176
TrentMesa | 1 | 78 | 2001-10-01 | 115189 | 810 | 114379 | 10.32% | 67.19% | 499.8936
TrentMesa | 1 | 79 | 2001-10-01 | 1396 | 1299 | 97 | 0.1251% | 50% | 372
TrentMesa | 1 | 80 | 2001-10-01 | 21128 | 756 | 20372 | 1.893% | 66.15% | 492.156
TrentMesa | 1 | 81 | 2001-10-01 | 30210 | 1744 | 28466 | 2.707% | 64.84% | 482.4096
TrentMesa | 1 | 82 | 2001-10-01 | 62502 | 2465 | 60037 | 5.601% | 71.06% | 528.6864
TrentMesa | 1 | 83 | 2001-10-01 | 104927 | 1408 | 103519 | 9.402% | 73.58% | 547.4352
TrentMesa | 1 | 84 | 2001-10-01 | 28711 | 749 | 27962 | 2.573% | 76.28% | 567.5232
TrentMesa | 1 | 85 | 2001-10-01 | 45159 | 35 | 45124 | 4.047% | 18.66% | 138.8304
TrentMesa | 1 | 86 | 2001-10-01 | 177314 | 1283 | 176031 | 15.89% | 81.3% | 604.872
TrentMesa | 1 | 87 | 2001-10-01 | 146194 | 1971 | 144223 | 13.1% | 80.83% | 601.3752
TrentMesa | 1 | 88 | 2001-10-01 | 44564 | 2298 | 42266 | 3.993% | 59.48% | 442.5312
TrentMesa | 1 | 89 | 2001-10-01 | 158821 | 2001 | 156820 | 14.23% | 94.16% | 700.5504
TrentMesa | 1 | 90 | 2001-10-01 | 105799 | 1192 | 104607 | 9.48% | 78.31% | 582.6264
TrentMesa | 1 | 91 | 2001-10-01 | Non comm
TrentMesa | 1 | 92 | 2001-10-01 | Non comm
TrentMesa | 1 | 93 | 2001-10-01 | Non comm
TrentMesa | 1 | 94 | 2001-10-01 | Non comm
TrentMesa | 1 | 95 | 2001-10-01 | Non comm
TrentMesa | 1 | 96 | 2001-10-01 | Non comm
TrentMesa | 1 | 97 | 2001-10-01 | Non comm
TrentMesa | 1 | 98 | 2001-10-01 | Non comm
TrentMesa | 1 | 99 | 2001-10-01 | Non comm
TrentMesa | 1 | 100 | 2001-10-01 | Non comm
|  | Project, Before line losses | 2001-10-01 | 17204549 | 80455 | 17124094 | 17.72% | 65.33% | 42284.3263
|  | Assumed 2% Line Loss | 2001-10-01 | 344090.98 | 1609.1 | 342481.88
|  | Project, After line losses | 2001-10-01 | 16860458.02 | 78845.9 | 16781612.12 | 17.37% | 65.33% | 42284.3263
|  | Project, After line losses | Year To Date3 | 31304871.08 | 219012.36 | 31085858.72 | 16.64% | 67.58% | 86030.2303
Notes:
1) Current month availability is based on the Enron availability formula as provided by K. Holtel 06/22/2001.
2) This is defined as (Turbine Net kWh - Substation Net kWh)/Turbine Net kWh
3) The acronym non comm implies the turbine was not commissioned in October.
OUTAGES AND CURTAILMENTS IN OCT 2001
Trent Mesa
Grid Availability= |  | 0%
Time Off |  | Time On | Machines Affected | Reason |  |  | Charge | Elapsed Hrs | No of WTG Affected
2001-10-01 00:01 |  | 2001-10-01 07:00 | all | Curtailed due to line work. Powered only for FAA lights |  |  | AEP | 6.9833 | 0
2001-10-01 07:00 |  | 2001-10-01 18:00 | all | Substation down for Sun to finish upgrading lines |  |  | AEP, Sun | 11 | 100
2001-10-02 10:00 |  | 2001-10-02 23:30 | 1-21 | Curtailed to 1 MW by AEP due to tripping Eskota |  |  | AEP, TXU | 13.5 | 0
2001-10-02 23:30 |  | 2001-10-03 07:30 | 1-21, 38-44 | 1-21 still 1MW, 38-44 paused due to tripping Eskota |  |  | AEP, TXU | 8 | 28
2001-10-03 07:30 |  | 2001-10-03 20:30 | 1-21, 38-58 | Substation switched for Sun to level transformers |  |  | SUN | 13 | 42
2001-10-03 20:30 |  | 2001-10-05 09:00 | 1-21 | 1-21 still 1MW due to tripping Eskota |  |  | AEP, TXU | 36.5 | 21
2001-10-03 20:30 |  | 2001-10-05 09:00 | 38-44 | Left powered down |  |  | Constructors | 36.5 | 7
2001-10-05 09:00 |  | 2001-10-05 18:00 | 1-21 | 1-21 still 1MW due to tripping Eskota |  |  | AEP, TXU | 9 | 21
2001-10-05 09:00 |  | 2001-10-05 18:00 | 38-61, 87-89 | Switched for Sun to level transformers, Blatner punch list |  |  | Sun, Constructors | 9 | 27
2001-10-05 18:00 |  | 2001-10-06 09:00 | 1-21, 38-44 | 1-21 still 1MW, 38-44 paused due to tripping Eskota |  |  | AEP, TXU | 15 | 28
2001-10-06 09:00 |  | 2001-10-06 18:00 | 1-21, 38-44 | 1-21 still 1MW, 38-44 paused due to tripping Eskota |  |  | AEP, TXU | 9 | 28
2001-10-06 09:00 |  | 2001-10-06 18:00 | 45-61, 87-89 | Switched for Sun to level transformers, Blatner punch list |  |  | AEP, EWC | 9 | 19
2001-10-06 18:00 |  | 2001-10-09 07:00 | 1-21, 38-44 | 1-21 still 1MW, 38-44 paused due to tripping Eskota |  |  | AEP, TXU | 61 | 28
2001-10-09 07:00 |  | 2001-10-09 20:00 | 1-21, 38-44 powered down, balance curtailed. | ABB breaker inspection, Punchlist, level transformers |  |  | EWC,EWC,AEP | 13 | 28
2001-10-09 20:00 |  | 2001-10-10 07:00 | All | Machines left down due to ABB breaker to facilitate switching |  |  | EWC | 11 | 100
2001-10-10 07:00 |  | 2001-10-10 20:00 | 1-21, 38-58 powered down, balance curtailed | ABB breaker inspection, Punchlist, level transformers |  |  | EWC,EWC,AEP | 13 | 42
2001-10-10 20:00 |  | 2001-10-11 07:00 | All | Machines left down due to ABB breaker to facilitate switching |  |  | EWC | 11 | 100
2001-10-11 07:00 |  | 2001-10-11 20:00 | 25-37, 62-90 powered down, balance curtailed | ABB breaker inspection, Punchlist, level transformers |  |  | EWC,EWC,AEP | 13 | 42
2001-10-11 20:00 |  | 2001-10-12 07:00 | All | Machines left down due to ABB breaker to facilitate switching |  |  |  | 11 | 100
2001-10-12 07:00 |  | 2001-10-12 20:00 | 25-37, 62-90 powered down, balance curtailed | ABB breaker inspection, Punchlist, level transformers |  |  |  | 13 | 42
2001-10-12 20:00 |  | 2001-10-15 07:00 |  | Running 30 machines to avoid consumption. Not running site due to ABB safety in prep for 10/15 outage. |  |  | EWC, TXU | 59 | 70
2001-10-15 07:00 |  | 2001-10-19 19:30 | All | Site down for substation completion work. Site powered up at night with backfeed power for FAA lights. |  |  | AEP, TXU | 108.5 | 100
2001-10-19 19:30 |  | 2001-10-20 10:00 |  | Curtailed to 45 machines due to grid limitations |  |  | TXU | 14.5 | 55
2001-10-20 10:00 |  | 2001-10-20 12:30 | all | Substation tripped by Encompass by accident |  |  | Encompass | 2.5 | 100
2001-10-20 12:30 |  | 2001-10-25 07:30 |  | Curtailed to 45 machines due to grid limitations |  |  | TXU | 115 | 55
2001-10-25 07:30 |  | 2001-10-25 19:00 | All | Substation down for Ercot testing, Substation punchlist |  |  | AEP, TXU | 11.5 | 100
2001-10-25 19:00 |  | 2001-11-01 |  | Curtailed to 45 machines due to grid limitations |  |  | TXU | 149 | 55
Project
Possible
Grid Avail

## 1101
Trent Mesa Project Operational Report For November 2001
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below. Due to the wide variation of availability of neighbors of turbines 77 and 99 which
77 and 99 there was no imputation of availability for these two turbines based on nearest neighbors.
|  |  |  | Operational Parameters |  | Operational Parameters
Site | Row | Pad | Reporting Month | kWh Generated | kWh Consumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs
TrentMesa | 1 | 1 | 2001-11-01 | 395472 | 324 | 395148 | 36.62% | 85.39% | 614.808
TrentMesa | 1 | 2 | 2001-11-01 | 255695 | 823 | 254872 | 23.68% | 65.95% | 474.8367
TrentMesa | 1 | 3 | 2001-11-01 | 332891 | 131 | 332760 | 30.82% | 86.59% | 623.448
TrentMesa | 1 | 4 | 2001-11-01 | 360576 | 120 | 360456 | 33.39% | 99.06% | 713.232
TrentMesa | 1 | 5 | 2001-11-01 | 279379 | 9 | 279370 | 25.87% | 97% | 698.4
TrentMesa | 1 | 6 | 2001-11-01 | 348575 | 257 | 348318 | 32.28% | 99.33% | 715.176
TrentMesa | 1 | 7 | 2001-11-01 | 312661 | 271 | 312390 | 28.95% | 89.02% | 640.944
TrentMesa | 1 | 8 | 2001-11-01 | 469115 | 3471 | 465644 | 43.44% | 92.31% | 664.632
TrentMesa | 1 | 9 | 2001-11-01 | 245604 | 470 | 245134 | 22.74% | 78.24% | 563.328
TrentMesa | 1 | 10 | 2001-11-01 | 184866 | 341 | 184525 | 17.12% | 85.14% | 613.008
TrentMesa | 1 | 11 | 2001-11-01 | 323854 | 215 | 323639 | 29.99% | 84.44% | 607.968
TrentMesa | 1 | 12 | 2001-11-01 | 359854 | 22 | 359832 | 33.32% | 99.69% | 717.768
TrentMesa | 1 | 13 | 2001-11-01 | 161919 | 1088 | 160831 | 14.99% | 69.64% | 501.4298
TrentMesa | 1 | 14 | 2001-11-01 | 327300 | 31 | 327269 | 30.31% | 88.2% | 635.04
TrentMesa | 1 | 15 | 2001-11-01 | 301103 | 1016 | 300087 | 27.88% | 98.78% | 711.216
TrentMesa | 1 | 16 | 2001-11-01 | 195587 | 525 | 195062 | 18.11% | 81.85% | 589.32
TrentMesa | 1 | 17 | 2001-11-01 | 350000 | 3713 | 346287 | 32.41% | 86.83% | 625.176
TrentMesa | 1 | 18 | 2001-11-01 | 333963 | 229 | 333734 | 30.92% | 97.26% | 700.272
TrentMesa | 1 | 19 | 2001-11-01 | 348790 | 279 | 348511 | 32.3% | 97.2% | 699.84
TrentMesa | 1 | 20 | 2001-11-01 | 391474 | 424 | 391050 | 36.25% | 96.97% | 698.1624
TrentMesa | 1 | 21 | 2001-11-01 | 339269 | 211 | 339058 | 31.41% | 73.27% | 527.544
TrentMesa | 1 | 22 | 2001-11-01 | 413736 | 80 | 413656 | 38.31% | 89% | 640.8
TrentMesa | 1 | 23 | 2001-11-01 | 160361 | 744 | 159617 | 14.85% | 37.72% | 271.584
TrentMesa | 1 | 24 | 2001-11-01 | 381573 | 306 | 381267 | 35.33% | 98.89% | 712.008
TrentMesa | 1 | 25 | 2001-11-01 | 525205 | 125 | 525080 | 48.63% | 98.79% | 711.288
TrentMesa | 1 | 26 | 2001-11-01 | 474389 | 224 | 474165 | 43.92% | 97.19% | 699.768
TrentMesa | 1 | 27 | 2001-11-01 | 480294 | 497 | 479797 | 44.47% | 99.57% | 716.904
TrentMesa | 1 | 28 | 2001-11-01 | 420408 | 203 | 420205 | 38.93% | 84.06% | 605.232
TrentMesa | 1 | 29 | 2001-11-01 | 451114 | 653 | 450461 | 41.77% | 87.85% | 632.52
TrentMesa | 1 | 30 | 2001-11-01 | 424236 | 410 | 423826 | 39.28% | 91.15% | 656.28
TrentMesa | 1 | 31 | 2001-11-01 | 432355 | 694 | 431661 | 40.03% | 91.58% | 659.376
TrentMesa | 1 | 32 | 2001-11-01 | 349247 | 283 | 348964 | 32.34% | 72.78% | 524.016
TrentMesa | 1 | 33 | 2001-11-01 | 158787 | 884 | 157903 | 14.7% | 99.07% | 713.304
TrentMesa | 1 | 34 | 2001-11-01 | 34229 | 348 | 33881 | 3.169% | 27.94% | 201.168
TrentMesa | 1 | 35 | 2001-11-01 | 151 | 2897 | 0 | 0.01398% | 51.26% | 369.0883
TrentMesa | 1 | 36 | 2001-11-01 | 230180 | 785 | 229395 | 21.31% | 68.38% | 492.336
TrentMesa | 1 | 37 | 2001-11-01 | 278787 | 301 | 278486 | 25.81% | 81.54% | 587.088
TrentMesa | 1 | 38 | 2001-11-01 | 435683 | 226 | 435457 | 40.34% | 95.51% | 687.672
TrentMesa | 1 | 39 | 2001-11-01 | 512052 | 123 | 511929 | 47.41% | 98.55% | 709.56
TrentMesa | 1 | 40 | 2001-11-01 | 475089 | 194 | 474895 | 43.99% | 92.31% | 664.632
TrentMesa | 1 | 41 | 2001-11-01 | 359085 | 116 | 358969 | 33.25% | 96.02% | 691.344
TrentMesa | 1 | 42 | 2001-11-01 | 465112 | 402 | 464710 | 43.07% | 97.4% | 701.28
TrentMesa | 1 | 43 | 2001-11-01 | 346671 | 784 | 345887 | 32.1% | 81.37% | 585.864
TrentMesa | 1 | 44 | 2001-11-01 | 443215 | 241 | 442974 | 41.04% | 95.49% | 687.528
TrentMesa | 1 | 45 | 2001-11-01 | 446918 | 356 | 446562 | 41.38% | 95.48% | 687.456
TrentMesa | 1 | 46 | 2001-11-01 | 357468 | 720 | 356748 | 33.1% | 72.84% | 524.448
TrentMesa | 1 | 47 | 2001-11-01 | 354444 | 355 | 354089 | 32.82% | 96.5% | 694.8
TrentMesa | 1 | 48 | 2001-11-01 | 360781 | 151 | 360630 | 33.41% | 91.31% | 657.432
TrentMesa | 1 | 49 | 2001-11-01 | 322551 | 722 | 321829 | 29.87% | 92.39% | 665.208
TrentMesa | 1 | 50 | 2001-11-01 | 89966 | 838 | 89128 | 8.33% | 84.2% | 606.2148
TrentMesa | 1 | 51 | 2001-11-01 | 9314 | 813 | 8501 | 0.8624% | 34.08% | 245.376
TrentMesa | 1 | 52 | 2001-11-01 | 298859 | 430 | 298429 | 27.67% | 93.03% | 669.816
TrentMesa | 1 | 53 | 2001-11-01 | 185958 | 732 | 185226 | 17.22% | 77.47% | 557.784
TrentMesa | 1 | 54 | 2001-11-01 | 338482 | 767 | 337715 | 31.34% | 94.96% | 683.7336
TrentMesa | 1 | 55 | 2001-11-01 | 192710 | 1379 | 191331 | 17.84% | 51.1% | 367.92
TrentMesa | 1 | 56 | 2001-11-01 | 279782 | 1103 | 278679 | 25.91% | 83.16% | 598.752
TrentMesa | 1 | 57 | 2001-11-01 | 458324 | 699 | 457625 | 42.44% | 98.46% | 708.912
TrentMesa | 1 | 58 | 2001-11-01 | 0 | 1782 | -1782 | 0% | 39.02% | 280.944
TrentMesa | 1 | 59 | 2001-11-01 | 405216 | 316 | 404900 | 37.52% | 95.49% | 687.528
TrentMesa | 1 | 60 | 2001-11-01 | 260579 | 996 | 259583 | 24.13% | 73.1% | 526.3431
TrentMesa | 1 | 61 | 2001-11-01 | 142474 | 1781 | 140693 | 13.19% | 75.69% | 544.968
TrentMesa | 1 | 62 | 2001-11-01 | 337206 | 700 | 336506 | 31.22% | 79.12% | 569.664
TrentMesa | 1 | 63 | 2001-11-01 | 288479 | 1119 | 287360 | 26.71% | 75.53% | 543.816
TrentMesa | 1 | 64 | 2001-11-01 | 262333 | 782 | 261551 | 24.29% | 80.96% | 582.912
TrentMesa | 1 | 65 | 2001-11-01 | 108595 | 1625 | 106970 | 10.06% | 45.38% | 326.736
TrentMesa | 1 | 66 | 2001-11-01 | 252655 | 962 | 251693 | 23.39% | 89.59% | 645.048
TrentMesa | 1 | 67 | 2001-11-01 | 0 | 947 | -947 | 0% | 33.76% | 243.072
TrentMesa | 1 | 68 | 2001-11-01 | 275349 | 718 | 274631 | 25.5% | 85.34% | 614.448
TrentMesa | 1 | 69 | 2001-11-01 | 354403 | 646 | 353757 | 32.82% | 91.69% | 660.168
TrentMesa | 1 | 70 | 2001-11-01 | 171450 | 257 | 171193 | 15.88% | 72.15% | 519.48
TrentMesa | 1 | 71 | 2001-11-01 | 341325 | 400 | 340925 | 31.6% | 93.43% | 672.696
TrentMesa | 1 | 72 | 2001-11-01 | 322151 | 784 | 321367 | 29.83% | 88.45% | 636.84
TrentMesa | 1 | 73 | 2001-11-01 | 95346 | 2732 | 92614 | 8.828% | 32.49% | 233.928
TrentMesa | 1 | 74 | 2001-11-01 | 342360 | 1122 | 341238 | 31.7% | 95.32% | 686.304
TrentMesa | 1 | 75 | 2001-11-01 | 240975 | 1303 | 239672 | 22.31% | 69.61% | 501.192
TrentMesa | 1 | 76 | 2001-11-01 | 148426 | 2020 | 146406 | 13.74% | 41.11% | 295.992
TrentMesa | 1 | 77 | 2001-11-01 | No commun 3
TrentMesa | 1 | 78 | 2001-11-01 | 276809 | 496 | 276313 | 25.63% | 74.82% | 538.704
TrentMesa | 1 | 79 | 2001-11-01 | 239194 | 711 | 238483 | 22.15% | 88.43% | 636.696
TrentMesa | 1 | 80 | 2001-11-01 | 335051 | 314 | 334737 | 31.02% | 93.56% | 673.632
TrentMesa | 1 | 81 | 2001-11-01 | 162579 | 573 | 162006 | 15.05% | 94.6% | 681.12
TrentMesa | 1 | 82 | 2001-11-01 | 289615 | 1857 | 287758 | 26.82% | 74.52% | 536.544
TrentMesa | 1 | 83 | 2001-11-01 | 302585 | 841 | 301744 | 28.02% | 77.59% | 558.648
TrentMesa | 1 | 84 | 2001-11-01 | 260867 | 332 | 260535 | 24.15% | 80.25% | 577.8
TrentMesa | 1 | 85 | 2001-11-01 | 131032 | 236 | 130796 | 12.13% | 90.72% | 653.2183
TrentMesa | 1 | 86 | 2001-11-01 | 342674 | 785 | 341889 | 31.73% | 98.41% | 708.552
TrentMesa | 1 | 87 | 2001-11-01 | 294856 | 1401 | 293455 | 27.3% | 83.42% | 600.624
TrentMesa | 1 | 88 | 2001-11-01 | 7483 | 2759 | 4724 | 0.6929% | 47.08% | 338.976
TrentMesa | 1 | 89 | 2001-11-01 | 367528 | 805 | 366723 | 34.03% | 94.9% | 683.28
TrentMesa | 1 | 90 | 2001-11-01 | 4989 | 1975 | 3014 | 0.4619% | 39.04% | 281.088
TrentMesa | 1 | 91 | 2001-11-01 | 135276 | 716 | 134560 | 12.53% | 97.48% | 701.856
TrentMesa | 1 | 92 | 2001-11-01 | 159842 | 604 | 159238 | 14.8% | 60.87% | 438.264
TrentMesa | 1 | 93 | 2001-11-01 | 150250 | 60 | 150190 | 13.91% | 99.97% | 719.784
TrentMesa | 1 | 94 | 2001-11-01 | 225412 | 1023 | 224389 | 20.87% | 72.81% | 524.232
TrentMesa | 1 | 95 | 2001-11-01 | 177966 | 532 | 177434 | 16.48% | 84.02% | 604.944
TrentMesa | 1 | 96 | 2001-11-01 | 54221 | 356 | 53865 | 5.02% | 59.9% | 431.28
TrentMesa | 1 | 97 | 2001-11-01 | 0 | 3586 | -3586 | 0% | 8.4% | 60.48
TrentMesa | 1 | 98 | 2001-11-01 | 110527 | 897 | 109630 | 10.23% | 57.27% | 412.344
TrentMesa | 1 | 99 | 2001-11-01 | No commun |  |  |  | 34.67% | 249.6
TrentMesa | 1 | 100 | 2001-11-01 | 14366 | 1339 | 13027 | 1.33% | 12.9% | 92.88
|  | Project, Before line losses | 2001-11-01 | 26957907 | 77745 | 26882908 | 25.47% | 79.13% | 56400.667
|  | Assumed 2% Line Loss | 2001-11-01 | 539158.14 | 1554.9 | 537658.16
|  | Project, After line losses | 2001-11-01 | 26418748.86 | 76190.1 | 26345249.84 | 24.96% | 79.13% | 56400.667
|  | Project, After line losses | Year To Date3 | 57723619.94 | 295202.46 | 57431108.56 | 19.42% | 71.43% | 142430.8973
Notes:
1) Current month availability is based on the Enron availability formula as provided by K. Holtel 06/22/2001. Year-to-date is based on data with two different definitions.
2) This is defined as (Turbine Net kWh - Substation Net kWh)/Turbine Net kWh
3) No commun implies no communication. Turbine 77 probably had excellent availability but there was no SCADA communication.
Turbine 77 removed from availability average to avoid skewing availability results. Turbine 77 doesn't aid or penalize project availability.
Turbine 99 also had no SCADA communication all month & had a shaft failure in mid month. Availability shown as (13/30) of project wide 80% since this was a
warranty failure at the end of the 13th. Turbine 99 penalizes project availability.
OUTAGES AND CURTAILMENTS IN NOV 2001
Trent Mesa
Grid Availability= |  | 98.17%
Time Off |  | Time On | Machines Affected | Reason |  |  | Charge | Elapsed Hrs | No of WTG Affected | Lost WTGHrs
2001-11-01 00:01 |  | 2001-11-02 07:00 |  | Curtailed 45 machines due to grid limitations |  |  | TXU | 30.9833 | 45 | 1394.25
2001-11-02 07:00 |  | 2001-11-02 18:20 | All | Substation down to complete sub & trip test |  |  | AEP | 11.3333 | 100 | 1133.3333
2001-11-03 07:00 |  | 2001-11-03 15:30 | 62-69 | Padmount retrofit |  |  | EWC | 8.5 | 8 | 68
2001-11-06 13:00 |  | 2001-11-06 16:00 | 18-21, 38-61, 75, 97-100 | Moisture in feeder deadend cap |  |  | Sun | 3 | 28 | 84
2001-11-07 07:00 |  | 2001-11-07 18:30 | 18-21, 38-61, 75, 97-100 | Padmount retrofit |  |  | EWC | 11.5 | 28 | 322
2001-11-08 07:00 |  | 2001-11-08 18:30 | 18-21, 38-61, 75, 97-100 | Padmount retrofit |  |  | EWC | 11.5 | 28 | 322
2001-11-09 07:00 |  | 2001-11-09 18:30 | 18-21, 38-61, 75, 97-100 | Padmount retrofit |  |  | EWC | 11.5 | 28 | 322
2001-11-09 13:00 |  | 2001-11-09 18:30 | 22-37 | Padmount retrofit |  |  | EWC | 5.5 | 16 | 88
2001-11-12 07:00 |  | 2001-11-12 18:30 | 1-17 | Padmount retrofit |  |  | EWC | 11.5 | 17 | 195.5
2001-11-13 11:00 |  | 2001-11-13 18:30 | 1-17 | Padmount retrofit |  |  | EWC | 7.5 | 17 | 127.5
2001-11-14 08:30 |  | 2001-11-14 15:30 | 62-69, 90-96 | Padmount retrofit |  |  | EWC | 7 | 15 | 105
2001-11-30 10:00 |  | 2001-11-30 15:30 | 18-21, 38-61, 75, 97-100 | Sub station work |  |  | AEP | 5.5 | 28 | 154
[10 empty] | 1314 | Total Lost
[10 empty] | 72000 | Possible
[10 empty] | 0.98175 | Grid Avail
Trent Mesa Project Operational Report For November 2001
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below. Due to the wide variation of availability of neighbors of turbines 77 and 99 which
77 and 99 there was no imputation of availability for these two turbines based on nearest neighbors.
|  |  |  | Operational Parameters |  | Operational Parameters
Site | Row | Pad | Reporting Month | kWh Generated | kWh Consumed | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs | Comment
TrentMesa | 1 | 97 | 2001-11-01 | 0 | 3586 | -3586 | 0% | 8.4% | 60.48 | Bad IBGT
TrentMesa | 1 | 35 | 2001-11-01 | 151 | 2897 | -2746 | 0% | 51.26% | 369.0883 | Bad IBGT
TrentMesa | 1 | 58 | 2001-11-01 | 0 | 1782 | -1782 | 0% | 39.02% | 280.944 | Coil failure in SEG
TrentMesa | 1 | 67 | 2001-11-01 | 0 | 947 | -947 | 0% | 33.76% | 243.072
TrentMesa | 1 | 90 | 2001-11-01 | 4989 | 1975 | 3014 | 0.4619% | 39.04% | 281.088 | Gen J-box failure.
TrentMesa | 1 | 88 | 2001-11-01 | 7483 | 2759 | 4724 | 0.6929% | 47.08% | 338.976
TrentMesa | 1 | 51 | 2001-11-01 | 9314 | 813 | 8501 | 0.8624% | 34.08% | 245.376
TrentMesa | 1 | 100 | 2001-11-01 | 14366 | 1339 | 13027 | 1.33% | 12.9% | 92.88
TrentMesa | 1 | 5 | 2001-11-01 | 13083 | 9 | 13074 | 1.211% | 97% | 698.4
TrentMesa | 1 | 34 | 2001-11-01 | 34229 | 348 | 33881 | 3.169% | 27.94% | 201.168 | T-bolt replacement.
TrentMesa | 1 | 96 | 2001-11-01 | 54221 | 356 | 53865 | 5.02% | 59.9% | 431.28
TrentMesa | 1 | 50 | 2001-11-01 | 89966 | 838 | 89128 | 8.33% | 84.2% | 606.2148
TrentMesa | 1 | 73 | 2001-11-01 | 95346 | 2732 | 92614 | 8.828% | 32.49% | 233.928
TrentMesa | 1 | 65 | 2001-11-01 | 108595 | 1625 | 106970 | 10.06% | 45.38% | 326.736
TrentMesa | 1 | 98 | 2001-11-01 | 110527 | 897 | 109630 | 10.23% | 57.27% | 412.344
TrentMesa | 1 | 85 | 2001-11-01 | 131032 | 236 | 130796 | 12.13% | 90.72% | 653.2183
TrentMesa | 1 | 91 | 2001-11-01 | 135276 | 716 | 134560 | 12.53% | 97.48% | 701.856
TrentMesa | 1 | 61 | 2001-11-01 | 142474 | 1781 | 140693 | 13.19% | 75.69% | 544.968
TrentMesa | 1 | 76 | 2001-11-01 | 148426 | 2020 | 146406 | 13.74% | 41.11% | 295.992
TrentMesa | 1 | 93 | 2001-11-01 | 150250 | 60 | 150190 | 13.91% | 99.97% | 719.784
TrentMesa | 1 | 33 | 2001-11-01 | 158787 | 884 | 157903 | 14.7% | 99.07% | 713.304
TrentMesa | 1 | 92 | 2001-11-01 | 159842 | 604 | 159238 | 14.8% | 60.87% | 438.264
TrentMesa | 1 | 23 | 2001-11-01 | 160361 | 744 | 159617 | 14.85% | 37.72% | 271.584
TrentMesa | 1 | 13 | 2001-11-01 | 161919 | 1088 | 160831 | 14.99% | 69.64% | 501.4298
TrentMesa | 1 | 81 | 2001-11-01 | 162579 | 573 | 162006 | 15.05% | 94.6% | 681.12
TrentMesa | 1 | 70 | 2001-11-01 | 171450 | 257 | 171193 | 15.88% | 72.15% | 519.48
TrentMesa | 1 | 95 | 2001-11-01 | 177966 | 532 | 177434 | 16.48% | 84.02% | 604.944
TrentMesa | 1 | 10 | 2001-11-01 | 184866 | 341 | 184525 | 17.12% | 85.14% | 613.008
TrentMesa | 1 | 53 | 2001-11-01 | 185958 | 732 | 185226 | 17.22% | 77.47% | 557.784
TrentMesa | 1 | 55 | 2001-11-01 | 192710 | 1379 | 191331 | 17.84% | 51.1% | 367.92
TrentMesa | 1 | 16 | 2001-11-01 | 195587 | 525 | 195062 | 18.11% | 81.85% | 589.32
TrentMesa | 1 | 94 | 2001-11-01 | 225412 | 1023 | 224389 | 20.87% | 72.81% | 524.232
TrentMesa | 1 | 36 | 2001-11-01 | 230180 | 785 | 229395 | 21.31% | 68.38% | 492.336
TrentMesa | 1 | 79 | 2001-11-01 | 239194 | 711 | 238483 | 22.15% | 88.43% | 636.696
TrentMesa | 1 | 75 | 2001-11-01 | 240975 | 1303 | 239672 | 22.31% | 69.61% | 501.192
TrentMesa | 1 | 9 | 2001-11-01 | 245604 | 470 | 245134 | 22.74% | 78.24% | 563.328
TrentMesa | 1 | 66 | 2001-11-01 | 252655 | 962 | 251693 | 23.39% | 89.59% | 645.048
TrentMesa | 1 | 2 | 2001-11-01 | 255695 | 823 | 254872 | 23.68% | 65.95% | 474.8367
TrentMesa | 1 | 60 | 2001-11-01 | 260579 | 996 | 259583 | 24.13% | 73.1% | 526.3431
TrentMesa | 1 | 84 | 2001-11-01 | 260867 | 332 | 260535 | 24.15% | 80.25% | 577.8
TrentMesa | 1 | 64 | 2001-11-01 | 262333 | 782 | 261551 | 24.29% | 80.96% | 582.912
TrentMesa | 1 | 68 | 2001-11-01 | 275349 | 718 | 274631 | 25.5% | 85.34% | 614.448
TrentMesa | 1 | 78 | 2001-11-01 | 276809 | 496 | 276313 | 25.63% | 74.82% | 538.704
TrentMesa | 1 | 37 | 2001-11-01 | 278787 | 301 | 278486 | 25.81% | 81.54% | 587.088
TrentMesa | 1 | 56 | 2001-11-01 | 279782 | 1103 | 278679 | 25.91% | 83.16% | 598.752
TrentMesa | 1 | 63 | 2001-11-01 | 288479 | 1119 | 287360 | 26.71% | 75.53% | 543.816
TrentMesa | 1 | 82 | 2001-11-01 | 289615 | 1857 | 287758 | 26.82% | 74.52% | 536.544
TrentMesa | 1 | 87 | 2001-11-01 | 294856 | 1401 | 293455 | 27.3% | 83.42% | 600.624
TrentMesa | 1 | 52 | 2001-11-01 | 298859 | 430 | 298429 | 27.67% | 93.03% | 669.816
TrentMesa | 1 | 15 | 2001-11-01 | 301103 | 1016 | 300087 | 27.88% | 98.78% | 711.216
TrentMesa | 1 | 83 | 2001-11-01 | 302585 | 841 | 301744 | 28.02% | 77.59% | 558.648
TrentMesa | 1 | 7 | 2001-11-01 | 312661 | 271 | 312390 | 28.95% | 89.02% | 640.944
TrentMesa | 1 | 72 | 2001-11-01 | 322151 | 784 | 321367 | 29.83% | 88.45% | 636.84
TrentMesa | 1 | 49 | 2001-11-01 | 322551 | 722 | 321829 | 29.87% | 92.39% | 665.208
TrentMesa | 1 | 11 | 2001-11-01 | 323854 | 215 | 323639 | 29.99% | 84.44% | 607.968
TrentMesa | 1 | 14 | 2001-11-01 | 327300 | 31 | 327269 | 30.31% | 88.2% | 635.04
TrentMesa | 1 | 3 | 2001-11-01 | 332891 | 131 | 332760 | 30.82% | 86.59% | 623.448
TrentMesa | 1 | 18 | 2001-11-01 | 333963 | 229 | 333734 | 30.92% | 97.26% | 700.272
TrentMesa | 1 | 80 | 2001-11-01 | 335051 | 314 | 334737 | 31.02% | 93.56% | 673.632
TrentMesa | 1 | 62 | 2001-11-01 | 337206 | 700 | 336506 | 31.22% | 79.12% | 569.664
TrentMesa | 1 | 54 | 2001-11-01 | 338482 | 767 | 337715 | 31.34% | 94.96% | 683.7336
TrentMesa | 1 | 21 | 2001-11-01 | 339269 | 211 | 339058 | 31.41% | 73.27% | 527.544
TrentMesa | 1 | 71 | 2001-11-01 | 341325 | 400 | 340925 | 31.6% | 93.43% | 672.696
TrentMesa | 1 | 74 | 2001-11-01 | 342360 | 1122 | 341238 | 31.7% | 95.32% | 686.304
TrentMesa | 1 | 86 | 2001-11-01 | 342674 | 785 | 341889 | 31.73% | 98.41% | 708.552
TrentMesa | 1 | 43 | 2001-11-01 | 346671 | 784 | 345887 | 32.1% | 81.37% | 585.864
TrentMesa | 1 | 6 | 2001-11-01 | 348575 | 257 | 348318 | 32.28% | 99.33% | 715.176
TrentMesa | 1 | 19 | 2001-11-01 | 348790 | 279 | 348511 | 32.3% | 97.2% | 699.84
TrentMesa | 1 | 32 | 2001-11-01 | 349247 | 283 | 348964 | 32.34% | 72.78% | 524.016
TrentMesa | 1 | 69 | 2001-11-01 | 354403 | 646 | 353757 | 32.82% | 91.69% | 660.168
TrentMesa | 1 | 47 | 2001-11-01 | 354444 | 355 | 354089 | 32.82% | 96.5% | 694.8
TrentMesa | 1 | 46 | 2001-11-01 | 357468 | 720 | 356748 | 33.1% | 72.84% | 524.448
TrentMesa | 1 | 41 | 2001-11-01 | 359085 | 116 | 358969 | 33.25% | 96.02% | 691.344
TrentMesa | 1 | 12 | 2001-11-01 | 359854 | 22 | 359832 | 33.32% | 99.69% | 717.768
TrentMesa | 1 | 4 | 2001-11-01 | 360576 | 120 | 360456 | 33.39% | 99.06% | 713.232
TrentMesa | 1 | 48 | 2001-11-01 | 360781 | 151 | 360630 | 33.41% | 91.31% | 657.432
TrentMesa | 1 | 89 | 2001-11-01 | 367528 | 805 | 366723 | 34.03% | 94.9% | 683.28
TrentMesa | 1 | 24 | 2001-11-01 | 381573 | 306 | 381267 | 35.33% | 98.89% | 712.008
TrentMesa | 1 | 20 | 2001-11-01 | 391474 | 424 | 391050 | 36.25% | 96.97% | 698.1624
TrentMesa | 1 | 1 | 2001-11-01 | 395472 | 324 | 395148 | 36.62% | 85.39% | 614.808
TrentMesa | 1 | 59 | 2001-11-01 | 405216 | 316 | 404900 | 37.52% | 95.49% | 687.528
TrentMesa | 1 | 22 | 2001-11-01 | 413736 | 80 | 413656 | 38.31% | 89% | 640.8
TrentMesa | 1 | 28 | 2001-11-01 | 420408 | 203 | 420205 | 38.93% | 84.06% | 605.232
TrentMesa | 1 | 30 | 2001-11-01 | 424236 | 410 | 423826 | 39.28% | 91.15% | 656.28
TrentMesa | 1 | 31 | 2001-11-01 | 432355 | 694 | 431661 | 40.03% | 91.58% | 659.376
TrentMesa | 1 | 38 | 2001-11-01 | 435683 | 226 | 435457 | 40.34% | 95.51% | 687.672
TrentMesa | 1 | 44 | 2001-11-01 | 443215 | 241 | 442974 | 41.04% | 95.49% | 687.528
TrentMesa | 1 | 45 | 2001-11-01 | 446918 | 356 | 446562 | 41.38% | 95.48% | 687.456
TrentMesa | 1 | 29 | 2001-11-01 | 451114 | 653 | 450461 | 41.77% | 87.85% | 632.52
TrentMesa | 1 | 57 | 2001-11-01 | 458324 | 699 | 457625 | 42.44% | 98.46% | 708.912
TrentMesa | 1 | 42 | 2001-11-01 | 465112 | 402 | 464710 | 43.07% | 97.4% | 701.28
TrentMesa | 1 | 8 | 2001-11-01 | 469115 | 3471 | 465644 | 43.44% | 50.43% | 363.1153
TrentMesa | 1 | 26 | 2001-11-01 | 474389 | 224 | 474165 | 43.92% | 97.19% | 699.768
TrentMesa | 1 | 40 | 2001-11-01 | 475089 | 194 | 474895 | 43.99% | 92.31% | 664.632
TrentMesa | 1 | 27 | 2001-11-01 | 480294 | 497 | 479797 | 44.47% | 99.57% | 716.904
TrentMesa | 1 | 39 | 2001-11-01 | 512052 | 123 | 511929 | 47.41% | 98.55% | 709.56
TrentMesa | 1 | 25 | 2001-11-01 | 525205 | 125 | 525080 | 48.63% | 98.79% | 711.288
TrentMesa | 1 | 17 | 2001-11-01 | 674754 | 3713 | 671041 | 62.48% | 86.83% | 625.176
TrentMesa | 1 | 77 | 2001-11-01 | No commun 3
TrentMesa | 1 | 99 | 2001-11-01 | No commun |  |  |  | 0% | 0

## 1201
Trent Mesa Project Operational Report For December 2001
Executive Summary
This interim report was generated to comply with the contractual monthly reporting requirement from the Windsystem, Operations, & Maintenance Agreement.
The description of outages, safety near miss events, accidents, infrastructure work, and maintenance records are not included in this interim report.
All other required components are provided below.
|  |  |  | Operational Parameters |  | Operational Parameters
Site | Row | Pad | Reporting Month | kWh Generated 2 | kWh Consumed 2 | Net kWh Production | Capacity Factor | Availability1 | Operating Hrs
TrentMesa | 1 | 1 | 2001-12-01 | 476326 | 295 | 476031 | 42.68% | 98.94% | 736.1136
TrentMesa | 1 | 2 | 2001-12-01 | 359804 | 684 | 359120 | 32.24% | 82.4% | 613.056
TrentMesa | 1 | 3 | 2001-12-01 | 388678 | 189 | 388489 | 34.83% | 89.83% | 668.3352
TrentMesa | 1 | 4 | 2001-12-01 | 453331 | 187 | 453144 | 40.62% | 97.83% | 727.8552
TrentMesa | 1 | 5 | 2001-12-01 | 427510 | 457 | 427053 | 38.31% | 96.9% | 720.936
TrentMesa | 1 | 6 | 2001-12-01 | 427337 | 467 | 426870 | 38.29% | 99.31% | 738.8664
TrentMesa | 1 | 7 | 2001-12-01 | 397039 | 488 | 396551 | 35.58% | 99.15% | 737.676
TrentMesa | 1 | 8 | 2001-12-01 | 232296 | 713 | 231583 | 20.82% | 76.35% | 568.044
TrentMesa | 1 | 9 | 2001-12-01 | 366107 | 259 | 365848 | 32.81% | 99.86% | 742.9584
TrentMesa | 1 | 10 | 2001-12-01 | 306283 | 310 | 305973 | 27.44% | 95.16% | 707.9904
TrentMesa | 1 | 11 | 2001-12-01 | 355884 | 419 | 355465 | 31.89% | 92.56% | 688.6464
TrentMesa | 1 | 12 | 2001-12-01 | 386351 | 19 | 386332 | 34.62% | 97.45% | 725.028
TrentMesa | 1 | 13 | 2001-12-01 | 390000 | 526 | 389474 | 34.95% | 97.21% | 723.2424
TrentMesa | 1 | 14 | 2001-12-01 | 420417 | 51 | 420366 | 37.67% | 99.95% | 743.628
TrentMesa | 1 | 15 | 2001-12-01 | 413689 | 845 | 412844 | 37.07% | 99.56% | 740.7264
TrentMesa | 1 | 16 | 2001-12-01 | 431966 | 236 | 431730 | 38.71% | 99.96% | 743.7024
TrentMesa | 1 | 17 | 2001-12-01 | 425630 | 560 | 425070 | 38.14% | 99.04% | 736.8576
TrentMesa | 1 | 18 | 2001-12-01 | 425114 | 331 | 424783 | 38.09% | 99.74% | 742.0656
TrentMesa | 1 | 19 | 2001-12-01 | 386747 | 152 | 386595 | 34.65% | 99.65% | 741.396
TrentMesa | 1 | 20 | 2001-12-01 | 461433 | 298 | 461135 | 41.35% | 99.93% | 743.4792
TrentMesa | 1 | 21 | 2001-12-01 | 458811 | 192 | 458619 | 41.11% | 99.54% | 740.5776
TrentMesa | 1 | 22 | 2001-12-01 | 486057 | 131 | 485926 | 43.55% | 99.23% | 738.2712
TrentMesa | 1 | 23 | 2001-12-01 | 380801 | 0.426 | 380800.574 | 34.12% | 87.62% | 651.8928
TrentMesa | 1 | 24 | 2001-12-01 | 451325 | 363 | 450962 | 40.44% | 98.18% | 730.4592
TrentMesa | 1 | 25 | 2001-12-01 | 534183 | 154 | 534029 | 47.87% | 97.54% | 725.6976
TrentMesa | 1 | 26 | 2001-12-01 | 486628 | 254 | 486374 | 43.6% | 97.45% | 725.028
TrentMesa | 1 | 27 | 2001-12-01 | 408601 | 806 | 407795 | 36.61% | 93.66% | 696.8304
TrentMesa | 1 | 28 | 2001-12-01 | 458939 | 252 | 458687 | 41.12% | 96.92% | 721.0848
TrentMesa | 1 | 29 | 2001-12-01 | 479041 | 357 | 478684 | 42.92% | 95.88% | 713.3472
TrentMesa | 1 | 30 | 2001-12-01 | 447646 | 361 | 447285 | 40.11% | 91.59% | 681.4296
TrentMesa | 1 | 31 | 2001-12-01 | 525420 | 419 | 525001 | 47.08% | 99.78% | 742.3632
TrentMesa | 1 | 32 | 2001-12-01 | 486438 | 254 | 486184 | 43.59% | 96.34% | 716.7696
TrentMesa | 1 | 33 | 2001-12-01 | 449826 | 535 | 449291 | 40.31% | 95.17% | 708.0648
TrentMesa | 1 | 34 | 2001-12-01 | 424463 | 326 | 424137 | 38.03% | 92.4% | 687.456
TrentMesa | 1 | 35 | 2001-12-01 | 406482 | 980 | 405502 | 36.42% | 96.24% | 716.0256
TrentMesa | 1 | 36 | 2001-12-01 | 444593 | 593 | 444000 | 39.84% | 96% | 714.24
TrentMesa | 1 | 37 | 2001-12-01 | 424510 | 311 | 424199 | 38.04% | 97.57% | 725.9208
TrentMesa | 1 | 38 | 2001-12-01 | 470112 | 210 | 469902 | 42.12% | 97.49% | 725.3256
TrentMesa | 1 | 39 | 2001-12-01 | 485511 | 177 | 485334 | 43.5% | 99.72% | 741.9168
TrentMesa | 1 | 40 | 2001-12-01 | 495028 | 242 | 494786 | 44.36% | 97.49% | 725.3256
TrentMesa | 1 | 41 | 2001-12-01 | 492911 | 256 | 492655 | 44.17% | 97.6% | 726.144
TrentMesa | 1 | 42 | 2001-12-01 | 509026 | 361 | 508665 | 45.61% | 99.25% | 738.42
TrentMesa | 1 | 43 | 2001-12-01 | 375042 | 841 | 374201 | 33.61% | 83.5% | 621.24
TrentMesa | 1 | 44 | 2001-12-01 | 511439 | 203 | 511236 | 45.83% | 99.77% | 742.2888
TrentMesa | 1 | 45 | 2001-12-01 | 460188 | 448 | 459740 | 41.24% | 89.67% | 667.1448
TrentMesa | 1 | 46 | 2001-12-01 | 423467 | 536 | 422931 | 37.95% | 95.41% | 709.8504
TrentMesa | 1 | 47 | 2001-12-01 | 420189 | 220 | 419969 | 37.65% | 99% | 736.56
TrentMesa | 1 | 48 | 2001-12-01 | 440679 | 126 | 440553 | 39.49% | 99.57% | 740.8008
TrentMesa | 1 | 49 | 2001-12-01 | 415079 | 497 | 414582 | 37.19% | 96.47% | 717.7368
TrentMesa | 1 | 50 | 2001-12-01 | 389578 | 461 | 389117 | 34.91% | 85.51% | 636.1944
TrentMesa | 1 | 51 | 2001-12-01 | 445172 | 9594 | 435578 | 39.89% | 97.65% | 726.516
TrentMesa | 1 | 52 | 2001-12-01 | 382037 | 551 | 381486 | 34.23% | 95.35% | 709.404
TrentMesa | 1 | 53 | 2001-12-01 | 409588 | 450 | 409138 | 36.7% | 95.3% | 709.032
TrentMesa | 1 | 54 | 2001-12-01 | 394846 | 883 | 393963 | 35.38% | 83.76% | 623.1744
TrentMesa | 1 | 55 | 2001-12-01 | 497837 | 393 | 497444 | 44.61% | 92.67% | 689.4648
TrentMesa | 1 | 56 | 2001-12-01 | 493198 | 406 | 492792 | 44.19% | 99.02% | 736.7088
TrentMesa | 1 | 57 | 2001-12-01 | 491456 | 348 | 491108 | 44.04% | 99.79% | 742.4376
TrentMesa | 1 | 58 | 2001-12-01 | 89054 | 1164 | 87890 | 7.98% | 32.31% | 240.3864
TrentMesa | 1 | 59 | 2001-12-01 | 459744 | 320 | 459424 | 41.2% | 99.75% | 742.14
TrentMesa | 1 | 60 | 2001-12-01 | 336500 | 1316 | 335184 | 30.15% | 75.27% | 560.0088
TrentMesa | 1 | 61 | 2001-12-01 | 397340 | 838 | 396502 | 35.6% | 96.02% | 714.3888
TrentMesa | 1 | 62 | 2001-12-01 | 460777 | 402 | 460375 | 41.29% | 99.74% | 742.0656
TrentMesa | 1 | 63 | 2001-12-01 | 372900 | 1091 | 371809 | 33.41% | 79.44% | 591.0336
TrentMesa | 1 | 64 | 2001-12-01 | 356540 | 381 | 356159 | 31.95% | 91.6% | 681.504
TrentMesa | 1 | 65 | 2001-12-01 | 309179 | 634 | 308545 | 27.7% | 83.51% | 621.3144
TrentMesa | 1 | 66 | 2001-12-01 | 425507 | 536 | 424971 | 38.13% | 99.2% | 738.048
TrentMesa | 1 | 67 | 2001-12-01 | 417115 | 261 | 416854 | 37.38% | 99.21% | 738.1224
TrentMesa | 1 | 68 | 2001-12-01 | 469408 | 445 | 468963 | 42.06% | 94.94% | 706.3536
TrentMesa | 1 | 69 | 2001-12-01 | 510234 | 385 | 509849 | 45.72% | 99.64% | 741.3216
TrentMesa | 1 | 70 | 2001-12-01 | 395665 | 384 | 395281 | 35.45% | 82.94% | 617.0736
TrentMesa | 1 | 71 | 2001-12-01 | 482761 | 236 | 482525 | 43.26% | 99.68% | 741.6192
TrentMesa | 1 | 72 | 2001-12-01 | 518406 | 305 | 518101 | 46.45% | 99.8% | 742.512
TrentMesa | 1 | 73 | 2001-12-01 | 488713 | 627 | 488086 | 43.79% | 99.09% | 737.2296
TrentMesa | 1 | 74 | 2001-12-01 | 466694 | 475 | 466219 | 41.82% | 99.66% | 741.4704
TrentMesa | 1 | 75 | 2001-12-01 | 413250 | 394 | 412856 | 37.03% | 99.04% | 736.8576
TrentMesa | 1 | 76 | 2001-12-01 | 435358 | 611 | 434747 | 39.01% | 87.38% | 650.1072
TrentMesa | 1 | 77 | 2001-12-01 | 366622 | 278 | 366344 | 32.85% | 91.1% | 677.784
TrentMesa | 1 | 78 | 2001-12-01 | 378562 | 429 | 378133 | 33.92% | 91.29% | 679.1976
TrentMesa | 1 | 79 | 2001-12-01 | 454194 | 404 | 453790 | 40.7% | 89.67% | 667.1448
TrentMesa | 1 | 80 | 2001-12-01 | 506108 | 135 | 505973 | 45.35% | 97.86% | 728.0784
TrentMesa | 1 | 81 | 2001-12-01 | 448101 | 497 | 447604 | 40.15% | 90.55% | 673.692
TrentMesa | 1 | 82 | 2001-12-01 | 476688 | 805 | 475883 | 42.71% | 93.78% | 697.7232
TrentMesa | 1 | 83 | 2001-12-01 | 486339 | 374 | 485965 | 43.58% | 99.56% | 740.7264
TrentMesa | 1 | 84 | 2001-12-01 | 539218 | 143 | 539075 | 48.32% | 99.73% | 741.9912
TrentMesa | 1 | 85 | 2001-12-01 | 381405 | 230 | 381175 | 34.18% | 90.37% | 672.3528
TrentMesa | 1 | 86 | 2001-12-01 | 447772 | 496 | 447276 | 40.12% | 89.81% | 668.1864
TrentMesa | 1 | 87 | 2001-12-01 | 426671 | 588 | 426083 | 38.23% | 93.47% | 695.4168
TrentMesa | 1 | 88 | 2001-12-01 | 452796 | 894 | 451902 | 40.57% | 86.47% | 643.3368
TrentMesa | 1 | 89 | 2001-12-01 | 466872 | 346 | 466526 | 41.83% | 99.86% | 742.9584
TrentMesa | 1 | 90 | 2001-12-01 | 442502 | 326 | 442176 | 39.65% | 98.41% | 732.1704
TrentMesa | 1 | 91 | 2001-12-01 | 499306 | 459 | 498847 | 44.74% | 97.17% | 722.9448
TrentMesa | 1 | 92 | 2001-12-01 | 486629 | 713 | 485916 | 43.6% | 98.54% | 733.1376
TrentMesa | 1 | 93 | 2001-12-01 | 467679 | 153 | 467526 | 41.91% | 95.23% | 708.5112
TrentMesa | 1 | 94 | 2001-12-01 | 464897 | 377 | 464520 | 41.66% | 98.28% | 731.2032
TrentMesa | 1 | 95 | 2001-12-01 | 341216 | 454 | 340762 | 30.57% | 88.3% | 656.952
TrentMesa | 1 | 96 | 2001-12-01 | 475575 | 255 | 475320 | 42.61% | 97.79% | 727.5576
TrentMesa | 1 | 97 | 2001-12-01 | 374342 | 860 | 373482 | 33.54% | 92.24% | 686.2656
TrentMesa | 1 | 98 | 2001-12-01 | 398004 | 419 | 397585 | 35.66% | 84.68% | 630.0192
TrentMesa | 1 | 99 | 2001-12-01 | 393724 | 448 | 393276 | 35.28% | 98.27% | 731.1288
TrentMesa | 1 | 100 | 2001-12-01 | 386797 | 473 | 386324 | 34.66% | 98.26% | 731.0544
|  | Project, Before line losses | 2001-12-01 | 43055253 | 52338.426 | 43002914.574 | 38.58% | 94.35% | 70194.8376
|  | Assumed 2% Line Loss | 2001-12-01 | 861105.06 | 1046.7685 | 860058.2915
|  | Project, After line losses | 2001-12-01 | 42194147.94 | 51291.6575 | 42142856.2825 | 37.81% | 94.35% | 70194.8376
|  | Project, After line losses | Year To Date | 99917767.88 | 346494.1175 | 99573964.8425 | 24.01% | 77.16% | 212625.7349
Notes:
1) Current month availability is based on the Enron availability formula as provided by K. Holtel 06/22/2001. Year-to-date is based on data with two different definitions.
2) SCADA system did not communicate with turbine 99 for the first 19 days of Dec. Production for first 19 days corrected based on production of turbine 98.
Also, turbine 87 production improperly reset to zero in early December. Turbine 87 corrected to include production before reset.
OUTAGES AND CURTAILMENTS IN DEC 2001
Trent Mesa
Grid Availability= |  | 100%
Time Off |  | Time On | Machines Affected | Reason |  |  | Charge | Elapsed Hrs | No of WTG Affected | Lost WTGHrs
No outages reported
0
74400
1