## 10-min Curtailment Periods
Clear Sky Curtailment Worksheet | [9 empty] | Notes: |  | signifies >1500 kW production per turbine
2002-02-01
NOTE: SEE LAST TAB (Problems-Limitations) FOR EXPLANATIONS
Year | Mo | Day | Hour | Min | Hours of curtailment | No of turbines curtailed | No of turbines not curtailed | Wind speed at Site 653 (mph) | Wind speed adjusted to hub-height (mps) | Est production per turbine, (kWh) | Actual Total Production(kWh) | Pro-Rated Total Production(kWh) | Est total curtailed production (kWh) | Wind Speed, mps | EWC 1.5 MW Turbine Power Curve, kW
2002 | 2 | 1 | 0 | 0 | 10 | 9 | 98 |  |  |  | 904.2167 | 987.257 | 83.0403 | 0 | 0
2002 | 2 | 1 | 0 | 10 |  | 9 | 98 |  |  |  | 1410.7667 | 1540.3269 | 129.5602 | 1 | 0
2002 | 2 | 1 | 0 | 20 |  | 9 | 98 |  |  |  | 1367.1 | 1492.65 | 125.55 | 2 | 0
2002 | 2 | 1 | 0 | 30 |  | 9 | 98 |  |  |  | 1453.55 | 1587.0393 | 133.4893 | 3 | 7
2002 | 2 | 1 | 0 | 40 |  | 9 | 98 |  |  |  | 1425.8167 | 1556.759 | 130.9423 | 4 | 32
2002 | 2 | 1 | 0 | 50 |  | 9 | 98 |  |  |  | 1317 | 1437.949 | 120.949 | 5 | 91
2002 | 2 | 1 | 1 | 0 |  | 9 | 98 |  |  |  | 1316.9333 | 1437.8762 | 120.9429 | 6 | 182
2002 | 2 | 1 | 1 | 10 |  | 9 | 98 |  |  |  | 1313.6 | 1434.2367 | 120.6367 | 7 | 307
2002 | 2 | 1 | 1 | 20 |  | 9 | 98 |  |  |  | 1162.1667 | 1268.8963 | 106.7296 | 8 | 472
2002 | 2 | 1 | 1 | 30 |  | 9 | 98 |  |  |  | 1169.4 | 1276.7939 | 107.3939 | 9 | 689
2002 | 2 | 1 | 1 | 40 |  | 9 | 98 |  |  |  | 1109.0667 | 1210.9197 | 101.8531 | 10 | 963
2002 | 2 | 1 | 1 | 50 |  | 9 | 98 |  |  |  | 1039.6667 | 1135.1463 | 95.4796 | 11 | 1232
2002 | 2 | 1 | 2 | 0 |  | 9 | 98 |  |  |  | 963.4833 | 1051.9665 | 88.4832 | 12 | 1406
2002 | 2 | 1 | 2 | 10 |  | 9 | 98 |  |  |  | 1003.4167 | 1095.5672 | 92.1505 | 13 | 1477
2002 | 2 | 1 | 2 | 20 |  | 9 | 98 |  |  |  | 1224.5167 | 1336.9723 | 112.4556 | 14 | 1497
2002 | 2 | 1 | 2 | 30 |  | 9 | 98 |  |  |  | 1177.15 | 1285.2556 | 108.1056 | 15 | 1500
2002 | 2 | 1 | 2 | 40 |  | 9 | 98 |  |  |  | 1197.6167 | 1307.6019 | 109.9852 | 16 | 1500
2002 | 2 | 1 | 2 | 50 |  | 9 | 98 |  |  |  | 968.9167 | 1057.8988 | 88.9821 | 17 | 1500
2002 | 2 | 1 | 3 | 0 |  | 9 | 98 |  |  |  | 788.2667 | 860.6585 | 72.3918 | 18 | 1500
2002 | 2 | 1 | 3 | 10 |  | 9 | 98 |  |  |  | 798.0667 | 871.3585 | 73.2918 | 19 | 1500
2002 | 2 | 1 | 3 | 20 |  | 9 | 98 |  |  |  | 1007.1 | 1099.5888 | 92.4888 | 20 | 1500
2002 | 2 | 1 | 3 | 30 |  | 9 | 98 |  |  |  | 1132.75 | 1236.7781 | 104.0281 | 21 | 1500
2002 | 2 | 1 | 3 | 40 |  | 9 | 98 |  |  |  | 1129.05 | 1232.7383 | 103.6883 | 22 | 1500
2002 | 2 | 1 | 3 | 50 |  | 9 | 98 |  |  |  | 1134.6333 | 1238.8344 | 104.201 | 23 | 1500
2002 | 2 | 1 | 4 | 0 |  | 9 | 98 |  |  |  | 1098.4667 | 1199.3463 | 100.8796 | 24 | 1500
2002 | 2 | 1 | 4 | 10 |  | 9 | 98 |  |  |  | 1197.8667 | 1307.8748 | 110.0082 | 25 | 1500
2002 | 2 | 1 | 4 | 20 |  | 9 | 98 |  |  |  | 1121.1333 | 1224.0946 | 102.9612 | 26 | 0
2002 | 2 | 1 | 4 | 30 |  | 9 | 98 |  |  |  | 1081.9833 | 1181.3491 | 99.3658 | 27 | 0
2002 | 2 | 1 | 4 | 40 |  | 9 | 98 |  |  |  | 1040.2667 | 1135.8014 | 95.5347 | 28 | 0
2002 | 2 | 1 | 4 | 50 |  | 9 | 98 |  |  |  | 918.8667 | 1003.2524 | 84.3857 | 29 | 0
2002 | 2 | 1 | 5 | 0 |  | 9 | 98 |  |  |  | 828.3167 | 904.3866 | 76.0699 | 30 | 0
2002 | 2 | 1 | 5 | 10 |  | 9 | 98 |  |  |  | 822.15 | 897.6536 | 75.5036 | 31 | 0
2002 | 2 | 1 | 5 | 20 |  | 9 | 98 |  |  |  | 810.6333 | 885.0793 | 74.4459 | 32 | 0
2002 | 2 | 1 | 5 | 30 |  | 9 | 98 |  |  |  | 971.5167 | 1060.7376 | 89.2209 | 33 | 0
2002 | 2 | 1 | 5 | 40 |  | 9 | 98 |  |  |  | 961.55 | 1049.8556 | 88.3056 | 34 | 0
2002 | 2 | 1 | 5 | 50 |  | 9 | 98 |  |  |  | 854.7833 | 933.2838 | 78.5005 | 35 | 0
2002 | 2 | 1 | 6 | 0 |  | 9 | 98 |  |  |  | 828.3833 | 904.4594 | 76.076 | 36 | 0
2002 | 2 | 1 | 6 | 10 |  | 9 | 98 |  |  |  | 908 | 991.3878 | 83.3878 | 37 | 0
2002 | 2 | 1 | 6 | 20 |  | 9 | 98 |  |  |  | 1035.1667 | 1130.233 | 95.0663 | 38 | 0
2002 | 2 | 1 | 6 | 30 |  | 9 | 98 |  |  |  | 899.9333 | 982.5803 | 82.6469 | 39 | 0
2002 | 2 | 1 | 6 | 40 |  | 9 | 98 |  |  |  | 1099.25 | 1200.2015 | 100.9515 | 40 | 0
2002 | 2 | 1 | 6 | 50 |  | 9 | 98 |  |  |  | 1072.5167 | 1171.0131 | 98.4964 | 41 | 0
2002 | 2 | 1 | 7 | 0 |  | 9 | 98 |  |  |  | 1028.25 | 1122.6811 | 94.4311 | 42 | 0
2002 | 2 | 1 | 7 | 10 |  | 9 | 98 |  |  |  | 1095.8833 | 1196.5257 | 100.6423 | 43 | 0
2002 | 2 | 1 | 7 | 20 |  | 9 | 98 |  |  |  | 1044.2167 | 1140.1141 | 95.8974 | 44 | 0
2002 | 2 | 1 | 7 | 30 |  | 9 | 98 |  |  |  | 851.3 | 929.4806 | 78.1806 | 45 | 0
2002 | 2 | 1 | 7 | 40 |  | 9 | 98 |  |  |  | 868.2667 | 948.0054 | 79.7388 | 46 | 0
2002 | 2 | 1 | 7 | 50 |  | 9 | 98 |  |  |  | 910.0167 | 993.5896 | 83.573 | 47 | 0
2002 | 2 | 1 | 8 | 0 |  | 9 | 98 |  |  |  | 831.25 | 907.5893 | 76.3393 | 48 | 0
2002 | 2 | 1 | 8 | 10 |  | 9 | 98 |  |  |  | 920.9 | 1005.4724 | 84.5724 | 49 | 0
2002 | 2 | 1 | 8 | 20 |  | 9 | 98 |  |  |  | 845.05 | 922.6566 | 77.6066 | 50 | 0
2002 | 2 | 1 | 8 | 30 |  | 9 | 98 |  |  |  | 770.6333 | 841.4058 | 70.7724 | 51 | 0
2002 | 2 | 1 | 8 | 40 |  | 9 | 98 |  |  |  | 751.2 | 820.1878 | 68.9878 | 52 | 0
2002 | 2 | 1 | 8 | 50 |  | 9 | 98 |  |  |  | 738.8667 | 806.7218 | 67.8551 | 53 | 0
2002 | 2 | 1 | 9 | 0 |  | 9 | 98 |  |  |  | 683.05 | 745.7791 | 62.7291 | 54 | 0
2002 | 2 | 1 | 9 | 10 |  | 9 | 98 |  |  |  | 732.3333 | 799.5884 | 67.2551 | 55 | 0
2002 | 2 | 1 | 9 | 20 |  | 9 | 98 |  |  |  | 722.7 | 789.0704 | 66.3704 | 56 | 0
2002 | 2 | 1 | 9 | 30 |  | 9 | 98 |  |  |  | 713.9333 | 779.4986 | 65.5653 | 57 | 0
2002 | 2 | 1 | 9 | 40 |  | 9 | 98 |  |  |  | 720.7667 | 786.9595 | 66.1929 | 58 | 0
2002 | 2 | 1 | 9 | 50 |  | 9 | 98 |  |  |  | 796.1 | 869.2112 | 73.1112 | 59 | 0
[14 empty] | 60 | 0
2002 | 2 | 5 | 6 | 0 | 13 | 9 | 98 |  |  |  | 2377.4333 | 2595.769 | 218.3357 | 61 | 0
2002 | 2 | 5 | 6 | 10 |  | 9 | 98 |  |  |  | 1814.2667 | 1980.883 | 166.6163 | 62 | 0
2002 | 2 | 5 | 6 | 20 |  | 9 | 98 |  |  |  | 1473.6833 | 1609.0216 | 135.3383 | 63 | 0
2002 | 2 | 5 | 6 | 30 |  | 9 | 98 |  |  |  | 1255.4 | 1370.6918 | 115.2918 | 64 | 0
2002 | 2 | 5 | 6 | 40 |  | 9 | 98 |  |  |  | 1375.85 | 1502.2036 | 126.3536 | 65 | 0
2002 | 2 | 5 | 6 | 50 |  | 9 | 98 |  |  |  | 1582.6 | 1727.9408 | 145.3408 | 66 | 0
2002 | 2 | 5 | 7 | 0 |  | 9 | 98 |  |  |  | 1568.4833 | 1712.5277 | 144.0444 | 67 | 0
2002 | 2 | 5 | 7 | 10 |  | 9 | 98 |  |  |  | 1643.8 | 1794.7612 | 150.9612 | 68 | 0
2002 | 2 | 5 | 7 | 20 |  | 9 | 98 |  |  |  | 1688.4 | 1843.4571 | 155.0571 | 69 | 0
2002 | 2 | 5 | 7 | 30 |  | 9 | 98 |  |  |  | 1535.0167 | 1675.9876 | 140.9709 | 70 | 0
2002 | 2 | 5 | 7 | 40 |  | 9 | 98 |  |  |  | 1727.15 | 1885.7658 | 158.6158 | 71 | 0
2002 | 2 | 5 | 7 | 50 |  | 9 | 98 |  |  |  | 2161.75 | 2360.2781 | 198.5281 | 72 | 0
2002 | 2 | 5 | 8 | 0 |  | 9 | 98 |  |  |  | 2728.3167 | 2978.8764 | 250.5597 | 73 | 0
2002 | 2 | 5 | 8 | 10 |  | 9 | 98 |  |  |  | 3079.8 | 3362.6388 | 282.8388 | 74 | 0
2002 | 2 | 5 | 8 | 20 |  | 9 | 98 |  |  |  | 3571.6 | 3899.6041 | 328.0041 | 75 | 0
2002 | 2 | 5 | 8 | 30 |  | 9 | 98 |  |  |  | 3429.4833 | 3744.4359 | 314.9526 | 76 | 0
2002 | 2 | 5 | 8 | 40 |  | 9 | 98 |  |  |  | 3711.9833 | 4052.8798 | 340.8964 | 77 | 0
2002 | 2 | 5 | 8 | 50 |  | 9 | 98 |  |  |  | 4253.75 | 4644.4005 | 390.6505 | 78 | 0
2002 | 2 | 5 | 9 | 0 |  | 9 | 98 |  |  |  | 4762.15 | 5199.4903 | 437.3403 | 79 | 0
2002 | 2 | 5 | 9 | 10 |  | 9 | 98 |  |  |  | 5327.6333 | 5816.9058 | 489.2724 | 80 | 0
2002 | 2 | 5 | 9 | 20 |  | 9 | 98 |  |  |  | 5829.3 | 6364.6439 | 535.3439 | 81 | 0
2002 | 2 | 5 | 9 | 30 |  | 9 | 98 |  |  |  | 5813.6667 | 6347.5748 | 533.9082 | 82 | 0
2002 | 2 | 5 | 9 | 40 |  | 9 | 98 |  |  |  | 5725.5167 | 6251.3294 | 525.8128 | 83 | 0
2002 | 2 | 5 | 9 | 50 |  | 9 | 98 |  |  |  | 5665.6833 | 6186.0012 | 520.3179 | 84 | 0
2002 | 2 | 5 | 10 | 0 |  | 9 | 98 |  |  |  | 5708.7667 | 6233.0412 | 524.2745 | 85 | 0
2002 | 2 | 5 | 10 | 10 |  | 9 | 98 |  |  |  | 5434.5833 | 5933.6777 | 499.0944 | 86 | 0
2002 | 2 | 5 | 10 | 20 |  | 9 | 98 |  |  |  | 5264.0833 | 5747.5196 | 483.4362 | 87 | 0
2002 | 2 | 5 | 10 | 30 |  | 9 | 98 |  |  |  | 4876.55 | 5324.3964 | 447.8464 | 88 | 0
2002 | 2 | 5 | 10 | 40 |  | 9 | 98 |  |  |  | 4754.7833 | 5191.4471 | 436.6638 | 89 | 0
2002 | 2 | 5 | 10 | 50 |  | 9 | 98 |  |  |  | 4272.1833 | 4664.5267 | 392.3434 | 90 | 0
2002 | 2 | 5 | 11 | 0 |  | 9 | 98 |  |  |  | 3836.4667 | 4188.7952 | 352.3286
2002 | 2 | 5 | 11 | 10 |  | 9 | 98 |  |  |  | 3925.8333 | 4286.369 | 360.5357
2002 | 2 | 5 | 11 | 20 |  | 9 | 98 |  |  |  | 4012.5667 | 4381.0677 | 368.501
2002 | 2 | 5 | 11 | 30 |  | 9 | 98 |  |  |  | 4138.75 | 4518.8393 | 380.0893
2002 | 2 | 5 | 11 | 40 |  | 9 | 98 |  |  |  | 4008.5167 | 4376.6457 | 368.1291
2002 | 2 | 5 | 11 | 50 |  | 9 | 98 |  |  |  | 4063.1333 | 4436.2782 | 373.1449
2002 | 2 | 5 | 12 | 0 |  | 9 | 98 |  |  |  | 4082.7333 | 4457.6782 | 374.9449
2002 | 2 | 5 | 12 | 10 |  | 9 | 98 |  |  |  | 4085.2333 | 4460.4078 | 375.1745
2002 | 2 | 5 | 12 | 20 |  | 9 | 98 |  |  |  | 3750.3333 | 4094.7517 | 344.4184
2002 | 2 | 5 | 12 | 30 |  | 9 | 98 |  |  |  | 3591.8167 | 3921.6774 | 329.8607
2002 | 2 | 5 | 12 | 40 |  | 9 | 98 |  |  |  | 3680.2333 | 4018.2139 | 337.9806
2002 | 2 | 5 | 12 | 50 |  | 9 | 98 |  |  |  | 3673.9167 | 4011.3172 | 337.4005
2002 | 2 | 5 | 13 | 0 |  | 9 | 98 |  |  |  | 3393.4167 | 3705.057 | 311.6403
2002 | 2 | 5 | 13 | 10 |  | 9 | 98 |  |  |  | 3119.7667 | 3406.2759 | 286.5092
2002 | 2 | 5 | 13 | 20 |  | 9 | 98 |  |  |  | 2748.5667 | 3000.9861 | 252.4194
2002 | 2 | 5 | 13 | 30 |  | 9 | 98 |  |  |  | 2509.65 | 2740.1281 | 230.4781
2002 | 2 | 5 | 13 | 40 |  | 9 | 98 |  |  |  | 2293.0667 | 2503.6544 | 210.5878
2002 | 2 | 5 | 13 | 50 |  | 9 | 98 |  |  |  | 2206.55 | 2409.1923 | 202.6423
2002 | 2 | 5 | 14 | 0 |  | 9 | 98 |  |  |  | 2352.1333 | 2568.1456 | 216.0122
2002 | 2 | 5 | 14 | 10 |  | 9 | 98 |  |  |  | 2412.25 | 2633.7832 | 221.5332
2002 | 2 | 5 | 14 | 20 |  | 9 | 98 |  |  |  | 2623.8667 | 2864.834 | 240.9673
2002 | 2 | 5 | 14 | 30 |  | 9 | 98 |  |  |  | 2658.2 | 2902.3204 | 244.1204
2002 | 2 | 5 | 14 | 40 |  | 9 | 98 |  |  |  | 2722.1833 | 2972.1798 | 249.9964
2002 | 2 | 5 | 14 | 50 |  | 9 | 98 |  |  |  | 2896.05 | 3162.0138 | 265.9638
2002 | 2 | 5 | 15 | 0 |  | 9 | 98 |  |  |  | 3085.3333 | 3368.6803 | 283.3469
2002 | 2 | 5 | 15 | 10 |  | 9 | 98 |  |  |  | 3397.3333 | 3709.3333 | 312
2002 | 2 | 5 | 15 | 20 |  | 9 | 98 |  |  |  | 3557.05 | 3883.7179 | 326.6679
2002 | 2 | 5 | 15 | 30 |  | 9 | 98 |  |  |  | 3734.0833 | 4077.0094 | 342.926
2002 | 2 | 5 | 15 | 40 |  | 9 | 98 |  |  |  | 3908.3667 | 4267.2983 | 358.9316
2002 | 2 | 5 | 15 | 50 |  | 9 | 98 |  |  |  | 3899.5167 | 4257.6355 | 358.1189
2002 | 2 | 5 | 16 | 0 |  | 9 | 98 |  |  |  | 4192.4333 | 4577.4527 | 385.0194
2002 | 2 | 5 | 16 | 10 |  | 9 | 98 |  |  |  | 4778.4833 | 5217.3236 | 438.8403
2002 | 2 | 5 | 16 | 20 |  | 9 | 98 |  |  |  | 4567.9167 | 4987.4192 | 419.5026
2002 | 2 | 5 | 16 | 30 |  | 9 | 98 |  |  |  | 4675.5333 | 5104.919 | 429.3857
2002 | 2 | 5 | 16 | 40 |  | 9 | 98 |  |  |  | 4273.9167 | 4666.4192 | 392.5026
2002 | 2 | 5 | 16 | 50 |  | 9 | 98 |  |  |  | 3865.2 | 4220.1673 | 354.9673
2002 | 2 | 5 | 17 | 0 |  | 9 | 98 |  |  |  | 4011.7833 | 4380.2124 | 368.4291
2002 | 2 | 5 | 17 | 10 |  | 9 | 98 |  |  |  | 3824.3167 | 4175.5294 | 351.2128
2002 | 2 | 5 | 17 | 20 |  | 9 | 98 |  |  |  | 3673.4 | 4010.7531 | 337.3531
2002 | 2 | 5 | 17 | 30 |  | 9 | 98 |  |  |  | 3684.9167 | 4023.3274 | 338.4107
2002 | 2 | 5 | 17 | 40 |  | 9 | 98 |  |  |  | 4033 | 4403.3776 | 370.3776
2002 | 2 | 5 | 17 | 50 |  | 9 | 98 |  |  |  | 3843.3 | 4196.2561 | 352.9561
2002 | 2 | 5 | 18 | 0 |  | 9 | 98 |  |  |  | 3835 | 4187.1939 | 352.1939
2002 | 2 | 5 | 18 | 10 |  | 9 | 98 |  |  |  | 3923.45 | 4283.7668 | 360.3168
2002 | 2 | 5 | 18 | 20 |  | 9 | 98 |  |  |  | 4018.4833 | 4387.5277 | 369.0444
2002 | 2 | 5 | 18 | 30 |  | 9 | 98 |  |  |  | 4080.4667 | 4455.2034 | 374.7367
2002 | 2 | 5 | 18 | 40 |  | 9 | 98 |  |  |  | 4273.6833 | 4666.1645 | 392.4811
2002 | 2 | 5 | 18 | 50 |  | 9 | 98 |  |  |  | 4502.4667 | 4915.9585 | 413.4918
2002 | 2 | 5 | 17 | 30 | 4.5 | 21 | 86 |  |  |  | 4102.1167 | 5103.7963 | 1001.6797
2002 | 2 | 5 | 17 | 40 |  | 21 | 86 |  |  |  | 3849.1167 | 4789.0172 | 939.9006
2002 | 2 | 5 | 17 | 50 |  | 21 | 86 |  |  |  | 3808.3167 | 4738.2545 | 929.9378
2002 | 2 | 5 | 18 | 0 |  | 21 | 86 |  |  |  | 3763.1333 | 4682.038 | 918.9047
2002 | 2 | 5 | 18 | 10 |  | 21 | 86 |  |  |  | 3915.9167 | 4872.1289 | 956.2122
2002 | 2 | 5 | 18 | 20 |  | 21 | 86 |  |  |  | 3694.9333 | 4597.1845 | 902.2512
2002 | 2 | 5 | 18 | 30 |  | 21 | 86 |  |  |  | 3856.8167 | 4798.5975 | 941.7808
2002 | 2 | 5 | 18 | 40 |  | 21 | 86 |  |  |  | 4155.2167 | 5169.8626 | 1014.6459
2002 | 2 | 5 | 18 | 50 |  | 21 | 86 |  |  |  | 4514.05 | 5616.318 | 1102.268
2002 | 2 | 5 | 19 | 0 |  | 21 | 86 |  |  |  | 4558.2667 | 5671.3318 | 1113.0651
2002 | 2 | 5 | 19 | 10 |  | 21 | 86 |  |  |  | 4299.3 | 5349.1291 | 1049.8291
2002 | 2 | 5 | 19 | 20 |  | 21 | 86 |  |  |  | 3971.2667 | 4940.9946 | 969.7279
2002 | 2 | 5 | 19 | 30 |  | 21 | 86 |  |  |  | 3437.3833 | 4276.7444 | 839.361
2002 | 2 | 5 | 19 | 40 |  | 21 | 86 |  |  |  | 3098.5 | 3855.1105 | 756.6105
2002 | 2 | 5 | 19 | 50 |  | 21 | 86 |  |  |  | 2815.2333 | 3502.674 | 687.4407
2002 | 2 | 5 | 20 | 0 |  | 21 | 86 |  |  |  | 3000.0167 | 3732.5789 | 732.5622
2002 | 2 | 5 | 20 | 10 |  | 21 | 86 |  |  |  | 3262.2167 | 4058.8045 | 796.5878
2002 | 2 | 5 | 20 | 20 |  | 21 | 86 |  |  |  | 3460.9667 | 4306.0864 | 845.1198
2002 | 2 | 5 | 20 | 30 |  | 21 | 86 |  |  |  | 3677.3333 | 4575.2868 | 897.9535
2002 | 2 | 5 | 20 | 40 |  | 21 | 86 |  |  |  | 3883.6667 | 4832.0039 | 948.3372
2002 | 2 | 5 | 20 | 50 |  | 21 | 86 |  |  |  | 3992.6 | 4967.5372 | 974.9372
2002 | 2 | 5 | 21 | 0 |  | 21 | 86 |  |  |  | 4033.3167 | 5018.1963 | 984.8797
2002 | 2 | 5 | 21 | 10 |  | 21 | 86 |  |  |  | 4155.2167 | 5169.8626 | 1014.6459
2002 | 2 | 5 | 21 | 20 |  | 21 | 86 |  |  |  | 4189.6333 | 5212.6833 | 1023.05
2002 | 2 | 5 | 21 | 30 |  | 21 | 86 |  |  |  | 4154.8 | 5169.3442 | 1014.5442
2002 | 2 | 5 | 21 | 40 |  | 21 | 86 |  |  |  | 4058.9833 | 5050.1304 | 991.1471
2002 | 2 | 5 | 21 | 50 |  | 21 | 86 |  |  |  | 4165.6 | 5182.7814 | 1017.1814
2002 | 2 | 5 | 19 | 0 | 3 | 24 | 83 |  |  |  | 4558.2667 | 5876.3197 | 1318.053
2002 | 2 | 5 | 19 | 10 |  | 24 | 83 |  |  |  | 4299.3 | 5542.4711 | 1243.1711
2002 | 2 | 5 | 19 | 20 |  | 24 | 83 |  |  |  | 3971.2667 | 5119.5847 | 1148.3181
2002 | 2 | 5 | 19 | 30 |  | 24 | 83 |  |  |  | 3437.3833 | 4431.3255 | 993.9422
2002 | 2 | 5 | 19 | 40 |  | 24 | 83 |  |  |  | 3098.5 | 3994.4518 | 895.9518
2002 | 2 | 5 | 19 | 50 |  | 24 | 83 |  |  |  | 2815.2333 | 3629.2767 | 814.0434
2002 | 2 | 5 | 20 | 0 |  | 24 | 83 |  |  |  | 3000.0167 | 3867.4914 | 867.4747
2002 | 2 | 5 | 20 | 10 |  | 24 | 83 |  |  |  | 3262.2167 | 4205.5082 | 943.2916
2002 | 2 | 5 | 20 | 20 |  | 24 | 83 |  |  |  | 3460.9667 | 4461.7281 | 1000.7614
2002 | 2 | 5 | 20 | 30 |  | 24 | 83 |  |  |  | 3677.3333 | 4740.6586 | 1063.3253
2002 | 2 | 5 | 20 | 40 |  | 24 | 83 |  |  |  | 3883.6667 | 5006.6546 | 1122.988
2002 | 2 | 5 | 20 | 50 |  | 24 | 83 |  |  |  | 3992.6 | 5147.0867 | 1154.4867
2002 | 2 | 5 | 21 | 0 |  | 24 | 83 |  |  |  | 4033.3167 | 5199.5769 | 1166.2602
2002 | 2 | 5 | 21 | 10 |  | 24 | 83 |  |  |  | 4155.2167 | 5356.7251 | 1201.5084
2002 | 2 | 5 | 21 | 20 |  | 24 | 83 |  |  |  | 4189.6333 | 5401.0936 | 1211.4602
2002 | 2 | 5 | 21 | 30 |  | 24 | 83 |  |  |  | 4154.8 | 5356.188 | 1201.388
2002 | 2 | 5 | 21 | 40 |  | 24 | 83 |  |  |  | 4058.9833 | 5232.6653 | 1173.6819
2002 | 2 | 5 | 21 | 50 |  | 24 | 83 |  |  |  | 4165.6 | 5370.1108 | 1204.5108
2002 | 2 | 9 | 23 | 0 | 9.5 | 75 | 32 |  |  |  | 9135.0667 | 30545.3792 | 21410.3125
2002 | 2 | 9 | 23 | 10 |  | 75 | 32 |  |  |  | 8805.9833 | 29445.0068 | 20639.0234
2002 | 2 | 9 | 23 | 20 |  | 75 | 32 |  |  |  | 7805.7 | 26100.3094 | 18294.6094
2002 | 2 | 9 | 23 | 30 |  | 75 | 32 |  |  |  | 8104.55 | 27099.5891 | 18995.0391
2002 | 2 | 9 | 23 | 40 |  | 75 | 32 |  |  |  | 7435.9 | 24863.7906 | 17427.8906
2002 | 2 | 9 | 23 | 50 |  | 75 | 32 |  |  |  | 6918.4833 | 23133.6786 | 16215.1953
2002 | 2 | 10 | 0 | 0 |  | 75 | 32 |  |  |  | 6543.5167 | 21879.8839 | 15336.3672
2002 | 2 | 10 | 0 | 10 |  | 75 | 32 |  |  |  | 7089.7667 | 23706.4073 | 16616.6406
2002 | 2 | 10 | 0 | 20 |  | 75 | 32 |  |  |  | 7156.2 | 23928.5438 | 16772.3438
2002 | 2 | 10 | 0 | 30 |  | 75 | 32 |  |  |  | 7091.6333 | 23712.649 | 16621.0156
2002 | 2 | 10 | 0 | 40 |  | 75 | 32 |  |  |  | 6916.5333 | 23127.1583 | 16210.625
2002 | 2 | 10 | 0 | 50 |  | 75 | 32 |  |  |  | 6897.1167 | 23062.2339 | 16165.1172
2002 | 2 | 10 | 1 | 0 |  | 75 | 32 |  |  |  | 7116.7833 | 23796.7443 | 16679.9609
2002 | 2 | 10 | 1 | 10 |  | 75 | 32 |  |  |  | 7209.7 | 24107.4344 | 16897.7344
2002 | 2 | 10 | 1 | 20 |  | 75 | 32 |  |  |  | 7507.6167 | 25103.5932 | 17595.9766
2002 | 2 | 10 | 1 | 30 |  | 75 | 32 |  |  |  | 6657.9333 | 22262.4646 | 15604.5312
2002 | 2 | 10 | 1 | 40 |  | 75 | 32 |  |  |  | 5990.85 | 20031.9047 | 14041.0547
2002 | 2 | 10 | 1 | 50 |  | 75 | 32 |  |  |  | 5810.4333 | 19428.6365 | 13618.2031
2002 | 2 | 10 | 2 | 0 |  | 75 | 32 |  |  |  | 5671.2333 | 18963.1865 | 13291.9531
2002 | 2 | 10 | 2 | 10 |  | 75 | 32 |  |  |  | 5654.0833 | 18905.8411 | 13251.7578
2002 | 2 | 10 | 2 | 20 |  | 75 | 32 |  |  |  | 5119.8333 | 17119.4427 | 11999.6094
2002 | 2 | 10 | 2 | 30 |  | 75 | 32 |  |  |  | 4653.4833 | 15560.0849 | 10906.6016
2002 | 2 | 10 | 2 | 40 |  | 75 | 32 |  |  |  | 4422.1833 | 14786.6755 | 10364.4922
2002 | 2 | 10 | 2 | 50 |  | 75 | 32 |  |  |  | 4085.7167 | 13661.6151 | 9575.8984
2002 | 2 | 10 | 3 | 0 |  | 75 | 32 |  |  |  | 4393.45 | 14690.5984 | 10297.1484
2002 | 2 | 10 | 3 | 10 |  | 75 | 32 |  |  |  | 4693.9 | 15695.2281 | 11001.3281
2002 | 2 | 10 | 3 | 20 |  | 75 | 32 |  |  |  | 4797.95 | 16043.1453 | 11245.1953
2002 | 2 | 10 | 3 | 30 |  | 75 | 32 |  |  |  | 5404.45 | 18071.1297 | 12666.6797
2002 | 2 | 10 | 3 | 40 |  | 75 | 32 |  |  |  | 6699.1 | 22400.1156 | 15701.0156
2002 | 2 | 10 | 3 | 50 |  | 75 | 32 |  |  |  | 6994.5667 | 23388.0823 | 16393.5156
2002 | 2 | 10 | 4 | 0 |  | 75 | 32 |  |  |  | 7260.8833 | 24278.5786 | 17017.6953
2002 | 2 | 10 | 4 | 10 |  | 75 | 32 |  |  |  | 7134.7333 | 23856.7646 | 16722.0312
2002 | 2 | 10 | 4 | 20 |  | 75 | 32 |  |  |  | 7514.7167 | 25127.3339 | 17612.6172
2002 | 2 | 10 | 4 | 30 |  | 75 | 32 |  |  |  | 7941.9667 | 26555.951 | 18613.9844
2002 | 2 | 10 | 4 | 40 |  | 75 | 32 |  |  |  | 8755 | 29274.5312 | 20519.5312
2002 | 2 | 10 | 4 | 50 |  | 75 | 32 |  |  |  | 8283 | 27696.2812 | 19413.2812
2002 | 2 | 10 | 5 | 0 |  | 75 | 32 |  |  |  | 7469.2167 | 24975.1932 | 17505.9766
2002 | 2 | 10 | 5 | 10 |  | 75 | 32 |  |  |  | 7097.9833 | 23733.8818 | 16635.8984
2002 | 2 | 10 | 5 | 20 |  | 75 | 32 |  |  |  | 6647.5833 | 22227.8568 | 15580.2734
2002 | 2 | 10 | 5 | 30 |  | 75 | 32 |  |  |  | 6651.9167 | 22242.3464 | 15590.4297
2002 | 2 | 10 | 5 | 40 |  | 75 | 32 |  |  |  | 6545.9 | 21887.8531 | 15341.9531
2002 | 2 | 10 | 5 | 50 |  | 75 | 32 |  |  |  | 6522.8667 | 21810.8354 | 15287.9688
2002 | 2 | 10 | 6 | 0 |  | 75 | 32 |  |  |  | 5028.7167 | 16814.7714 | 11786.0547
2002 | 2 | 10 | 6 | 10 |  | 75 | 32 |  |  |  | 4889.5167 | 16349.3214 | 11459.8047
2002 | 2 | 10 | 6 | 20 |  | 75 | 32 |  |  |  | 4700.4667 | 15717.1854 | 11016.7188
2002 | 2 | 10 | 6 | 30 |  | 75 | 32 |  |  |  | 4233.8333 | 14156.8802 | 9923.0469
2002 | 2 | 10 | 6 | 40 |  | 75 | 32 |  |  |  | 4100.1667 | 13709.9323 | 9609.7656
2002 | 2 | 10 | 6 | 50 |  | 75 | 32 |  |  |  | 3958.7833 | 13237.1818 | 9278.3984
2002 | 2 | 10 | 7 | 0 |  | 75 | 32 |  |  |  | 3690.2167 | 12339.162 | 8648.9453
2002 | 2 | 10 | 7 | 10 |  | 75 | 32 |  |  |  | 3915.3 | 13091.7844 | 9176.4844
2002 | 2 | 10 | 7 | 20 |  | 75 | 32 |  |  |  | 3774.5833 | 12621.263 | 8846.6797
2002 | 2 | 10 | 7 | 30 |  | 75 | 32 |  |  |  | 3894.7167 | 13022.9589 | 9128.2422
2002 | 2 | 10 | 7 | 40 |  | 75 | 32 |  |  |  | 3931.55 | 13146.1203 | 9214.5703
2002 | 2 | 10 | 7 | 50 |  | 75 | 32 |  |  |  | 3804.1167 | 12720.0151 | 8915.8984
2002 | 2 | 10 | 8 | 0 |  | 75 | 32 |  |  |  | 3733.4167 | 12483.612 | 8750.1953
2002 | 2 | 10 | 8 | 10 |  | 75 | 32 |  |  |  | 3512.7167 | 11745.6464 | 8232.9297
2002 | 2 | 10 | 8 | 20 |  | 75 | 32 |  |  |  | 3734.7 | 12487.9031 | 8753.2031
2002 | 2 | 10 | 10 | 40 | 1.75 | 8 | 99 |  |  |  | 6130.8333 | 6626.2542 | 495.4209
2002 | 2 | 10 | 10 | 50 |  | 8 | 99 |  |  |  | 6917.4333 | 7476.4178 | 558.9845
2002 | 2 | 10 | 11 | 0 |  | 8 | 99 |  |  |  | 6823.05 | 7374.4076 | 551.3576
2002 | 2 | 10 | 11 | 10 |  | 8 | 99 |  |  |  | 6975.6333 | 7539.3209 | 563.6875
2002 | 2 | 10 | 11 | 20 |  | 8 | 99 |  |  |  | 7147.9667 | 7725.5801 | 577.6135
2002 | 2 | 10 | 11 | 30 |  | 8 | 99 |  |  |  | 7364.2833 | 7959.3769 | 595.0936
2002 | 2 | 10 | 11 | 40 |  | 8 | 99 |  |  |  | 7300.05 | 7889.953 | 589.903
2002 | 2 | 10 | 11 | 50 |  | 8 | 99 |  |  |  | 7435.6667 | 8036.5286 | 600.862
2002 | 2 | 10 | 12 | 0 |  | 8 | 99 |  |  |  | 6827.6 | 7379.3253 | 551.7253
2002 | 2 | 10 | 12 | 10 |  | 8 | 99 |  |  |  | 7007.7 | 7573.9788 | 566.2788
2002 | 2 | 10 | 12 | 20 |  | 8 | 99 |  |  |  | 6997.15 | 7562.5763 | 565.4263
2002 | 2 | 14 | 7 | 0 | 17 | 61 | 46 |  |  |  | 5829.9167 | 13560.8931 | 7730.9764
2002 | 2 | 14 | 7 | 10 |  | 61 | 46 |  |  |  | 5362.0333 | 12472.5558 | 7110.5225
2002 | 2 | 14 | 7 | 20 |  | 61 | 46 |  |  |  | 4462.2167 | 10379.504 | 5917.2873
2002 | 2 | 14 | 7 | 30 |  | 61 | 46 |  |  |  | 3508.3667 | 8160.7659 | 4652.3993
2002 | 2 | 14 | 7 | 40 |  | 61 | 46 |  |  |  | 3193.0167 | 7427.2344 | 4234.2178
2002 | 2 | 14 | 7 | 50 |  | 61 | 46 |  |  |  | 3184.3333 | 7407.0362 | 4222.7029
2002 | 2 | 14 | 8 | 0 |  | 61 | 46 |  |  |  | 3536.0333 | 8225.121 | 4689.0877
2002 | 2 | 14 | 8 | 10 |  | 61 | 46 |  |  |  | 3716.8 | 8645.6 | 4928.8
2002 | 2 | 14 | 8 | 20 |  | 61 | 46 |  |  |  | 3723.45 | 8661.0685 | 4937.6185
2002 | 2 | 14 | 8 | 30 |  | 61 | 46 |  |  |  | 3596.65 | 8366.1207 | 4769.4707
2002 | 2 | 14 | 8 | 40 |  | 61 | 46 |  |  |  | 3749.15 | 8720.8489 | 4971.6989
2002 | 2 | 14 | 8 | 50 |  | 61 | 46 |  |  |  | 4022.8333 | 9357.4601 | 5334.6268
2002 | 2 | 14 | 9 | 0 |  | 61 | 46 |  |  |  | 4272.1167 | 9937.3149 | 5665.1982
2002 | 2 | 14 | 9 | 10 |  | 61 | 46 |  |  |  | 4220.5 | 9817.25 | 5596.75
2002 | 2 | 14 | 9 | 20 |  | 61 | 46 |  |  |  | 3962.2 | 9216.4217 | 5254.2217
2002 | 2 | 14 | 9 | 30 |  | 61 | 46 |  |  |  | 3877.4667 | 9019.3246 | 5141.858
2002 | 2 | 14 | 9 | 40 |  | 61 | 46 |  |  |  | 3925.9833 | 9132.1786 | 5206.1953
2002 | 2 | 14 | 9 | 50 |  | 61 | 46 |  |  |  | 4224.2833 | 9826.0504 | 5601.767
2002 | 2 | 14 | 10 | 0 |  | 61 | 46 |  |  |  | 4673.8167 | 10871.704 | 6197.8873
2002 | 2 | 14 | 10 | 10 |  | 61 | 46 |  |  |  | 5103.8833 | 11872.0764 | 6768.1931
2002 | 2 | 14 | 10 | 20 |  | 61 | 46 |  |  |  | 5509.0333 | 12814.4906 | 7305.4572
2002 | 2 | 14 | 10 | 30 |  | 61 | 46 |  |  |  | 5643.6833 | 13127.6982 | 7484.0149
2002 | 2 | 14 | 10 | 40 |  | 61 | 46 |  |  |  | 6039.05 | 14047.3554 | 8008.3054
2002 | 2 | 14 | 10 | 50 |  | 61 | 46 |  |  |  | 6122.6167 | 14241.7388 | 8119.1221
2002 | 2 | 14 | 11 | 0 |  | 61 | 46 |  |  |  | 6674.6667 | 15525.8551 | 8851.1884
2002 | 2 | 14 | 11 | 10 |  | 61 | 46 |  |  |  | 7022.05 | 16333.8989 | 9311.8489
2002 | 2 | 14 | 11 | 20 |  | 61 | 46 |  |  |  | 7322.6167 | 17033.0431 | 9710.4264
2002 | 2 | 14 | 11 | 30 |  | 61 | 46 |  |  |  | 7407.9167 | 17231.4583 | 9823.5417
2002 | 2 | 14 | 11 | 40 |  | 61 | 46 |  |  |  | 7465.3167 | 17364.9757 | 9899.6591
2002 | 2 | 14 | 11 | 50 |  | 61 | 46 |  |  |  | 8640.05 | 20097.5076 | 11457.4576
2002 | 2 | 14 | 12 | 0 |  | 61 | 46 |  |  |  | 9020.8 | 20983.1652 | 11962.3652
2002 | 2 | 14 | 12 | 10 |  | 61 | 46 |  |  |  | 9585.9333 | 22297.7145 | 12711.7812
2002 | 2 | 14 | 12 | 20 |  | 61 | 46 |  |  |  | 9711.4167 | 22589.5996 | 12878.183
2002 | 2 | 14 | 12 | 30 |  | 61 | 46 |  |  |  | 9947.1 | 23137.8196 | 13190.7196
2002 | 2 | 14 | 12 | 40 |  | 61 | 46 |  |  |  | 10323.15 | 24012.5446 | 13689.3946
2002 | 2 | 14 | 12 | 50 |  | 61 | 46 |  |  |  | 10867.3667 | 25278.4399 | 14411.0732
2002 | 2 | 14 | 13 | 0 |  | 61 | 46 |  |  |  | 11267.0167 | 26208.0605 | 14941.0438
2002 | 2 | 14 | 13 | 10 |  | 61 | 46 |  |  |  | 10239.8833 | 23818.8591 | 13578.9757
2002 | 2 | 14 | 13 | 20 |  | 61 | 46 |  |  |  | 9571.2333 | 22263.521 | 12692.2877
2002 | 2 | 14 | 13 | 30 |  | 61 | 46 |  |  |  | 8981.9333 | 20892.758 | 11910.8246
2002 | 2 | 14 | 13 | 40 |  | 61 | 46 |  |  |  | 9004.75 | 20945.8315 | 11941.0815
2002 | 2 | 14 | 13 | 50 |  | 61 | 46 |  |  |  | 9258.65 | 21536.425 | 12277.775
2002 | 2 | 14 | 14 | 0 |  | 61 | 46 |  |  |  | 9113.0333 | 21197.708 | 12084.6746
2002 | 2 | 14 | 14 | 10 |  | 61 | 46 |  |  |  | 8180.5 | 19028.5543 | 10848.0543
2002 | 2 | 14 | 14 | 20 |  | 61 | 46 |  |  |  | 7056.1 | 16413.1022 | 9357.0022
2002 | 2 | 14 | 14 | 30 |  | 61 | 46 |  |  |  | 6691.0667 | 15564.0029 | 8872.9362
2002 | 2 | 14 | 14 | 40 |  | 61 | 46 |  |  |  | 6853.15 | 15941.0228 | 9087.8728
2002 | 2 | 14 | 14 | 50 |  | 61 | 46 |  |  |  | 6931.15 | 16122.4576 | 9191.3076
2002 | 2 | 14 | 15 | 0 |  | 61 | 46 |  |  |  | 7054.1833 | 16408.6438 | 9354.4605
2002 | 2 | 14 | 15 | 10 |  | 61 | 46 |  |  |  | 7143.7333 | 16616.9449 | 9473.2116
2002 | 2 | 14 | 15 | 20 |  | 61 | 46 |  |  |  | 7385.95 | 17180.362 | 9794.412
2002 | 2 | 14 | 15 | 30 |  | 61 | 46 |  |  |  | 7233.3667 | 16825.4399 | 9592.0732
2002 | 2 | 14 | 15 | 40 |  | 61 | 46 |  |  |  | 7115.7833 | 16551.9308 | 9436.1475
2002 | 2 | 14 | 15 | 50 |  | 61 | 46 |  |  |  | 6911.85 | 16077.5641 | 9165.7141
2002 | 2 | 14 | 16 | 0 |  | 61 | 46 |  |  |  | 7076.45 | 16460.438 | 9383.988
2002 | 2 | 14 | 16 | 10 |  | 61 | 46 |  |  |  | 7336.25 | 17064.7554 | 9728.5054
2002 | 2 | 14 | 16 | 20 |  | 61 | 46 |  |  |  | 7375.3667 | 17155.7442 | 9780.3775
2002 | 2 | 14 | 16 | 30 |  | 61 | 46 |  |  |  | 7258.0667 | 16882.8942 | 9624.8275
2002 | 2 | 14 | 16 | 40 |  | 61 | 46 |  |  |  | 7253.4667 | 16872.1942 | 9618.7275
2002 | 2 | 14 | 16 | 50 |  | 61 | 46 |  |  |  | 7313.9167 | 17012.8062 | 9698.8895
2002 | 2 | 14 | 17 | 0 |  | 61 | 46 |  |  |  | 7391.8333 | 17194.0471 | 9802.2138
2002 | 2 | 14 | 17 | 10 |  | 61 | 46 |  |  |  | 7231.45 | 16820.9815 | 9589.5315
2002 | 2 | 14 | 17 | 20 |  | 61 | 46 |  |  |  | 7625.95 | 17738.6228 | 10112.6728
2002 | 2 | 14 | 17 | 30 |  | 61 | 46 |  |  |  | 7607.9833 | 17696.8308 | 10088.8475
2002 | 2 | 14 | 17 | 40 |  | 61 | 46 |  |  |  | 7211.1833 | 16773.8395 | 9562.6562
2002 | 2 | 14 | 17 | 50 |  | 61 | 46 |  |  |  | 7104.3833 | 16525.4134 | 9421.0301
2002 | 2 | 14 | 18 | 0 |  | 61 | 46 |  |  |  | 7347.9 | 17091.8543 | 9743.9543
2002 | 2 | 14 | 18 | 10 |  | 61 | 46 |  |  |  | 8875.1833 | 20644.4482 | 11769.2649
2002 | 2 | 14 | 18 | 20 |  | 61 | 46 |  |  |  | 11040.7167 | 25681.667 | 14640.9504
2002 | 2 | 14 | 18 | 30 |  | 61 | 46 |  |  |  | 11010.9667 | 25612.4659 | 14601.4993
2002 | 2 | 14 | 18 | 40 |  | 61 | 46 |  |  |  | 11217.6 | 26093.113 | 14875.513
2002 | 2 | 14 | 18 | 50 |  | 61 | 46 |  |  |  | 11842.85 | 27547.4989 | 15704.6489
2002 | 2 | 14 | 19 | 0 |  | 61 | 46 |  |  |  | 11903.9167 | 27689.5453 | 15785.6286
2002 | 2 | 14 | 19 | 10 |  | 61 | 46 |  |  |  | 11117.9167 | 25861.2409 | 14743.3243
2002 | 2 | 14 | 19 | 20 |  | 61 | 46 |  |  |  | 9976.4167 | 23206.0127 | 13229.596
2002 | 2 | 14 | 19 | 30 |  | 61 | 46 |  |  |  | 9667.5 | 22487.4457 | 12819.9457
2002 | 2 | 14 | 19 | 40 |  | 61 | 46 |  |  |  | 9824.3667 | 22852.3312 | 13027.9645
2002 | 2 | 14 | 19 | 50 |  | 61 | 46 |  |  |  | 9860.1167 | 22935.4888 | 13075.3721
2002 | 2 | 14 | 20 | 0 |  | 61 | 46 |  |  |  | 9790.2167 | 22772.8953 | 12982.6786
2002 | 2 | 14 | 20 | 10 |  | 61 | 46 |  |  |  | 9283.9333 | 21595.2362 | 12311.3029
2002 | 2 | 14 | 20 | 20 |  | 61 | 46 |  |  |  | 9274.4833 | 21573.2547 | 12298.7714
2002 | 2 | 14 | 20 | 30 |  | 61 | 46 |  |  |  | 9146.7167 | 21276.0583 | 12129.3417
2002 | 2 | 14 | 20 | 40 |  | 61 | 46 |  |  |  | 9059.7 | 21073.65 | 12013.95
2002 | 2 | 14 | 20 | 50 |  | 61 | 46 |  |  |  | 9323.9333 | 21688.2797 | 12364.3464
2002 | 2 | 14 | 21 | 0 |  | 61 | 46 |  |  |  | 9208.25 | 21419.1902 | 12210.9402
2002 | 2 | 14 | 21 | 10 |  | 61 | 46 |  |  |  | 8827.0167 | 20532.4083 | 11705.3917
2002 | 2 | 14 | 21 | 20 |  | 61 | 46 |  |  |  | 8595.9167 | 19994.8496 | 11398.933
2002 | 2 | 14 | 21 | 30 |  | 61 | 46 |  |  |  | 8681.5667 | 20194.079 | 11512.5123
2002 | 2 | 14 | 21 | 40 |  | 61 | 46 |  |  |  | 8310.2167 | 19330.2866 | 11020.0699
2002 | 2 | 14 | 21 | 50 |  | 61 | 46 |  |  |  | 7808.4 | 18163.0174 | 10354.6174
2002 | 2 | 14 | 22 | 0 |  | 61 | 46 |  |  |  | 7748.1333 | 18022.8319 | 10274.6986
2002 | 2 | 14 | 22 | 10 |  | 61 | 46 |  |  |  | 7889.25 | 18351.0815 | 10461.8315
2002 | 2 | 14 | 22 | 20 |  | 61 | 46 |  |  |  | 8173.9667 | 19013.3572 | 10839.3906
2002 | 2 | 14 | 22 | 30 |  | 61 | 46 |  |  |  | 8475.1167 | 19713.8583 | 11238.7417
2002 | 2 | 14 | 22 | 40 |  | 61 | 46 |  |  |  | 8676.45 | 20182.1772 | 11505.7272
2002 | 2 | 14 | 22 | 50 |  | 61 | 46 |  |  |  | 8566.0667 | 19925.4159 | 11359.3493
2002 | 2 | 14 | 23 | 0 |  | 61 | 46 |  |  |  | 8469.2 | 19700.0957 | 11230.8957
2002 | 2 | 14 | 23 | 10 |  | 61 | 46 |  |  |  | 8382.9667 | 19499.5094 | 11116.5428
2002 | 2 | 14 | 23 | 20 |  | 61 | 46 |  |  |  | 8337.0667 | 19392.742 | 11055.6754
2002 | 2 | 14 | 23 | 30 |  | 61 | 46 |  |  |  | 8252.7667 | 19196.6529 | 10943.8862
2002 | 2 | 14 | 23 | 40 |  | 61 | 46 |  |  |  | 8336.0667 | 19390.4159 | 11054.3493
2002 | 2 | 14 | 23 | 50 |  | 61 | 46 |  |  |  | 8419.4667 | 19584.4116 | 11164.9449
2002 | 2 | 15 | 0 | 0 | 6 | 61 | 46 |  |  |  | 8487.95 | 19743.7098 | 11255.7598
2002 | 2 | 15 | 0 | 10 |  | 61 | 46 |  |  |  | 8951.9333 | 20822.9754 | 11871.042
2002 | 2 | 15 | 0 | 20 |  | 61 | 46 |  |  |  | 10957.0333 | 25487.0123 | 14529.979
2002 | 2 | 15 | 0 | 30 |  | 61 | 46 |  |  |  | 11406.3333 | 26532.1232 | 15125.7899
2002 | 2 | 15 | 0 | 40 |  | 61 | 46 |  |  |  | 11315.1667 | 26320.0616 | 15004.8949
2002 | 2 | 15 | 0 | 50 |  | 61 | 46 |  |  |  | 11342.3833 | 26383.3699 | 15040.9866
2002 | 2 | 15 | 1 | 0 |  | 61 | 46 |  |  |  | 11067.5167 | 25744.0062 | 14676.4895
2002 | 2 | 15 | 1 | 10 |  | 61 | 46 |  |  |  | 11531.7 | 26823.737 | 15292.037
2002 | 2 | 15 | 1 | 20 |  | 61 | 46 |  |  |  | 13355.55 | 31066.1707 | 17710.6207
2002 | 2 | 15 | 1 | 30 |  | 61 | 46 |  |  |  | 13029.2667 | 30307.2072 | 17277.9406
2002 | 2 | 15 | 1 | 40 |  | 61 | 46 |  |  |  | 12950.0333 | 30122.9036 | 17172.8703
2002 | 2 | 15 | 1 | 50 |  | 61 | 46 |  |  |  | 12690.7333 | 29519.7493 | 16829.0159
2002 | 2 | 15 | 2 | 0 |  | 61 | 46 |  |  |  | 12345.4 | 28716.4739 | 16371.0739
2002 | 2 | 15 | 2 | 10 |  | 61 | 46 |  |  |  | 11769.0333 | 27375.7949 | 15606.7616
2002 | 2 | 15 | 2 | 20 |  | 61 | 46 |  |  |  | 11401.0333 | 26519.7949 | 15118.7616
2002 | 2 | 15 | 2 | 30 |  | 61 | 46 |  |  |  | 11124.5 | 25876.5543 | 14752.0543
2002 | 2 | 15 | 2 | 40 |  | 61 | 46 |  |  |  | 11002.25 | 25592.1902 | 14589.9402
2002 | 2 | 15 | 2 | 50 |  | 61 | 46 |  |  |  | 11094.2333 | 25806.1514 | 14711.9181
2002 | 2 | 15 | 3 | 0 |  | 61 | 46 |  |  |  | 11010.4667 | 25611.3029 | 14600.8362
2002 | 2 | 15 | 3 | 10 |  | 61 | 46 |  |  |  | 10367.7333 | 24116.2493 | 13748.5159
2002 | 2 | 15 | 3 | 20 |  | 61 | 46 |  |  |  | 10012.0667 | 23288.9377 | 13276.871
2002 | 2 | 15 | 3 | 30 |  | 61 | 46 |  |  |  | 10601.8333 | 24660.7862 | 14058.9529
2002 | 2 | 15 | 3 | 40 |  | 61 | 46 |  |  |  | 9998.25 | 23256.7989 | 13258.5489
2002 | 2 | 15 | 3 | 50 |  | 61 | 46 |  |  |  | 9799.1 | 22793.5587 | 12994.4587
2002 | 2 | 15 | 4 | 0 |  | 61 | 46 |  |  |  | 9764.7 | 22713.5413 | 12948.8413
2002 | 2 | 15 | 4 | 10 |  | 61 | 46 |  |  |  | 9720.1167 | 22609.8366 | 12889.7199
2002 | 2 | 15 | 4 | 20 |  | 61 | 46 |  |  |  | 9497.9833 | 22093.1351 | 12595.1518
2002 | 2 | 15 | 4 | 30 |  | 61 | 46 |  |  |  | 9281.3333 | 21589.1884 | 12307.8551
2002 | 2 | 15 | 4 | 40 |  | 61 | 46 |  |  |  | 8137.6667 | 18928.9203 | 10791.2536
2002 | 2 | 15 | 4 | 50 |  | 61 | 46 |  |  |  | 7521.3833 | 17495.3917 | 9974.0083
2002 | 2 | 15 | 5 | 0 |  | 61 | 46 |  |  |  | 7228.7833 | 16814.7786 | 9585.9953
2002 | 2 | 15 | 5 | 10 |  | 61 | 46 |  |  |  | 7010.8667 | 16307.8855 | 9297.0188
2002 | 2 | 15 | 5 | 20 |  | 61 | 46 |  |  |  | 6644.85 | 15456.4989 | 8811.6489
2002 | 2 | 15 | 5 | 30 |  | 61 | 46 |  |  |  | 5965.8333 | 13877.0471 | 7911.2138
2002 | 2 | 15 | 5 | 40 |  | 61 | 46 |  |  |  | 6060.1167 | 14096.3583 | 8036.2417
2002 | 2 | 15 | 5 | 50 |  | 61 | 46 |  |  |  | 6377.7 | 14835.0848 | 8457.3848
2002 | 2 | 15 | 6 | 0 | 2 | 13 | 94 |  |  |  | 6509.45 | 7409.6931 | 900.2431
2002 | 2 | 15 | 6 | 10 |  | 13 | 94 |  |  |  | 8032.9333 | 9143.8709 | 1110.9376
2002 | 2 | 15 | 6 | 20 |  | 13 | 94 |  |  |  | 9998 | 11380.7021 | 1382.7021
2002 | 2 | 15 | 6 | 30 |  | 13 | 94 |  |  |  | 10112 | 11510.4681 | 1398.4681
2002 | 2 | 15 | 6 | 40 |  | 13 | 94 |  |  |  | 9945.4 | 11320.8277 | 1375.4277
2002 | 2 | 15 | 6 | 50 |  | 13 | 94 |  |  |  | 10010.1833 | 11394.5704 | 1384.3871
2002 | 2 | 15 | 7 | 0 |  | 13 | 94 |  |  |  | 10137.6833 | 11539.7034 | 1402.02
2002 | 2 | 15 | 7 | 10 |  | 13 | 94 |  |  |  | 9664.9667 | 11001.611 | 1336.6443
2002 | 2 | 15 | 7 | 20 |  | 13 | 94 |  |  |  | 9404.3167 | 10704.9137 | 1300.597
2002 | 2 | 15 | 7 | 30 |  | 13 | 94 |  |  |  | 8774.7667 | 9988.2982 | 1213.5316
2002 | 2 | 15 | 7 | 40 |  | 13 | 94 |  |  |  | 8595.3167 | 9784.0307 | 1188.714
2002 | 2 | 15 | 7 | 50 |  | 13 | 94 |  |  |  | 9338.2667 | 10629.7291 | 1291.4624
2002 | 2 | 16 | 21 | 10 | 2.5 | 75 | 32 |  |  |  | 4374.1167 | 14625.9526 | 10251.8359
2002 | 2 | 16 | 21 | 20 |  | 75 | 32 |  |  |  | 4347.2 | 14535.95 | 10188.75
2002 | 2 | 16 | 21 | 30 |  | 75 | 32 |  |  |  | 4287.3667 | 14335.8823 | 10048.5156
2002 | 2 | 16 | 21 | 40 |  | 75 | 32 |  |  |  | 3591.65 | 12009.5797 | 8417.9297
2002 | 2 | 16 | 21 | 50 |  | 75 | 32 |  |  |  | 3409.6167 | 11400.9057 | 7991.2891
2002 | 2 | 16 | 22 | 0 |  | 75 | 32 |  |  |  | 3338 | 11161.4375 | 7823.4375
2002 | 2 | 16 | 22 | 10 |  | 75 | 32 |  |  |  | 3317.8833 | 11094.1724 | 7776.2891
2002 | 2 | 16 | 22 | 20 |  | 75 | 32 |  |  |  | 3616.5167 | 12092.7276 | 8476.2109
2002 | 2 | 16 | 22 | 30 |  | 75 | 32 |  |  |  | 3806.15 | 12726.8141 | 8920.6641
2002 | 2 | 16 | 22 | 40 |  | 75 | 32 |  |  |  | 3812.2 | 12747.0437 | 8934.8438
2002 | 2 | 16 | 22 | 50 |  | 75 | 32 |  |  |  | 4052.15 | 13549.3766 | 9497.2266
2002 | 2 | 16 | 23 | 0 |  | 75 | 32 |  |  |  | 4227.6167 | 14136.0932 | 9908.4766
2002 | 2 | 16 | 23 | 10 |  | 75 | 32 |  |  |  | 4428.7333 | 14808.5771 | 10379.8438
2002 | 2 | 16 | 23 | 20 |  | 75 | 32 |  |  |  | 4559.25 | 15244.9922 | 10685.7422
2002 | 2 | 16 | 23 | 30 |  | 75 | 32 |  |  |  | 4162.0167 | 13916.7432 | 9754.7266
2002 | 2 | 16 | 23 | 40 |  | 75 | 32 |  |  |  | 4345.9167 | 14531.6589 | 10185.7422
2002 | 2 | 18 | 19 | 50 | 3.5 | 33 | 74 |  |  |  | 11671.5833 | 16876.4786 | 5204.8953
2002 | 2 | 18 | 20 | 0 |  | 33 | 74 |  |  |  | 11483.8333 | 16605.0023 | 5121.1689
2002 | 2 | 18 | 20 | 10 |  | 33 | 74 |  |  |  | 11743.2333 | 16980.0806 | 5236.8473
2002 | 2 | 18 | 20 | 20 |  | 33 | 74 |  |  |  | 12356.3333 | 17866.5901 | 5510.2568
2002 | 2 | 18 | 20 | 30 |  | 33 | 74 |  |  |  | 12610.9667 | 18234.7761 | 5623.8095
2002 | 2 | 18 | 20 | 40 |  | 33 | 74 |  |  |  | 12602.0833 | 18221.9313 | 5619.848
2002 | 2 | 18 | 20 | 50 |  | 33 | 74 |  |  |  | 12544.5 | 18138.6689 | 5594.1689
2002 | 2 | 18 | 21 | 0 |  | 33 | 74 |  |  |  | 12394.5167 | 17921.8011 | 5527.2845
2002 | 2 | 18 | 21 | 10 |  | 33 | 74 |  |  |  | 12090.5167 | 17482.2336 | 5391.7169
2002 | 2 | 18 | 21 | 20 |  | 33 | 74 |  |  |  | 12401.6167 | 17932.0673 | 5530.4507
2002 | 2 | 18 | 21 | 30 |  | 33 | 74 |  |  |  | 12157.9833 | 17579.7867 | 5421.8034
2002 | 2 | 18 | 21 | 40 |  | 33 | 74 |  |  |  | 10313.5 | 14912.7635 | 4599.2635
2002 | 2 | 18 | 21 | 50 |  | 33 | 74 |  |  |  | 10726.3333 | 15509.6982 | 4783.3649
2002 | 2 | 18 | 22 | 0 |  | 33 | 74 |  |  |  | 11084.95 | 16028.2385 | 4943.2885
2002 | 2 | 18 | 22 | 10 |  | 33 | 74 |  |  |  | 11105.25 | 16057.5912 | 4952.3412
2002 | 2 | 18 | 22 | 20 |  | 33 | 74 |  |  |  | 11300.6167 | 16340.0809 | 5039.4642
2002 | 2 | 18 | 22 | 30 |  | 33 | 74 |  |  |  | 11028.5167 | 15946.639 | 4918.1223
2002 | 2 | 18 | 22 | 40 |  | 33 | 74 |  |  |  | 11192.3 | 16183.4608 | 4991.1608
2002 | 2 | 18 | 22 | 50 |  | 33 | 74 |  |  |  | 11385.65 | 16463.0345 | 5077.3845
2002 | 2 | 18 | 23 | 0 | 1 | 11 | 96 |  |  |  | 11015.0167 | 12277.154 | 1262.1373
2002 | 2 | 18 | 23 | 10 |  | 11 | 96 |  |  |  | 11569.6833 | 12895.3762 | 1325.6929
2002 | 2 | 18 | 23 | 20 |  | 11 | 96 |  |  |  | 11238.5 | 12526.2448 | 1287.7448
2002 | 2 | 18 | 23 | 30 |  | 11 | 96 |  |  |  | 11097.65 | 12369.2557 | 1271.6057
2002 | 2 | 18 | 23 | 40 |  | 11 | 96 |  |  |  | 10621.6333 | 11838.6955 | 1217.0622
2002 | 2 | 18 | 23 | 50 |  | 11 | 96 |  |  |  | 10169.55 | 11334.8109 | 1165.2609
2002 | 2 | 19 | 2 | 0 | 2.5 | 46 | 61 |  |  |  | 12253.15 | 21493.2303 | 9240.0803
2002 | 2 | 19 | 2 | 10 |  | 46 | 61 |  |  |  | 11839.5 | 20767.6475 | 8928.1475
2002 | 2 | 19 | 2 | 20 |  | 46 | 61 |  |  |  | 11281.95 | 19789.65 | 8507.7
2002 | 2 | 19 | 2 | 30 |  | 46 | 61 |  |  |  | 10625.0833 | 18637.4413 | 8012.3579
2002 | 2 | 19 | 2 | 40 |  | 46 | 61 |  |  |  | 9199.6833 | 16137.1495 | 6937.4661
2002 | 2 | 19 | 2 | 50 |  | 46 | 61 |  |  |  | 7332.9667 | 12862.7448 | 5529.7781
2002 | 2 | 19 | 3 | 0 |  | 46 | 61 |  |  |  | 7195.9833 | 12622.4626 | 5426.4792
2002 | 2 | 19 | 3 | 10 |  | 46 | 61 |  |  |  | 7388.1667 | 12959.571 | 5571.4044
2002 | 2 | 19 | 3 | 20 |  | 46 | 61 |  |  |  | 7316.65 | 12834.1238 | 5517.4738
2002 | 2 | 19 | 3 | 30 |  | 46 | 61 |  |  |  | 7121.6167 | 12492.0161 | 5370.3995
2002 | 2 | 19 | 3 | 40 |  | 46 | 61 |  |  |  | 6292.8 | 11038.1902 | 4745.3902
2002 | 2 | 19 | 3 | 50 |  | 46 | 61 |  |  |  | 6184.2333 | 10847.7536 | 4663.5202
2002 | 2 | 19 | 4 | 0 |  | 46 | 61 |  |  |  | 6606.5833 | 11588.597 | 4982.0137
2002 | 2 | 19 | 4 | 10 |  | 46 | 61 |  |  |  | 6918.35 | 12135.4664 | 5217.1164
2002 | 2 | 19 | 4 | 20 |  | 46 | 61 |  |  |  | 6701.3333 | 11754.7978 | 5053.4645
2002 | 2 | 19 | 4 | 30 | 4 | 52 | 55 |  |  |  | 6398.0833 | 12447.1803 | 6049.097
2002 | 2 | 19 | 4 | 40 |  | 52 | 55 |  |  |  | 5735.9167 | 11158.9652 | 5423.0485
2002 | 2 | 19 | 4 | 50 |  | 52 | 55 |  |  |  | 5445.2167 | 10593.4215 | 5148.2048
2002 | 2 | 19 | 5 | 0 |  | 52 | 55 |  |  |  | 8163.35 | 15881.4264 | 7718.0764
2002 | 2 | 19 | 5 | 10 |  | 52 | 55 |  |  |  | 8408.85 | 16359.0355 | 7950.1855
2002 | 2 | 19 | 5 | 20 |  | 52 | 55 |  |  |  | 6835.05 | 13297.2791 | 6462.2291
2002 | 2 | 19 | 5 | 30 |  | 52 | 55 |  |  |  | 6024.15 | 11719.71 | 5695.56
2002 | 2 | 19 | 5 | 40 |  | 52 | 55 |  |  |  | 5656.8167 | 11005.0797 | 5348.263
2002 | 2 | 19 | 5 | 50 |  | 52 | 55 |  |  |  | 5498.1333 | 10696.3685 | 5198.2352
2002 | 2 | 19 | 6 | 0 |  | 52 | 55 |  |  |  | 5309.2333 | 10328.8721 | 5019.6388
2002 | 2 | 19 | 6 | 10 |  | 52 | 55 |  |  |  | 5564.2167 | 10824.9306 | 5260.7139
2002 | 2 | 19 | 6 | 20 |  | 52 | 55 |  |  |  | 5687.9833 | 11065.713 | 5377.7297
2002 | 2 | 19 | 6 | 30 |  | 52 | 55 |  |  |  | 5147.4667 | 10014.1624 | 4866.6958
2002 | 2 | 19 | 6 | 40 |  | 52 | 55 |  |  |  | 4606.7167 | 8962.1579 | 4355.4412
2002 | 2 | 19 | 6 | 50 |  | 52 | 55 |  |  |  | 4592.5 | 8934.5 | 4342
2002 | 2 | 19 | 7 | 0 |  | 52 | 55 |  |  |  | 4371.6833 | 8504.9112 | 4133.2279
2002 | 2 | 19 | 7 | 10 |  | 52 | 55 |  |  |  | 4809.5 | 9356.6636 | 4547.1636
2002 | 2 | 19 | 7 | 20 |  | 52 | 55 |  |  |  | 5287.8167 | 10287.207 | 4999.3903
2002 | 2 | 19 | 7 | 30 |  | 52 | 55 |  |  |  | 5373.3167 | 10453.5433 | 5080.2267
2002 | 2 | 19 | 7 | 40 |  | 52 | 55 |  |  |  | 6093 | 11853.6545 | 5760.6545
2002 | 2 | 19 | 7 | 50 |  | 52 | 55 |  |  |  | 7431.85 | 14458.3264 | 7026.4764
2002 | 2 | 19 | 8 | 0 |  | 52 | 55 |  |  |  | 8317.6167 | 16181.5452 | 7863.9285
2002 | 2 | 19 | 8 | 10 |  | 52 | 55 |  |  |  | 8696.7667 | 16919.1642 | 8222.3976
2002 | 2 | 19 | 8 | 20 |  | 52 | 55 |  |  |  | 9076.7333 | 17658.3721 | 8581.6388
2002 | 2 | 19 | 8 | 30 | 1.75 | 65 | 42 |  |  |  | 9042.45 | 23036.7179 | 13994.2679
2002 | 2 | 19 | 8 | 40 |  | 65 | 42 |  |  |  | 9240.8 | 23542.0381 | 14301.2381
2002 | 2 | 19 | 8 | 50 |  | 65 | 42 |  |  |  | 10481.65 | 26703.2512 | 16221.6012
2002 | 2 | 19 | 9 | 0 |  | 65 | 42 |  |  |  | 10791.4167 | 27492.4187 | 16701.002
2002 | 2 | 19 | 9 | 10 |  | 65 | 42 |  |  |  | 10850.9833 | 27644.1718 | 16793.1885
2002 | 2 | 19 | 9 | 20 |  | 65 | 42 |  |  |  | 11111.4 | 28307.6143 | 17196.2143
2002 | 2 | 19 | 9 | 30 |  | 65 | 42 |  |  |  | 11166.5667 | 28448.1579 | 17281.5913
2002 | 2 | 19 | 9 | 40 |  | 65 | 42 |  |  |  | 10691.3167 | 27237.402 | 16546.0853
2002 | 2 | 19 | 9 | 50 |  | 65 | 42 |  |  |  | 10946.45 | 27887.3845 | 16940.9345
2002 | 2 | 19 | 10 | 0 |  | 65 | 42 |  |  |  | 11212.1833 | 28564.3718 | 17352.1885
2002 | 2 | 19 | 10 | 10 |  | 65 | 42 |  |  |  | 11209.1167 | 28556.5591 | 17347.4425
2002 | 2 | 19 | 10 | 10 | 4 | 68 | 39 |  |  |  | 11209.1167 | 30753.2175 | 19544.1009
2002 | 2 | 19 | 10 | 20 |  | 68 | 39 |  |  |  | 10935.5667 | 30002.7085 | 19067.1419
2002 | 2 | 19 | 10 | 30 |  | 68 | 39 |  |  |  | 11282.1 | 30953.4538 | 19671.3538
2002 | 2 | 19 | 10 | 40 |  | 68 | 39 |  |  |  | 11255.8833 | 30881.5261 | 19625.6427
2002 | 2 | 19 | 10 | 50 |  | 68 | 39 |  |  |  | 11495.7333 | 31539.5761 | 20043.8427
2002 | 2 | 19 | 11 | 0 |  | 68 | 39 |  |  |  | 12695.5 | 34831.2436 | 22135.7436
2002 | 2 | 19 | 11 | 10 |  | 68 | 39 |  |  |  | 13041.9667 | 35781.806 | 22739.8393
2002 | 2 | 19 | 11 | 20 |  | 68 | 39 |  |  |  | 11718.6333 | 32151.1222 | 20432.4889
2002 | 2 | 19 | 11 | 30 |  | 68 | 39 |  |  |  | 11596.4333 | 31815.8556 | 20219.4222
2002 | 2 | 19 | 11 | 40 |  | 68 | 39 |  |  |  | 11172.6 | 30653.0308 | 19480.4308
2002 | 2 | 19 | 11 | 50 |  | 68 | 39 |  |  |  | 10588.9167 | 29051.6432 | 18462.7265
2002 | 2 | 19 | 12 | 0 |  | 68 | 39 |  |  |  | 12326 | 33817.4872 | 21491.4872
2002 | 2 | 19 | 12 | 10 |  | 68 | 39 |  |  |  | 11685.8667 | 32061.2239 | 20375.3573
2002 | 2 | 19 | 12 | 20 |  | 68 | 39 |  |  |  | 10647.9 | 29213.4692 | 18565.5692
2002 | 2 | 19 | 12 | 30 |  | 68 | 39 |  |  |  | 10572.3 | 29006.0538 | 18433.7538
2002 | 2 | 19 | 12 | 40 |  | 68 | 39 |  |  |  | 10313.65 | 28296.4244 | 17982.7744
2002 | 2 | 19 | 12 | 50 |  | 68 | 39 |  |  |  | 10120.5833 | 27766.7286 | 17646.1453
2002 | 2 | 19 | 13 | 0 |  | 68 | 39 |  |  |  | 10349.8333 | 28395.6966 | 18045.8632
2002 | 2 | 19 | 13 | 10 |  | 68 | 39 |  |  |  | 10693.6 | 29338.8513 | 18645.2513
2002 | 2 | 19 | 13 | 20 |  | 68 | 39 |  |  |  | 10287.55 | 28224.8167 | 17937.2667
2002 | 2 | 19 | 13 | 30 |  | 68 | 39 |  |  |  | 9567.95 | 26250.5295 | 16682.5795
2002 | 2 | 19 | 13 | 40 |  | 68 | 39 |  |  |  | 9757.6333 | 26770.9427 | 17013.3094
2002 | 2 | 19 | 13 | 50 |  | 68 | 39 |  |  |  | 9262.1333 | 25411.494 | 16149.3607
2002 | 2 | 19 | 14 | 0 |  | 68 | 39 |  |  |  | 8631.4833 | 23681.2491 | 15049.7658
2002 | 2 | 19 | 14 | 10 | 1.75 | 61 | 46 |  |  |  | 8564.6167 | 19922.0431 | 11357.4264
2002 | 2 | 19 | 14 | 20 |  | 61 | 46 |  |  |  | 8685.7167 | 20203.7322 | 11518.0156
2002 | 2 | 19 | 14 | 30 |  | 61 | 46 |  |  |  | 9195.8833 | 21390.4243 | 12194.5409
2002 | 2 | 19 | 14 | 40 |  | 61 | 46 |  |  |  | 9484.9167 | 22062.7409 | 12577.8243
2002 | 2 | 19 | 14 | 50 |  | 61 | 46 |  |  |  | 9177.4333 | 21347.508 | 12170.0746
2002 | 2 | 19 | 15 | 0 |  | 61 | 46 |  |  |  | 8428.5167 | 19605.4627 | 11176.946
2002 | 2 | 19 | 15 | 10 |  | 61 | 46 |  |  |  | 8743.7667 | 20338.7616 | 11594.9949
2002 | 2 | 19 | 15 | 20 |  | 61 | 46 |  |  |  | 9262.2 | 21544.6826 | 12282.4826
2002 | 2 | 19 | 15 | 30 |  | 61 | 46 |  |  |  | 9654.1667 | 22456.4312 | 12802.2645
2002 | 2 | 19 | 15 | 40 |  | 61 | 46 |  |  |  | 9956.65 | 23160.0337 | 13203.3837
2002 | 2 | 19 | 15 | 50 |  | 61 | 46 |  |  |  | 8935.9 | 20785.6804 | 11849.7804
2002 | 2 | 19 | 16 | 0 | 6.5 | 70 | 37 |  |  |  | 8365.7333 | 24192.7964 | 15827.0631
2002 | 2 | 19 | 16 | 10 |  | 70 | 37 |  |  |  | 8217.3333 | 23763.6396 | 15546.3063
2002 | 2 | 19 | 16 | 20 |  | 70 | 37 |  |  |  | 8010.0167 | 23164.1023 | 15154.0856
2002 | 2 | 19 | 16 | 30 |  | 70 | 37 |  |  |  | 8820.2167 | 25507.1131 | 16686.8964
2002 | 2 | 19 | 16 | 40 |  | 70 | 37 |  |  |  | 9069.8 | 26228.8811 | 17159.0811
2002 | 2 | 19 | 16 | 50 |  | 70 | 37 |  |  |  | 8942.15 | 25859.7311 | 16917.5811
2002 | 2 | 19 | 17 | 0 |  | 70 | 37 |  |  |  | 8696.5 | 25149.3378 | 16452.8378
2002 | 2 | 19 | 17 | 10 |  | 70 | 37 |  |  |  | 8552.3167 | 24732.3752 | 16180.0586
2002 | 2 | 19 | 17 | 20 |  | 70 | 37 |  |  |  | 8669.3 | 25070.6784 | 16401.3784
2002 | 2 | 19 | 17 | 30 |  | 70 | 37 |  |  |  | 8729.15 | 25243.7581 | 16514.6081
2002 | 2 | 19 | 17 | 40 |  | 70 | 37 |  |  |  | 8752.9833 | 25312.6815 | 16559.6982
2002 | 2 | 19 | 17 | 50 |  | 70 | 37 |  |  |  | 8560.3833 | 24755.7032 | 16195.3198
2002 | 2 | 19 | 18 | 0 |  | 70 | 37 |  |  |  | 8368.8667 | 24201.8577 | 15832.991
2002 | 2 | 19 | 18 | 10 |  | 70 | 37 |  |  |  | 8515.1833 | 24624.9896 | 16109.8063
2002 | 2 | 19 | 18 | 20 |  | 70 | 37 |  |  |  | 8773.3667 | 25371.6279 | 16598.2613
2002 | 2 | 19 | 18 | 30 |  | 70 | 37 |  |  |  | 8265.7667 | 23903.7036 | 15637.9369
2002 | 2 | 19 | 18 | 40 |  | 70 | 37 |  |  |  | 8103.15 | 23433.4338 | 15330.2838
2002 | 2 | 19 | 18 | 50 |  | 70 | 37 |  |  |  | 8186.4667 | 23674.3766 | 15487.9099
2002 | 2 | 19 | 19 | 0 |  | 70 | 37 |  |  |  | 7948.7167 | 22986.8293 | 15038.1126
2002 | 2 | 19 | 19 | 10 |  | 70 | 37 |  |  |  | 7873.1 | 22768.1541 | 14895.0541
2002 | 2 | 19 | 19 | 20 |  | 70 | 37 |  |  |  | 7938.6333 | 22957.6694 | 15019.036
2002 | 2 | 19 | 19 | 30 |  | 70 | 37 |  |  |  | 7587 | 21940.7838 | 14353.7838
2002 | 2 | 19 | 19 | 40 |  | 70 | 37 |  |  |  | 8032.5167 | 23229.1698 | 15196.6532
2002 | 2 | 19 | 19 | 50 |  | 70 | 37 |  |  |  | 8131.0167 | 23514.0212 | 15383.0045
2002 | 2 | 19 | 20 | 0 |  | 70 | 37 |  |  |  | 7763.5167 | 22451.2509 | 14687.7342
2002 | 2 | 19 | 20 | 10 |  | 70 | 37 |  |  |  | 7909.9833 | 22874.8167 | 14964.8333
2002 | 2 | 19 | 20 | 20 |  | 70 | 37 |  |  |  | 7681.1167 | 22212.959 | 14531.8423
2002 | 2 | 19 | 20 | 30 |  | 70 | 37 |  |  |  | 8165.9333 | 23614.9964 | 15449.0631
2002 | 2 | 19 | 20 | 40 |  | 70 | 37 |  |  |  | 8501.6667 | 24585.9009 | 16084.2342
2002 | 2 | 19 | 20 | 50 |  | 70 | 37 |  |  |  | 8651.2667 | 25018.5279 | 16367.2613
2002 | 2 | 19 | 21 | 0 |  | 70 | 37 |  |  |  | 9608.9167 | 27787.9482 | 18179.0315
2002 | 2 | 19 | 21 | 10 |  | 70 | 37 |  |  |  | 9927.3167 | 28708.7266 | 18781.4099
2002 | 2 | 19 | 21 | 20 |  | 70 | 37 |  |  |  | 9810.7833 | 28371.7248 | 18560.9414
2002 | 2 | 19 | 21 | 30 |  | 70 | 37 |  |  |  | 10637.2 | 30761.6324 | 20124.4324
2002 | 2 | 19 | 21 | 40 |  | 70 | 37 |  |  |  | 10381.95 | 30023.477 | 19641.527
2002 | 2 | 19 | 21 | 50 |  | 70 | 37 |  |  |  | 9865.8667 | 28531.0198 | 18665.1532
2002 | 2 | 19 | 22 | 0 |  | 70 | 37 |  |  |  | 9547.7 | 27610.9162 | 18063.2162
2002 | 2 | 19 | 22 | 10 |  | 70 | 37 |  |  |  | 9838.4 | 28451.5892 | 18613.1892
2002 | 2 | 19 | 22 | 20 |  | 70 | 37 |  |  |  | 9836 | 28444.6486 | 18608.6486
2002 | 2 | 19 | 22 | 30 |  | 70 | 37 |  |  |  | 10291.5833 | 29762.1464 | 19470.5631
2002 | 2 | 19 | 22 | 40 |  | 70 | 37 |  |  |  | 9774.3167 | 28266.2671 | 18491.9505
2002 | 2 | 21 | 0 | 0 | 2 | 9 | 98 |  |  |  | 1729.9667 | 1888.8412 | 158.8745
2002 | 2 | 21 | 0 | 10 |  | 9 | 98 |  |  |  | 1344.4167 | 1467.8835 | 123.4668
2002 | 2 | 21 | 0 | 20 |  | 9 | 98 |  |  |  | 1238.3667 | 1352.0942 | 113.7276
2002 | 2 | 21 | 0 | 30 |  | 9 | 98 |  |  |  | 1147.1833 | 1252.5369 | 105.3536
2002 | 2 | 21 | 0 | 40 |  | 9 | 98 |  |  |  | 1123.9667 | 1227.1881 | 103.2214
2002 | 2 | 21 | 0 | 50 |  | 9 | 98 |  |  |  | 1090.2333 | 1190.3568 | 100.1235
2002 | 2 | 21 | 1 | 0 |  | 9 | 98 |  |  |  | 1283.3 | 1401.1541 | 117.8541
2002 | 2 | 21 | 1 | 10 |  | 9 | 98 |  |  |  | 1522.15 | 1661.9393 | 139.7893
2002 | 2 | 21 | 1 | 20 |  | 9 | 98 |  |  |  | 1695.6167 | 1851.3366 | 155.7199
2002 | 2 | 21 | 1 | 30 |  | 9 | 98 |  |  |  | 2235.0833 | 2440.3461 | 205.2628
2002 | 2 | 21 | 1 | 40 |  | 9 | 98 |  |  |  | 2784.3 | 3040.001 | 255.701
2002 | 2 | 21 | 1 | 50 |  | 9 | 98 |  |  |  | 2808.3333 | 3066.2415 | 257.9082
2002 | 2 | 21 | 2 | 0 | 4 | 26 | 81 |  |  |  | 2137.15 | 2823.1488 | 685.9988
2002 | 2 | 21 | 2 | 10 |  | 26 | 81 |  |  |  | 2854.1167 | 3770.2529 | 916.1362
2002 | 2 | 21 | 2 | 20 |  | 26 | 81 |  |  |  | 3405.0667 | 4498.051 | 1092.9844
2002 | 2 | 21 | 2 | 30 |  | 26 | 81 |  |  |  | 3561.9167 | 4705.2479 | 1143.3313
2002 | 2 | 21 | 2 | 40 |  | 26 | 81 |  |  |  | 3700.4833 | 4888.2928 | 1187.8095
2002 | 2 | 21 | 2 | 50 |  | 26 | 81 |  |  |  | 3977.25 | 5253.8981 | 1276.6481
2002 | 2 | 21 | 3 | 0 |  | 26 | 81 |  |  |  | 3243.45 | 4284.5574 | 1041.1074
2002 | 2 | 21 | 3 | 10 |  | 26 | 81 |  |  |  | 2855.1667 | 3771.6399 | 916.4733
2002 | 2 | 21 | 3 | 20 |  | 26 | 81 |  |  |  | 3778.3 | 4991.0877 | 1212.7877
2002 | 2 | 21 | 3 | 30 |  | 26 | 81 |  |  |  | 4899.0167 | 6471.5405 | 1572.5239
2002 | 2 | 21 | 3 | 40 |  | 26 | 81 |  |  |  | 4654.9333 | 6149.1095 | 1494.1761
2002 | 2 | 21 | 3 | 50 |  | 26 | 81 |  |  |  | 4670.8167 | 6170.0912 | 1499.2745
2002 | 2 | 21 | 4 | 0 |  | 26 | 81 |  |  |  | 5343.3167 | 7058.4553 | 1715.1387
2002 | 2 | 21 | 4 | 10 |  | 26 | 81 |  |  |  | 4862.3333 | 6423.0823 | 1560.749
2002 | 2 | 21 | 4 | 20 |  | 26 | 81 |  |  |  | 4627.9833 | 6113.5088 | 1485.5255
2002 | 2 | 21 | 4 | 30 |  | 26 | 81 |  |  |  | 4967.5167 | 6562.0282 | 1594.5115
2002 | 2 | 21 | 4 | 40 |  | 26 | 81 |  |  |  | 5687.7333 | 7513.4255 | 1825.6922
2002 | 2 | 21 | 4 | 50 |  | 26 | 81 |  |  |  | 5597.15 | 7393.766 | 1796.616
2002 | 2 | 21 | 5 | 0 |  | 26 | 81 |  |  |  | 5407.65 | 7143.4389 | 1735.7889
2002 | 2 | 21 | 5 | 10 |  | 26 | 81 |  |  |  | 6599.8333 | 8718.2984 | 2118.465
2002 | 2 | 21 | 5 | 20 |  | 26 | 81 |  |  |  | 8760.8667 | 11572.9967 | 2812.13
2002 | 2 | 21 | 5 | 30 |  | 26 | 81 |  |  |  | 8296.0333 | 10958.9576 | 2662.9243
2002 | 2 | 21 | 5 | 40 |  | 26 | 81 |  |  |  | 9203.7167 | 12157.9961 | 2954.2794
2002 | 2 | 21 | 5 | 50 |  | 26 | 81 |  |  |  | 9396.85 | 12413.1228 | 3016.2728
2002 | 2 | 21 | 6 | 0 | 0.5 | 39 | 68 |  |  |  | 8049.1833 | 12665.6267 | 4616.4434
2002 | 2 | 21 | 6 | 10 |  | 39 | 68 |  |  |  | 7892.4 | 12418.9235 | 4526.5235
2002 | 2 | 21 | 6 | 20 |  | 39 | 68 |  |  |  | 8281.1 | 13030.5544 | 4749.4544
2002 | 2 | 21 | 6 | 30 | 2 | 31 | 76 |  |  |  | 8179.9333 | 11516.4851 | 3336.5518
2002 | 2 | 21 | 6 | 40 |  | 31 | 76 |  |  |  | 7717.3833 | 10865.2634 | 3147.88
2002 | 2 | 21 | 6 | 50 |  | 31 | 76 |  |  |  | 7203.6333 | 10141.9575 | 2938.3241
2002 | 2 | 21 | 7 | 0 |  | 31 | 76 |  |  |  | 7119.9167 | 10024.0932 | 2904.1765
2002 | 2 | 21 | 7 | 10 |  | 31 | 76 |  |  |  | 6873.5167 | 9677.1879 | 2803.6713
2002 | 2 | 21 | 7 | 20 |  | 31 | 76 |  |  |  | 7090.95 | 9983.3112 | 2892.3612
2002 | 2 | 21 | 7 | 30 |  | 31 | 76 |  |  |  | 8830.4 | 12432.2737 | 3601.8737
2002 | 2 | 21 | 7 | 40 |  | 31 | 76 |  |  |  | 10853.0833 | 15279.9989 | 4426.9156
2002 | 2 | 21 | 7 | 50 |  | 31 | 76 |  |  |  | 11077.05 | 15595.3204 | 4518.2704
2002 | 2 | 21 | 8 | 0 |  | 31 | 76 |  |  |  | 8570.7333 | 12066.6904 | 3495.957
2002 | 2 | 21 | 8 | 10 |  | 31 | 76 |  |  |  | 8692.4833 | 12238.1015 | 3545.6182
2002 | 2 | 21 | 8 | 20 |  | 31 | 76 |  |  |  | 9044.1 | 12733.1408 | 3689.0408
2002 | 2 | 21 | 9 | 40 | 1 | 11 | 96 |  |  |  | 5128.5333 | 5716.1778 | 587.6444
2002 | 2 | 21 | 9 | 50 |  | 11 | 96 |  |  |  | 5203.1833 | 5799.3814 | 596.1981
2002 | 2 | 21 | 10 | 0 |  | 11 | 96 |  |  |  | 5596.5667 | 6237.8399 | 641.2733
2002 | 2 | 21 | 10 | 10 |  | 11 | 96 |  |  |  | 6625.15 | 7384.2818 | 759.1318
2002 | 2 | 21 | 10 | 20 |  | 11 | 96 |  |  |  | 7517.2333 | 8378.583 | 861.3497
2002 | 2 | 21 | 10 | 30 |  | 11 | 96 |  |  |  | 8247.8 | 9192.8604 | 945.0604
2002 | 2 | 21 | 10 | 40 | 1.25 | 27 | 80 |  |  |  | 8280.6167 | 11075.3248 | 2794.7081
2002 | 2 | 21 | 10 | 50 |  | 27 | 80 |  |  |  | 7982.3667 | 10676.4154 | 2694.0487
2002 | 2 | 21 | 11 | 0 |  | 27 | 80 |  |  |  | 7865.2667 | 10519.7942 | 2654.5275
2002 | 2 | 21 | 11 | 10 |  | 27 | 80 |  |  |  | 8179.7 | 10940.3487 | 2760.6487
2002 | 2 | 21 | 11 | 20 |  | 27 | 80 |  |  |  | 10691.0833 | 14299.324 | 3608.2406
2002 | 2 | 21 | 11 | 30 |  | 27 | 80 |  |  |  | 8934.0833 | 11949.3365 | 3015.2531
2002 | 2 | 21 | 11 | 40 |  | 27 | 80 |  |  |  | 7041.75 | 9418.3406 | 2376.5906
2002 | 2 | 21 | 11 | 50 |  | 27 | 80 |  |  |  | 6275.2167 | 8393.1023 | 2117.8856
2002 | 2 | 21 | 12 | 0 | 4.25 | 53 | 54 |  |  |  | 6432.4167 | 12745.7145 | 6313.2978
2002 | 2 | 21 | 12 | 10 |  | 53 | 54 |  |  |  | 5426.0667 | 10751.6506 | 5325.584
2002 | 2 | 21 | 12 | 20 |  | 53 | 54 |  |  |  | 5186.2 | 10276.3593 | 5090.1593
2002 | 2 | 21 | 12 | 30 |  | 53 | 54 |  |  |  | 5883.4167 | 11657.8812 | 5774.4645
2002 | 2 | 21 | 12 | 40 |  | 53 | 54 |  |  |  | 6357.5333 | 12597.3346 | 6239.8012
2002 | 2 | 21 | 12 | 50 |  | 53 | 54 |  |  |  | 5612.7667 | 11121.5932 | 5508.8265
2002 | 2 | 21 | 13 | 0 |  | 53 | 54 |  |  |  | 5438.35 | 10775.9898 | 5337.6398
2002 | 2 | 21 | 13 | 10 |  | 53 | 54 |  |  |  | 6014 | 11916.6296 | 5902.6296
2002 | 2 | 21 | 13 | 20 |  | 53 | 54 |  |  |  | 7721.2833 | 15299.5799 | 7578.2966
2002 | 2 | 21 | 13 | 30 |  | 53 | 54 |  |  |  | 6797.1333 | 13468.3938 | 6671.2605
2002 | 2 | 21 | 13 | 40 |  | 53 | 54 |  |  |  | 6288.4333 | 12460.4142 | 6171.9809
2002 | 2 | 21 | 13 | 50 |  | 53 | 54 |  |  |  | 5444.1 | 10787.3833 | 5343.2833
2002 | 2 | 21 | 14 | 0 |  | 53 | 54 |  |  |  | 6943.2 | 13757.8222 | 6814.6222
2002 | 2 | 21 | 14 | 10 |  | 53 | 54 |  |  |  | 8195.4167 | 16239.0664 | 8043.6497
2002 | 2 | 21 | 14 | 20 |  | 53 | 54 |  |  |  | 7816.65 | 15488.5472 | 7671.8972
2002 | 2 | 21 | 14 | 30 |  | 53 | 54 |  |  |  | 6717.2167 | 13310.0404 | 6592.8238
2002 | 2 | 21 | 14 | 40 |  | 53 | 54 |  |  |  | 6147.25 | 12180.662 | 6033.412
2002 | 2 | 21 | 14 | 50 |  | 53 | 54 |  |  |  | 8077 | 16004.4259 | 7927.4259
2002 | 2 | 21 | 15 | 0 |  | 53 | 54 |  |  |  | 10789.2833 | 21378.7651 | 10589.4818
2002 | 2 | 21 | 15 | 10 |  | 53 | 54 |  |  |  | 9909.9 | 19636.2833 | 9726.3833
2002 | 2 | 21 | 15 | 20 |  | 53 | 54 |  |  |  | 11491.9833 | 22771.1522 | 11279.1688
2002 | 2 | 21 | 15 | 30 |  | 53 | 54 |  |  |  | 11441.0333 | 22670.1957 | 11229.1623
2002 | 2 | 21 | 15 | 40 |  | 53 | 54 |  |  |  | 13105.65 | 25968.6028 | 12862.9528
2002 | 2 | 21 | 15 | 50 |  | 53 | 54 |  |  |  | 12331.9667 | 24435.5636 | 12103.5969
2002 | 2 | 21 | 16 | 0 |  | 53 | 54 |  |  |  | 9379.95 | 18586.1972 | 9206.2472
2002 | 2 | 21 | 16 | 10 | 1.75 | 27 | 80 |  |  |  | 9905.0167 | 13247.9598 | 3342.9431
2002 | 2 | 21 | 16 | 20 |  | 27 | 80 |  |  |  | 10325.6833 | 13810.6015 | 3484.9181
2002 | 2 | 21 | 16 | 30 |  | 27 | 80 |  |  |  | 10270.5833 | 13736.9052 | 3466.3219
2002 | 2 | 21 | 16 | 40 |  | 27 | 80 |  |  |  | 11880.1 | 15889.6337 | 4009.5337
2002 | 2 | 21 | 16 | 50 |  | 27 | 80 |  |  |  | 12195.8333 | 16311.9271 | 4116.0938
2002 | 2 | 21 | 17 | 0 |  | 27 | 80 |  |  |  | 8946.1667 | 11965.4979 | 3019.3312
2002 | 2 | 21 | 17 | 10 |  | 27 | 80 |  |  |  | 7128.95 | 9534.9706 | 2406.0206
2002 | 2 | 21 | 17 | 20 |  | 27 | 80 |  |  |  | 9616.3667 | 12861.8904 | 3245.5237
2002 | 2 | 21 | 17 | 30 |  | 27 | 80 |  |  |  | 11232.55 | 15023.5356 | 3790.9856
2002 | 2 | 21 | 17 | 40 |  | 27 | 80 |  |  |  | 11956.8833 | 15992.3315 | 4035.4481
2002 | 2 | 21 | 17 | 50 |  | 27 | 80 |  |  |  | 13241.6667 | 17710.7292 | 4469.0625
2002 | 2 | 23 | 20 | 10 | 3.75 | 58 | 49 |  |  |  | 1391.7333 | 3039.0912 | 1647.3578
2002 | 2 | 23 | 20 | 20 |  | 58 | 49 |  |  |  | 1911.1333 | 4173.2912 | 2262.1578
2002 | 2 | 23 | 20 | 30 |  | 58 | 49 |  |  |  | 1874.55 | 4093.4051 | 2218.8551
2002 | 2 | 23 | 20 | 40 |  | 58 | 49 |  |  |  | 2250.8667 | 4915.1578 | 2664.2912
2002 | 2 | 23 | 20 | 50 |  | 58 | 49 |  |  |  | 2459.4333 | 5370.5993 | 2911.166
2002 | 2 | 23 | 21 | 0 |  | 58 | 49 |  |  |  | 2113.55 | 4615.3031 | 2501.7531
2002 | 2 | 23 | 21 | 10 |  | 58 | 49 |  |  |  | 1906.6167 | 4163.4282 | 2256.8116
2002 | 2 | 23 | 21 | 20 |  | 58 | 49 |  |  |  | 2045.9833 | 4467.7595 | 2421.7762
2002 | 2 | 23 | 21 | 30 |  | 58 | 49 |  |  |  | 2820.3 | 6158.6143 | 3338.3143
2002 | 2 | 23 | 21 | 40 |  | 58 | 49 |  |  |  | 3350.05 | 7315.4153 | 3965.3653
2002 | 2 | 23 | 21 | 50 |  | 58 | 49 |  |  |  | 3203.3667 | 6995.1068 | 3791.7401
2002 | 2 | 23 | 22 | 0 |  | 58 | 49 |  |  |  | 3136.7667 | 6849.6741 | 3712.9075
2002 | 2 | 23 | 22 | 10 |  | 58 | 49 |  |  |  | 3110.45 | 6792.2071 | 3681.7571
2002 | 2 | 23 | 22 | 20 |  | 58 | 49 |  |  |  | 3158.6333 | 6897.4238 | 3738.7905
2002 | 2 | 23 | 22 | 30 |  | 58 | 49 |  |  |  | 4340.0167 | 9477.1793 | 5137.1626
2002 | 2 | 23 | 22 | 40 |  | 58 | 49 |  |  |  | 5125.15 | 11191.6541 | 6066.5041
2002 | 2 | 23 | 22 | 50 |  | 58 | 49 |  |  |  | 5890.85 | 12863.6929 | 6972.8429
2002 | 2 | 23 | 23 | 0 |  | 58 | 49 |  |  |  | 6454.5833 | 14094.7024 | 7640.119
2002 | 2 | 23 | 23 | 10 |  | 58 | 49 |  |  |  | 6936.8 | 15147.7061 | 8210.9061
2002 | 2 | 23 | 23 | 20 |  | 58 | 49 |  |  |  | 8395.6333 | 18333.3218 | 9937.6884
2002 | 2 | 23 | 23 | 30 |  | 58 | 49 |  |  |  | 9591.7 | 20945.1408 | 11353.4408
2002 | 2 | 23 | 23 | 40 |  | 58 | 49 |  |  |  | 10806.6833 | 23598.2677 | 12791.5844
2002 | 2 | 23 | 23 | 50 |  | 58 | 49 |  |  |  | 12060.75 | 26336.7398 | 14275.9898
2002 | 2 | 24 | 0 | 0 | 6.5 | 58 | 49 |  |  |  | 12747.75 | 27836.9235 | 15089.1735
2002 | 2 | 24 | 0 | 10 |  | 58 | 49 |  |  |  | 13772.4833 | 30074.6065 | 16302.1231
2002 | 2 | 24 | 0 | 20 |  | 58 | 49 |  |  |  | 14062.6167 | 30708.1629 | 16645.5463
2002 | 2 | 24 | 0 | 30 |  | 58 | 49 |  |  |  | 14997.5167 | 32749.6793 | 17752.1626
2002 | 2 | 24 | 0 | 40 |  | 58 | 49 |  |  |  | 15063.2667 | 32893.2558 | 17829.9891
2002 | 2 | 24 | 0 | 50 |  | 58 | 49 |  |  |  | 16154.8333 | 35276.881 | 19122.0476
2002 | 2 | 24 | 1 | 0 |  | 58 | 49 |  |  |  | 17682.3833 | 38612.5514 | 20930.168
2002 | 2 | 24 | 1 | 10 |  | 58 | 49 |  |  |  | 18922.4167 | 41320.3793 | 22397.9626
2002 | 2 | 24 | 1 | 20 |  | 58 | 49 |  |  |  | 18961.6 | 41405.9429 | 22444.3429
2002 | 2 | 24 | 1 | 30 |  | 58 | 49 |  |  |  | 19519.1167 | 42623.3772 | 23104.2605
2002 | 2 | 24 | 1 | 40 |  | 58 | 49 |  |  |  | 20167.35 | 44038.9071 | 23871.5571
2002 | 2 | 24 | 1 | 50 |  | 58 | 49 |  |  |  | 20140.1833 | 43979.584 | 23839.4007
2002 | 2 | 24 | 2 | 0 |  | 58 | 49 |  |  |  | 20102.7833 | 43897.9146 | 23795.1313
2002 | 2 | 24 | 2 | 10 |  | 58 | 49 |  |  |  | 20619.6333 | 45026.5463 | 24406.9129
2002 | 2 | 24 | 2 | 20 |  | 58 | 49 |  |  |  | 20988.7833 | 45832.6493 | 24843.866
2002 | 2 | 24 | 2 | 30 |  | 58 | 49 |  |  |  | 18233.6167 | 39816.265 | 21582.6483
2002 | 2 | 24 | 2 | 40 |  | 58 | 49 |  |  |  | 14300.2333 | 31227.0401 | 16926.8068
2002 | 2 | 24 | 2 | 50 |  | 58 | 49 |  |  |  | 13770.3833 | 30070.0207 | 16299.6374
2002 | 2 | 24 | 3 | 0 |  | 58 | 49 |  |  |  | 14175.6667 | 30955.0272 | 16779.3605
2002 | 2 | 24 | 3 | 10 |  | 58 | 49 |  |  |  | 14278.7833 | 31180.2003 | 16901.417
2002 | 2 | 24 | 3 | 20 |  | 58 | 49 |  |  |  | 14350.6 | 31337.0245 | 16986.4245
2002 | 2 | 24 | 3 | 30 |  | 58 | 49 |  |  |  | 14062.0167 | 30706.8527 | 16644.8361
2002 | 2 | 24 | 3 | 40 |  | 58 | 49 |  |  |  | 14139.4333 | 30875.9054 | 16736.4721
2002 | 2 | 24 | 3 | 50 |  | 58 | 49 |  |  |  | 14489.3333 | 31639.9728 | 17150.6395
2002 | 2 | 24 | 4 | 0 |  | 58 | 49 |  |  |  | 14378.3 | 31397.5122 | 17019.2122
2002 | 2 | 24 | 4 | 10 |  | 58 | 49 |  |  |  | 14178.5333 | 30961.2871 | 16782.7537
2002 | 2 | 24 | 4 | 20 |  | 58 | 49 |  |  |  | 14071 | 30726.4694 | 16655.4694
2002 | 2 | 24 | 4 | 30 |  | 58 | 49 |  |  |  | 14267.3833 | 31155.3065 | 16887.9231
2002 | 2 | 24 | 4 | 40 |  | 58 | 49 |  |  |  | 14472.05 | 31602.2316 | 17130.1816
2002 | 2 | 24 | 4 | 50 |  | 58 | 49 |  |  |  | 14494.9833 | 31652.3105 | 17157.3272
2002 | 2 | 24 | 5 | 0 |  | 58 | 49 |  |  |  | 14833.55 | 32391.6296 | 17558.0796
2002 | 2 | 24 | 5 | 10 |  | 58 | 49 |  |  |  | 14942.15 | 32628.7765 | 17686.6265
2002 | 2 | 24 | 5 | 20 |  | 58 | 49 |  |  |  | 14758.7 | 32228.1816 | 17469.4816
2002 | 2 | 24 | 5 | 30 |  | 58 | 49 |  |  |  | 14656.55 | 32005.1194 | 17348.5694
2002 | 2 | 24 | 5 | 40 |  | 58 | 49 |  |  |  | 14715.4667 | 32133.7741 | 17418.3075
2002 | 2 | 24 | 5 | 50 |  | 58 | 49 |  |  |  | 14440.7333 | 31533.8463 | 17093.1129
2002 | 2 | 24 | 6 | 0 |  | 58 | 49 |  |  |  | 14595.95 | 31872.7888 | 17276.8388
2002 | 2 | 24 | 6 | 10 |  | 58 | 49 |  |  |  | 14666.0833 | 32025.9371 | 17359.8537
2002 | 2 | 24 | 6 | 20 |  | 58 | 49 |  |  |  | 14654.35 | 32000.3153 | 17345.9653
2002 | 2 | 24 | 6 | 30 |  | 58 | 49 |  |  |  | 14743.7 | 32195.4265 | 17451.7265
2002 | 2 | 24 | 6 | 40 |  | 58 | 49 |  |  |  | 15014.7 | 32787.202 | 17772.502
2002 | 2 | 24 | 6 | 50 |  | 58 | 49 |  |  |  | 15055.1833 | 32875.6044 | 17820.4211
2002 | 2 | 24 | 7 | 0 |  | 58 | 49 |  |  |  | 15158.0667 | 33100.268 | 17942.2014
2002 | 2 | 24 | 7 | 10 |  | 58 | 49 |  |  |  | 15128.9167 | 33036.6139 | 17907.6973
2002 | 2 | 24 | 7 | 20 |  | 58 | 49 |  |  |  | 14878.4167 | 32489.6037 | 17611.1871
2002 | 2 | 24 | 7 | 30 |  | 58 | 49 |  |  |  | 15164.2333 | 33113.734 | 17949.5007
2002 | 2 | 24 | 7 | 40 |  | 58 | 49 |  |  |  | 15209.3333 | 33212.2177 | 18002.8844
2002 | 2 | 24 | 7 | 50 |  | 58 | 49 |  |  |  | 15339.0333 | 33495.4401 | 18156.4068
2002 | 2 | 24 | 8 | 0 |  | 58 | 49 |  |  |  | 15051.3333 | 32867.1973 | 17815.8639
2002 | 2 | 24 | 8 | 10 |  | 58 | 49 |  |  |  | 14906.9333 | 32551.8748 | 17644.9415
2002 | 2 | 24 | 8 | 20 |  | 58 | 49 |  |  |  | 14938.2167 | 32620.1874 | 17681.9707
2002 | 2 | 24 | 8 | 30 |  | 58 | 49 |  |  |  | 15243.7667 | 33287.4088 | 18043.6422
2002 | 2 | 24 | 8 | 40 |  | 58 | 49 |  |  |  | 15370.4833 | 33564.1167 | 18193.6333
2002 | 2 | 24 | 8 | 50 |  | 58 | 49 |  |  |  | 15376.2 | 33576.6 | 18200.4
2002 | 2 | 24 | 9 | 0 |  | 58 | 49 |  |  |  | 15359.8167 | 33540.8241 | 18181.0075
2002 | 2 | 24 | 9 | 10 |  | 58 | 49 |  |  |  | 15263.7 | 33330.9367 | 18067.2367
2002 | 2 | 24 | 9 | 20 |  | 58 | 49 |  |  |  | 15064.6333 | 32896.2401 | 17831.6068
2002 | 2 | 24 | 9 | 30 |  | 58 | 49 |  |  |  | 15099.5333 | 32972.4503 | 17872.917
2002 | 2 | 24 | 9 | 40 |  | 58 | 49 |  |  |  | 15313.2833 | 33439.2105 | 18125.9272
2002 | 2 | 24 | 9 | 50 |  | 58 | 49 |  |  |  | 15294.9667 | 33399.2129 | 18104.2463
2002 | 2 | 24 | 10 | 0 |  | 58 | 49 |  |  |  | 15002.4667 | 32760.4884 | 17758.0218
2002 | 2 | 24 | 10 | 10 |  | 58 | 49 |  |  |  | 14983.9167 | 32719.9813 | 17736.0646
2002 | 2 | 24 | 10 | 20 |  | 58 | 49 |  |  |  | 15114.55 | 33005.2418 | 17890.6918
2002 | 2 | 24 | 10 | 30 |  | 58 | 49 |  |  |  | 14926.95 | 32595.5847 | 17668.6347
2002 | 2 | 24 | 10 | 40 |  | 58 | 49 |  |  |  | 14978.8167 | 32708.8446 | 17730.0279
2002 | 2 | 24 | 10 | 50 |  | 58 | 49 |  |  |  | 14975.3667 | 32701.3109 | 17725.9442
2002 | 2 | 24 | 11 | 0 |  | 58 | 49 |  |  |  | 14672.35 | 32039.6214 | 17367.2714
2002 | 2 | 24 | 11 | 10 |  | 58 | 49 |  |  |  | 14056.15 | 30694.0418 | 16637.8918
2002 | 2 | 24 | 11 | 20 |  | 58 | 49 |  |  |  | 14440.4833 | 31533.3003 | 17092.817
2002 | 2 | 24 | 11 | 30 |  | 58 | 49 |  |  |  | 15007.1833 | 32770.7881 | 17763.6048
2002 | 2 | 24 | 11 | 40 |  | 58 | 49 |  |  |  | 15098.6833 | 32970.5942 | 17871.9109
2002 | 2 | 24 | 11 | 50 |  | 58 | 49 |  |  |  | 14871.5167 | 32474.5364 | 17603.0197
2002 | 2 | 24 | 12 | 0 |  | 58 | 49 |  |  |  | 14908.5333 | 32555.3687 | 17646.8354
2002 | 2 | 24 | 12 | 10 |  | 58 | 49 |  |  |  | 15029.1 | 32818.6469 | 17789.5469
2002 | 2 | 24 | 12 | 20 |  | 58 | 49 |  |  |  | 14645.7 | 31981.4265 | 17335.7265
2002 | 2 | 24 | 12 | 30 |  | 58 | 49 |  |  |  | 14516.0833 | 31698.3861 | 17182.3027
2002 | 2 | 24 | 12 | 40 |  | 58 | 49 |  |  |  | 13309.4 | 29063.3837 | 15753.9837
2002 | 2 | 24 | 12 | 50 |  | 58 | 49 |  |  |  | 9538.5 | 20828.9694 | 11290.4694
2002 | 2 | 24 | 13 | 0 |  | 58 | 49 |  |  |  | 8305.65 | 18136.8276 | 9831.1776
2002 | 2 | 24 | 13 | 10 |  | 58 | 49 |  |  |  | 8460.1333 | 18474.1687 | 10014.0354
2002 | 2 | 24 | 13 | 20 |  | 58 | 49 |  |  |  | 7958.9 | 17379.6388 | 9420.7388
2002 | 2 | 24 | 13 | 30 |  | 58 | 49 |  |  |  | 8152.8 | 17803.0531 | 9650.2531
2002 | 2 | 24 | 13 | 40 |  | 58 | 49 |  |  |  | 8493.0667 | 18546.0844 | 10053.0177
2002 | 2 | 24 | 13 | 50 |  | 58 | 49 |  |  |  | 8287.4167 | 18097.0119 | 9809.5952
2002 | 2 | 24 | 14 | 0 |  | 58 | 49 |  |  |  | 7844.4333 | 17129.681 | 9285.2476
2002 | 2 | 24 | 14 | 10 |  | 58 | 49 |  |  |  | 8108.1 | 17705.4429 | 9597.3429
2002 | 2 | 24 | 14 | 20 |  | 58 | 49 |  |  |  | 7888.5167 | 17225.9446 | 9337.4279
2002 | 2 | 24 | 14 | 30 |  | 58 | 49 |  |  |  | 7473.9 | 16320.5571 | 8846.6571
2002 | 2 | 24 | 14 | 40 |  | 58 | 49 |  |  |  | 7693.5167 | 16800.1282 | 9106.6116
2002 | 2 | 24 | 14 | 50 |  | 58 | 49 |  |  |  | 8018.1 | 17508.9122 | 9490.8122
2002 | 2 | 24 | 15 | 0 |  | 58 | 49 |  |  |  | 8027.8833 | 17530.2759 | 9502.3925
2002 | 2 | 24 | 15 | 10 |  | 58 | 49 |  |  |  | 8081.5333 | 17647.4299 | 9565.8966
2002 | 2 | 24 | 15 | 20 |  | 58 | 49 |  |  |  | 7921.7167 | 17298.4425 | 9376.7259
2002 | 2 | 24 | 15 | 30 |  | 58 | 49 |  |  |  | 7628.8833 | 16658.9901 | 9030.1068
2002 | 2 | 24 | 15 | 40 |  | 58 | 49 |  |  |  | 7449.0667 | 16266.3293 | 8817.2626
2002 | 2 | 24 | 15 | 50 |  | 58 | 49 |  |  |  | 7403.6833 | 16167.2269 | 8763.5435
2002 | 2 | 24 | 16 | 0 |  | 58 | 49 |  |  |  | 7684.4333 | 16780.2932 | 9095.8599
2002 | 2 | 24 | 16 | 10 |  | 58 | 49 |  |  |  | 7482.9833 | 16340.3922 | 8857.4088
2002 | 2 | 24 | 16 | 20 |  | 58 | 49 |  |  |  | 7664.9333 | 16737.7116 | 9072.7782
2002 | 2 | 24 | 16 | 30 |  | 58 | 49 |  |  |  | 7436.5667 | 16239.0333 | 8802.4667
2002 | 2 | 24 | 16 | 40 |  | 58 | 49 |  |  |  | 6945.45 | 15166.5949 | 8221.1449
2002 | 2 | 24 | 16 | 50 |  | 58 | 49 |  |  |  | 6961.4667 | 15201.5701 | 8240.1034
2002 | 2 | 24 | 17 | 0 |  | 58 | 49 |  |  |  | 6691.35 | 14611.7235 | 7920.3735
2002 | 2 | 24 | 17 | 10 |  | 58 | 49 |  |  |  | 6289.4 | 13733.9959 | 7444.5959
2002 | 2 | 24 | 17 | 20 |  | 58 | 49 |  |  |  | 5902.8 | 12889.7878 | 6986.9878
2002 | 2 | 24 | 17 | 30 |  | 58 | 49 |  |  |  | 5937.1833 | 12964.8697 | 7027.6864
2002 | 2 | 24 | 17 | 40 |  | 58 | 49 |  |  |  | 5590.2167 | 12207.2078 | 6616.9912
2002 | 2 | 24 | 17 | 50 |  | 58 | 49 |  |  |  | 4148.8167 | 9059.6609 | 4910.8442
2002 | 2 | 24 | 18 | 0 |  | 58 | 49 |  |  |  | 3735.4167 | 8156.9303 | 4421.5136
2002 | 2 | 24 | 18 | 10 |  | 58 | 49 |  |  |  | 3929.2 | 8580.0898 | 4650.8898
2002 | 2 | 24 | 18 | 20 |  | 58 | 49 |  |  |  | 4225.25 | 9226.5663 | 5001.3163
2002 | 2 | 25 | 4 | 30 | 4 | 30 | 77 |  |  |  | 10073.4167 | 13998.1245 | 3924.7078
2002 | 2 | 25 | 4 | 40 |  | 30 | 77 |  |  |  | 10627.9333 | 14768.6866 | 4140.7532
2002 | 2 | 25 | 4 | 50 |  | 30 | 77 |  |  |  | 11113.8 | 15443.8519 | 4330.0519
2002 | 2 | 25 | 5 | 0 |  | 30 | 77 |  |  |  | 11396.45 | 15836.6253 | 4440.1753
2002 | 2 | 25 | 5 | 10 |  | 30 | 77 |  |  |  | 10928.9667 | 15187.0056 | 4258.039
2002 | 2 | 25 | 5 | 20 |  | 30 | 77 |  |  |  | 10897.8 | 15143.6961 | 4245.8961
2002 | 2 | 25 | 5 | 30 |  | 30 | 77 |  |  |  | 10331.0667 | 14356.1576 | 4025.0909
2002 | 2 | 25 | 5 | 40 |  | 30 | 77 |  |  |  | 9724.75 | 13513.6136 | 3788.8636
2002 | 2 | 25 | 5 | 50 |  | 30 | 77 |  |  |  | 8837.5167 | 12280.705 | 3443.1883
2002 | 2 | 25 | 6 | 0 |  | 30 | 77 |  |  |  | 8454.6333 | 11748.6463 | 3294.013
2002 | 2 | 25 | 6 | 10 |  | 30 | 77 |  |  |  | 7768.75 | 10795.5357 | 3026.7857
2002 | 2 | 25 | 6 | 20 |  | 30 | 77 |  |  |  | 8582.6 | 11926.4701 | 3343.8701
2002 | 2 | 25 | 6 | 30 |  | 30 | 77 |  |  |  | 9347.6833 | 12989.6379 | 3641.9545
2002 | 2 | 25 | 6 | 40 |  | 30 | 77 |  |  |  | 9473.1 | 13163.9182 | 3690.8182
2002 | 2 | 25 | 6 | 50 |  | 30 | 77 |  |  |  | 9187.55 | 12767.1149 | 3579.5649
2002 | 2 | 25 | 7 | 0 |  | 30 | 77 |  |  |  | 9782.9333 | 13594.4658 | 3811.5325
2002 | 2 | 25 | 7 | 10 |  | 30 | 77 |  |  |  | 11581.1667 | 16093.3095 | 4512.1429
2002 | 2 | 25 | 7 | 20 |  | 30 | 77 |  |  |  | 12944.6333 | 17987.997 | 5043.3636
2002 | 2 | 25 | 7 | 30 |  | 30 | 77 |  |  |  | 13185.0167 | 18322.0361 | 5137.0195
2002 | 2 | 25 | 7 | 40 |  | 30 | 77 |  |  |  | 12242.1167 | 17011.7725 | 4769.6558
2002 | 2 | 25 | 7 | 50 |  | 30 | 77 |  |  |  | 9426.05 | 13098.537 | 3672.487
2002 | 2 | 25 | 8 | 0 |  | 30 | 77 |  |  |  | 6438.3 | 8946.7286 | 2508.4286
2002 | 2 | 25 | 8 | 10 |  | 30 | 77 |  |  |  | 6119.1833 | 8503.2807 | 2384.0974
2002 | 2 | 25 | 8 | 20 |  | 30 | 77 |  |  |  | 5834.9167 | 8108.2608 | 2273.3442
2002 | 2 | 25 | 21 | 40 | 1.25 | 91 | 16 |  |  |  | 559.7667 | 3743.4396 | 3183.6729
2002 | 2 | 25 | 21 | 50 |  | 91 | 16 |  |  |  | 527.6333 | 3528.5479 | 3000.9146
2002 | 2 | 25 | 22 | 0 |  | 91 | 16 |  |  |  | 286.75 | 1917.6406 | 1630.8906
2002 | 2 | 25 | 22 | 10 |  | 91 | 16 |  |  |  | 272.6833 | 1823.5698 | 1550.8865
2002 | 2 | 25 | 22 | 20 |  | 91 | 16 |  |  |  | 141.6 | 946.95 | 805.35
2002 | 2 | 25 | 22 | 30 |  | 91 | 16 |  |  |  | 325.8333 | 2179.0104 | 1853.1771
2002 | 2 | 25 | 22 | 40 |  | 91 | 16 |  |  |  | 265.5333 | 1775.7542 | 1510.2208
2002 | 2 | 25 | 22 | 50 |  | 91 | 16 |  |  |  | 198.0667 | 1324.5708 | 1126.5042
2002 | 2 | 25 | 23 | 0 | 1 | 74 | 33 |  |  |  | 45.7 | 148.1788 | 102.4788
2002 | 2 | 25 | 23 | 10 |  | 74 | 33 |  |  |  | 8.15 | 26.4258 | 18.2758
2002 | 2 | 25 | 23 | 20 |  | 74 | 33 |  |  |  | 235.6833 | 764.1854 | 528.502
2002 | 2 | 25 | 23 | 30 |  | 74 | 33 |  |  |  | 376.2667 | 1220.0162 | 843.7495
2002 | 2 | 25 | 23 | 40 |  | 74 | 33 |  |  |  | 285.7333 | 926.4687 | 640.7354
2002 | 2 | 25 | 23 | 50 |  | 74 | 33 |  |  |  | 528.4 | 1713.297 | 1184.897
2002 | 2 | 26 | 0 | 0 | 2.25 | 62 | 45 |  |  |  | 861.6333 | 2048.7726 | 1187.1393
2002 | 2 | 26 | 0 | 10 |  | 62 | 45 |  |  |  | 1416.7 | 3368.5978 | 1951.8978
2002 | 2 | 26 | 0 | 20 |  | 62 | 45 |  |  |  | 1112.7667 | 2645.9119 | 1533.1452
2002 | 2 | 26 | 0 | 30 |  | 62 | 45 |  |  |  | 796.4667 | 1893.8207 | 1097.3541
2002 | 2 | 26 | 0 | 40 |  | 62 | 45 |  |  |  | 921.15 | 2190.29 | 1269.14
2002 | 2 | 26 | 0 | 50 |  | 62 | 45 |  |  |  | 1221.5 | 2904.4556 | 1682.9556
2002 | 2 | 26 | 1 | 0 |  | 62 | 45 |  |  |  | 1762.0667 | 4189.803 | 2427.7363
2002 | 2 | 26 | 1 | 10 |  | 62 | 45 |  |  |  | 2885.0333 | 6859.9681 | 3974.9348
2002 | 2 | 26 | 1 | 20 |  | 62 | 45 |  |  |  | 3636.35 | 8646.4322 | 5010.0822
2002 | 2 | 26 | 1 | 30 |  | 62 | 45 |  |  |  | 3561.4 | 8468.2178 | 4906.8178
2002 | 2 | 26 | 1 | 40 |  | 62 | 45 |  |  |  | 4695.6333 | 11165.1726 | 6469.5393
2002 | 2 | 26 | 1 | 50 |  | 62 | 45 |  |  |  | 6962.8 | 16555.9911 | 9593.1911
2002 | 2 | 26 | 2 | 0 |  | 62 | 45 |  |  |  | 6579.7167 | 15645.1041 | 9065.3874
2002 | 2 | 26 | 2 | 10 |  | 62 | 45 |  |  |  | 6320.15 | 15027.9122 | 8707.7622
2002 | 2 | 26 | 2 | 20 | 2.75 | 20 | 87 |  |  |  | 7655.1167 | 9414.9136 | 1759.7969
2002 | 2 | 26 | 2 | 30 |  | 20 | 87 |  |  |  | 5385.7833 | 6623.8944 | 1238.1111
2002 | 2 | 26 | 2 | 40 |  | 20 | 87 |  |  |  | 4849.4667 | 5964.2866 | 1114.8199
2002 | 2 | 26 | 2 | 50 |  | 20 | 87 |  |  |  | 4747.9833 | 5839.4738 | 1091.4904
2002 | 2 | 26 | 3 | 0 |  | 20 | 87 |  |  |  | 10446.15 | 12847.5638 | 2401.4138
2002 | 2 | 26 | 3 | 10 |  | 20 | 87 |  |  |  | 6477.3167 | 7966.355 | 1489.0383
2002 | 2 | 26 | 3 | 20 |  | 20 | 87 |  |  |  | 9652.3 | 11871.2195 | 2218.9195
2002 | 2 | 26 | 3 | 30 |  | 20 | 87 |  |  |  | 18862.1667 | 23198.2969 | 4336.1303
2002 | 2 | 26 | 3 | 40 |  | 20 | 87 |  |  |  | 18903.05 | 23248.5787 | 4345.5287
2002 | 2 | 26 | 3 | 50 |  | 20 | 87 |  |  |  | 14185.8667 | 17446.9854 | 3261.1188
2002 | 2 | 26 | 4 | 0 |  | 20 | 87 |  |  |  | 4285.75 | 5270.9799 | 985.2299
2002 | 2 | 26 | 4 | 10 |  | 20 | 87 |  |  |  | 3077.8167 | 3785.3607 | 707.5441
2002 | 2 | 26 | 4 | 20 |  | 20 | 87 |  |  |  | 3281.7167 | 4036.1343 | 754.4176
2002 | 2 | 26 | 4 | 30 |  | 20 | 87 |  |  |  | 3209.55 | 3947.3776 | 737.8276
2002 | 2 | 26 | 4 | 40 |  | 20 | 87 |  |  |  | 3269.4333 | 4021.0272 | 751.5939
2002 | 2 | 26 | 4 | 50 |  | 20 | 87 |  |  |  | 3182.7333 | 3914.3962 | 731.6628
2002 | 2 | 26 | 5 | 0 | 1.5 | 20 | 87 |  |  |  | 3162.15 | 3889.081 | 726.931
2002 | 2 | 26 | 5 | 10 |  | 20 | 87 |  |  |  | 4548.9 | 5594.6241 | 1045.7241
2002 | 2 | 26 | 5 | 20 |  | 20 | 87 |  |  |  | 5567.2333 | 6847.0571 | 1279.8238
2002 | 2 | 26 | 5 | 30 |  | 20 | 87 |  |  |  | 5579.9333 | 6862.6766 | 1282.7433
2002 | 2 | 26 | 5 | 40 |  | 20 | 87 |  |  |  | 5942.35 | 7308.4075 | 1366.0575
2002 | 2 | 26 | 5 | 50 |  | 20 | 87 |  |  |  | 6146.9667 | 7560.0625 | 1413.0958
2002 | 2 | 26 | 6 | 0 |  | 20 | 87 |  |  |  | 5844.2833 | 7187.7967 | 1343.5134
2002 | 2 | 26 | 6 | 10 |  | 20 | 87 |  |  |  | 8416.9833 | 10351.922 | 1934.9387
2002 | 2 | 26 | 6 | 20 |  | 20 | 87 |  |  |  | 7143.8 | 8786.0529 | 1642.2529
2002 | 2 | 26 | 6 | 30 | 2.5 | 38 | 69 |  |  |  | 7985.9833 | 12384.0611 | 4398.0778
2002 | 2 | 26 | 6 | 40 |  | 38 | 69 |  |  |  | 8680.3167 | 13460.7809 | 4780.4643
2002 | 2 | 26 | 6 | 50 |  | 38 | 69 |  |  |  | 8991.15 | 13942.7978 | 4951.6478
2002 | 2 | 26 | 7 | 0 |  | 38 | 69 |  |  |  | 8674.05 | 13451.063 | 4777.013
2002 | 2 | 26 | 7 | 10 |  | 38 | 69 |  |  |  | 8508.25 | 13193.9529 | 4685.7029
2002 | 2 | 26 | 7 | 20 |  | 38 | 69 |  |  |  | 7986.1667 | 12384.3454 | 4398.1787
2002 | 2 | 26 | 7 | 30 |  | 38 | 69 |  |  |  | 8183.1167 | 12689.7606 | 4506.644
2002 | 2 | 26 | 7 | 40 |  | 38 | 69 |  |  |  | 7851.5167 | 12175.5403 | 4324.0237
2002 | 2 | 26 | 7 | 50 |  | 38 | 69 |  |  |  | 7903.4 | 12255.9971 | 4352.5971
2002 | 2 | 26 | 8 | 0 |  | 38 | 69 |  |  |  | 7458.85 | 11566.6225 | 4107.7725
2002 | 2 | 26 | 8 | 10 |  | 38 | 69 |  |  |  | 6744.6333 | 10459.0691 | 3714.4357
2002 | 2 | 26 | 8 | 20 |  | 38 | 69 |  |  |  | 6187.7 | 9595.4188 | 3407.7188
2002 | 2 | 26 | 8 | 30 |  | 38 | 69 |  |  |  | 6047.3333 | 9377.7488 | 3330.4155
2002 | 2 | 26 | 8 | 40 |  | 38 | 69 |  |  |  | 6256.0667 | 9701.4367 | 3445.37
2002 | 2 | 26 | 8 | 50 |  | 38 | 69 |  |  |  | 5938.1667 | 9208.4614 | 3270.2947
Note: since all turbines were curtailed during the final curtailment perioe, the wind speed method was used. Also note that CPS promised to pay as if all turbines at full power.
2002 | 2 | 26 | 9 | 0 | 1 | 107 | 0 | 25.27 | 12.5834 | 1447.4213 | 39312.65 | 139386.6717 | 100074.0217
2002 | 2 | 26 | 10 | 0 | 1 | 107 | 0 | 22.97 | 11.4381 | 1308.2286 | 36447.5 | 125982.4118 | 89534.9118
2002 | 2 | 26 | 11 | 0 | 1 | 107 | 0 | 23.18 | 11.5427 | 1326.424 | 36051.4167 | 127734.6274 | 91683.2107
2002 | 2 | 26 | 12 | 0 | 1 | 107 | 0 | 22.43 | 11.1692 | 1261.4404 | 52113.4333 | 121476.7145 | 69363.2812
2002 | 2 | 26 | 13 | 0 | 1 | 107 | 0 | 19.65 | 9.7849 | 904.0557 | 37440.7333 | 87060.5608 | 49619.8275
2002 | 2 | 26 | 14 | 0 | 1 | 107 | 0 | 20.67 | 10.2928 | 1041.761 | 33712.4167 | 100321.5853 | 66609.1686
2002 | 2 | 26 | 15 | 0 | 1 | 107 | 0 | 17.41 | 8.6694 | 617.2704 | 3042.3 | 59443.1381 | 56400.8381
2002 | 2 | 26 | 16 | 0 | 1 | 107 | 0 | 15.27 | 7.6038 | 406.6301 | 2599.25 | 39158.4766 | 36559.2266
2002 | 2 | 26 | 17 | 0 | 1 | 107 | 0 | 13.45 | 6.6975 | 269.1919 | 1896.6333 | 25923.1788 | 24026.5454
2002 | 2 | 26 | 18 | 0 | 1 | 107 | 0 | 10.35 | 5.1539 | 105.0017 | -260.5333 | 10111.6678 | 10372.2011
2002 | 2 | 26 | 19 | 0 | 1 | 107 | 0 | 2.01 | 1.0009 | 0 | 158.1833 | 0 | -158.1833
2002 | 2 | 26 | 20 | 0 | 1 | 107 | 0 | 2.12 | 1.0557 | 0 | 252.95 | 0 | -252.95
2002 | 2 | 26 | 21 | 0 | 0.33333 | 107 | 0 | 4.68 | 2.3304 | 2.3131 | -96.9333 | 74.2499 | 171.1832

## 15-min Curtailment Periods
Clear Sky Curtailment Worksheet
2002-02-01
Year | Mo | Day | Hour | Min | Hours of curtailment | No of turbines curtailed | No of turbines operating | Wind speed at Site 653 (mph) | Wind speed adjusted to hub-height (mps) | Est production per turbine, (kWh) | Actual Total Production(MW) | Pro-Rated Total Production(MW) | Est total curtailed production (MW)
2002 | 2 | 1 | 0 | 0 | 10 | 9 | 98 | Not used for this analysis |  |  | 3.299 | 3.6019 | 0.30297 | 3593.6962
2002 | 2 | 1 | 0 | 15 |  | 9 | 98 |  |  |  | 3.2467 | 3.5448 | 0.29816
2002 | 2 | 1 | 0 | 30 |  | 9 | 98 |  |  |  | 3.1628 | 3.4532 | 0.29046
2002 | 2 | 1 | 0 | 45 |  | 9 | 98 |  |  |  | 2.9971 | 3.2724 | 0.27525
2002 | 2 | 1 | 1 | 0 |  | 9 | 98 |  |  |  | 2.5872 | 2.8248 | 0.2376
2002 | 2 | 1 | 1 | 15 |  | 9 | 98 |  |  |  | 2.1467 | 2.3438 | 0.19714
2002 | 2 | 1 | 1 | 30 |  | 9 | 98 |  |  |  | 2.3542 | 2.5704 | 0.2162
2002 | 2 | 1 | 1 | 45 |  | 9 | 98 |  |  |  | 2.6009 | 2.8397 | 0.23885
2002 | 2 | 1 | 2 | 0 |  | 9 | 98 |  |  |  | 2.4882 | 2.7168 | 0.22851
2002 | 2 | 1 | 2 | 15 |  | 9 | 98 |  |  |  | 2.0611 | 2.2503 | 0.18928
2002 | 2 | 1 | 2 | 30 |  | 9 | 98 |  |  |  | 1.4826 | 1.6188 | 0.13616
2002 | 2 | 1 | 2 | 45 |  | 9 | 98 |  |  |  | 0.82213 | 0.89763 | 0.075502
2002 | 2 | 1 | 3 | 0 |  | 9 | 98 |  |  |  | 0.34214 | 0.37357 | 0.031421
2002 | 2 | 1 | 3 | 15 |  | 9 | 98 |  |  |  | 0.37139 | 0.4055 | 0.034108
2002 | 2 | 1 | 3 | 30 |  | 9 | 98 |  |  |  | 1.1723 | 1.28 | 0.10766
2002 | 2 | 1 | 3 | 45 |  | 9 | 98 |  |  |  | 1.9287 | 2.1059 | 0.17713
2002 | 2 | 1 | 4 | 0 |  | 9 | 98 |  |  |  | 2.2409 | 2.4467 | 0.2058
2002 | 2 | 1 | 4 | 15 |  | 9 | 98 |  |  |  | 1.639 | 1.7895 | 0.15052
2002 | 2 | 1 | 4 | 30 |  | 9 | 98 |  |  |  | 1.1698 | 1.2772 | 0.10743
2002 | 2 | 1 | 4 | 45 |  | 9 | 98 |  |  |  | 0.72321 | 0.78962 | 0.066417
2002 | 2 | 1 | 5 | 0 |  | 9 | 98 |  |  |  | 0.2954 | 0.32253 | 0.027129
2002 | 2 | 1 | 5 | 15 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 5 | 30 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 5 | 45 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 6 | 0 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 6 | 15 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 6 | 30 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 6 | 45 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 7 | 0 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 7 | 15 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 7 | 30 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 7 | 45 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 8 | 0 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 8 | 15 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 8 | 30 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 8 | 45 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 9 | 0 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 9 | 15 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 9 | 30 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 1 | 9 | 45 |  | 9 | 98 |  |  |  | 0 | 0 | 0
2002 | 2 | 5 | 6 | 0 | 13 | 9 | 98 |  |  |  | 8.0251 | 8.7621 | 0.737 | 36686.8524
2002 | 2 | 5 | 6 | 15 |  | 9 | 98 |  |  |  | 6.528 | 7.1275 | 0.59951
2002 | 2 | 5 | 6 | 30 |  | 9 | 98 |  |  |  | 6.3854 | 6.9718 | 0.58641
2002 | 2 | 5 | 6 | 45 |  | 9 | 98 |  |  |  | 7.3449 | 8.0195 | 0.67453
2002 | 2 | 5 | 7 | 0 |  | 9 | 98 |  |  |  | 6.8506 | 7.4797 | 0.62914
2002 | 2 | 5 | 7 | 15 |  | 9 | 98 |  |  |  | 6.1908 | 6.7594 | 0.56854
2002 | 2 | 5 | 7 | 30 |  | 9 | 98 |  |  |  | 5.9931 | 6.5435 | 0.55039
2002 | 2 | 5 | 7 | 45 |  | 9 | 98 |  |  |  | 6.7595 | 7.3803 | 0.62077
2002 | 2 | 5 | 8 | 0 |  | 9 | 98 |  |  |  | 7.7204 | 8.4294 | 0.70902
2002 | 2 | 5 | 8 | 15 |  | 9 | 98 |  |  |  | 8.8348 | 9.6462 | 0.81136
2002 | 2 | 5 | 8 | 30 |  | 9 | 98 |  |  |  | 9.7997 | 10.6997 | 0.89997
2002 | 2 | 5 | 8 | 45 |  | 9 | 98 |  |  |  | 11.0769 | 12.0942 | 1.0173
2002 | 2 | 5 | 9 | 0 |  | 9 | 98 |  |  |  | 12.9903 | 14.1833 | 1.193
2002 | 2 | 5 | 9 | 15 |  | 9 | 98 |  |  |  | 11.7814 | 12.8634 | 1.082
2002 | 2 | 5 | 9 | 30 |  | 9 | 98 |  |  |  | 10.0512 | 10.9743 | 0.92307
2002 | 2 | 5 | 9 | 45 |  | 9 | 98 |  |  |  | 9.2952 | 10.1488 | 0.85364
2002 | 2 | 5 | 10 | 0 |  | 9 | 98 |  |  |  | 6.9814 | 7.6226 | 0.64115
2002 | 2 | 5 | 10 | 15 |  | 9 | 98 |  |  |  | 5.6104 | 6.1256 | 0.51524
2002 | 2 | 5 | 10 | 30 |  | 9 | 98 |  |  |  | 4.7211 | 5.1547 | 0.43357
2002 | 2 | 5 | 10 | 45 |  | 9 | 98 |  |  |  | 3.156 | 3.4458 | 0.28984
2002 | 2 | 5 | 11 | 0 |  | 9 | 98 |  |  |  | 4.3169 | 4.7134 | 0.39645
2002 | 2 | 5 | 11 | 15 |  | 9 | 98 |  |  |  | 3.6308 | 3.9642 | 0.33344
2002 | 2 | 5 | 11 | 30 |  | 9 | 98 |  |  |  | 3.138 | 3.4262 | 0.28819
2002 | 2 | 5 | 11 | 45 |  | 9 | 98 |  |  |  | 4.089 | 4.4645 | 0.37552
2002 | 2 | 5 | 12 | 0 |  | 9 | 98 |  |  |  | 3.8442 | 4.1972 | 0.35304
2002 | 2 | 5 | 12 | 15 |  | 9 | 98 |  |  |  | 3.1697 | 3.4608 | 0.29109
2002 | 2 | 5 | 12 | 30 |  | 9 | 98 |  |  |  | 2.8791 | 3.1435 | 0.2644
2002 | 2 | 5 | 12 | 45 |  | 9 | 98 |  |  |  | 1.8949 | 2.0689 | 0.17402
2002 | 2 | 5 | 13 | 0 |  | 9 | 98 |  |  |  | 1.9738 | 2.1551 | 0.18127
2002 | 2 | 5 | 13 | 15 |  | 9 | 98 |  |  |  | 0.89148 | 0.97335 | 0.081871
2002 | 2 | 5 | 13 | 30 |  | 9 | 98 |  |  |  | 0.27989 | 0.30559 | 0.025704
2002 | 2 | 5 | 13 | 45 |  | 9 | 98 |  |  |  | 0.96655 | 1.0553 | 0.088765
2002 | 2 | 5 | 14 | 0 |  | 9 | 98 |  |  |  | 2.9086 | 3.1758 | 0.26712
2002 | 2 | 5 | 14 | 15 |  | 9 | 98 |  |  |  | 3.8312 | 4.183 | 0.35184
2002 | 2 | 5 | 14 | 30 |  | 9 | 98 |  |  |  | 4.5554 | 4.9738 | 0.41836
2002 | 2 | 5 | 14 | 45 |  | 9 | 98 |  |  |  | 3.5356 | 3.8603 | 0.3247
2002 | 2 | 5 | 15 | 0 |  | 9 | 98 |  |  |  | 3.1663 | 3.4571 | 0.29078
2002 | 2 | 5 | 15 | 15 |  | 9 | 98 |  |  |  | 4.27 | 4.6622 | 0.39214
2002 | 2 | 5 | 15 | 30 |  | 9 | 98 |  |  |  | 4.3682 | 4.7693 | 0.40116
2002 | 2 | 5 | 15 | 45 |  | 9 | 98 |  |  |  | 6.6496 | 7.2602 | 0.61067
2002 | 2 | 5 | 16 | 0 |  | 9 | 98 |  |  |  | 8.5194 | 9.3018 | 0.7824
2002 | 2 | 5 | 16 | 15 |  | 9 | 98 |  |  |  | 12.122 | 13.2353 | 1.1132
2002 | 2 | 5 | 16 | 30 |  | 9 | 98 |  |  |  | 12.5742 | 13.729 | 1.1548
2002 | 2 | 5 | 16 | 45 |  | 9 | 98 |  |  |  | 12.8609 | 14.042 | 1.1811
2002 | 2 | 5 | 17 | 0 |  | 9 | 98 |  |  |  | 11.9275 | 13.0229 | 1.0954
2002 | 2 | 5 | 17 | 15 |  | 9 | 98 |  |  |  | 14.4709 | 15.7999 | 1.329
2002 | 2 | 5 | 17 | 30 |  | 9 | 98 |  |  |  | 17.2999 | 18.8887 | 1.5888
2002 | 2 | 5 | 17 | 45 |  | 9 | 98 |  |  |  | 17.0872 | 18.6564 | 1.5692
2002 | 2 | 5 | 18 | 0 |  | 9 | 98 |  |  |  | 16.0455 | 17.519 | 1.4736
2002 | 2 | 5 | 18 | 15 |  | 9 | 98 |  |  |  | 17.6849 | 19.309 | 1.6241
2002 | 2 | 5 | 18 | 30 |  | 9 | 98 |  |  |  | 18.6916 | 20.4082 | 1.7166
2002 | 2 | 5 | 18 | 45 |  | 9 | 98 |  |  |  | 19.7394 | 21.5522 | 1.8128
2002 | 2 | 5 | 17 | 30 | 4.5 | 21 | 86 |  |  |  | 17.2999 | 21.5243 | 4.2244 | 61025.3837
2002 | 2 | 5 | 17 | 45 |  | 21 | 86 |  |  |  | 17.0872 | 21.2596 | 4.1725
2002 | 2 | 5 | 18 | 0 |  | 21 | 86 |  |  |  | 16.0455 | 19.9635 | 3.9181
2002 | 2 | 5 | 18 | 15 |  | 21 | 86 |  |  |  | 17.6849 | 22.0033 | 4.3184
2002 | 2 | 5 | 18 | 30 |  | 21 | 86 |  |  |  | 18.6916 | 23.2559 | 4.5642
2002 | 2 | 5 | 18 | 45 |  | 21 | 86 |  |  |  | 19.7394 | 24.5595 | 4.8201
2002 | 2 | 5 | 19 | 0 |  | 21 | 86 |  |  |  | 17.833 | 22.1876 | 4.3546
2002 | 2 | 5 | 19 | 15 |  | 21 | 86 |  |  |  | 14.8558 | 18.4834 | 3.6276
2002 | 2 | 5 | 19 | 30 |  | 21 | 86 |  |  |  | 8.9574 | 11.1446 | 2.1873
2002 | 2 | 5 | 19 | 45 |  | 21 | 86 |  |  |  | 8.7537 | 10.8913 | 2.1375
2002 | 2 | 5 | 20 | 0 |  | 21 | 86 |  |  |  | 10.3277 | 12.8496 | 2.5219
2002 | 2 | 5 | 20 | 15 |  | 21 | 86 |  |  |  | 10.9929 | 13.6773 | 2.6843
2002 | 2 | 5 | 20 | 30 |  | 21 | 86 |  |  |  | 11.5551 | 14.3767 | 2.8216
2002 | 2 | 5 | 20 | 45 |  | 21 | 86 |  |  |  | 11.9567 | 14.8764 | 2.9197
2002 | 2 | 5 | 21 | 0 |  | 21 | 86 |  |  |  | 11.5717 | 14.3974 | 2.8256
2002 | 2 | 5 | 21 | 15 |  | 21 | 86 |  |  |  | 11.3852 | 14.1653 | 2.7801
2002 | 2 | 5 | 21 | 30 |  | 21 | 86 |  |  |  | 10.4413 | 12.9909 | 2.5496
2002 | 2 | 5 | 21 | 45 |  | 21 | 86 |  |  |  | 14.7344 | 18.3324 | 3.5979
2002 | 2 | 5 | 19 | 0 | 3 | 24 | 83 |  |  |  | 17.833 | 22.9895 | 5.1565 | 41454.9424
2002 | 2 | 5 | 19 | 15 |  | 24 | 83 |  |  |  | 14.8558 | 19.1515 | 4.2957
2002 | 2 | 5 | 19 | 30 |  | 24 | 83 |  |  |  | 8.9574 | 11.5475 | 2.5901
2002 | 2 | 5 | 19 | 45 |  | 24 | 83 |  |  |  | 8.7537 | 11.2849 | 2.5312
2002 | 2 | 5 | 20 | 0 |  | 24 | 83 |  |  |  | 10.3277 | 13.3141 | 2.9863
2002 | 2 | 5 | 20 | 15 |  | 24 | 83 |  |  |  | 10.9929 | 14.1716 | 3.1787
2002 | 2 | 5 | 20 | 30 |  | 24 | 83 |  |  |  | 11.5551 | 14.8963 | 3.3412
2002 | 2 | 5 | 20 | 45 |  | 24 | 83 |  |  |  | 11.9567 | 15.4141 | 3.4574
2002 | 2 | 5 | 21 | 0 |  | 24 | 83 |  |  |  | 11.5717 | 14.9177 | 3.346
2002 | 2 | 5 | 21 | 15 |  | 24 | 83 |  |  |  | 11.3852 | 14.6773 | 3.2921
2002 | 2 | 5 | 21 | 30 |  | 24 | 83 |  |  |  | 10.4413 | 13.4604 | 3.0192
2002 | 2 | 5 | 21 | 45 |  | 24 | 83 |  |  |  | 14.7344 | 18.995 | 4.2606
2002 | 2 | 9 | 23 | 0 | 9.5 | 75 | 32 |  |  |  | 9.6346 | 32.2157 | 22.5811 | 582487.0711
2002 | 2 | 9 | 23 | 15 |  | 75 | 32 |  |  |  | 6.8708 | 22.9741 | 16.1033
2002 | 2 | 9 | 23 | 30 |  | 75 | 32 |  |  |  | 4.5427 | 15.1897 | 10.647
2002 | 2 | 9 | 23 | 45 |  | 75 | 32 |  |  |  | 2.9055 | 9.7151 | 6.8097
2002 | 2 | 10 | 0 | 0 |  | 75 | 32 |  |  |  | 2.5562 | 8.5473 | 5.9911
2002 | 2 | 10 | 0 | 15 |  | 75 | 32 |  |  |  | 2.8528 | 9.5391 | 6.6863
2002 | 2 | 10 | 0 | 30 |  | 75 | 32 |  |  |  | 3.2656 | 10.9195 | 7.6539
2002 | 2 | 10 | 0 | 45 |  | 75 | 32 |  |  |  | 3.8046 | 12.7215 | 8.917
2002 | 2 | 10 | 1 | 0 |  | 75 | 32 |  |  |  | 5.6345 | 18.8404 | 13.2059
2002 | 2 | 10 | 1 | 15 |  | 75 | 32 |  |  |  | 7.6408 | 25.5488 | 17.9081
2002 | 2 | 10 | 1 | 30 |  | 75 | 32 |  |  |  | 7.7 | 25.7468 | 18.0468
2002 | 2 | 10 | 1 | 45 |  | 75 | 32 |  |  |  | 7.028 | 23.4998 | 16.4718
2002 | 2 | 10 | 2 | 0 |  | 75 | 32 |  |  |  | 5.9334 | 19.8397 | 13.9064
2002 | 2 | 10 | 2 | 15 |  | 75 | 32 |  |  |  | 4.8973 | 16.3754 | 11.4781
2002 | 2 | 10 | 2 | 30 |  | 75 | 32 |  |  |  | 5.2683 | 17.616 | 12.3476
2002 | 2 | 10 | 2 | 45 |  | 75 | 32 |  |  |  | 5.7414 | 19.1977 | 13.4563
2002 | 2 | 10 | 3 | 0 |  | 75 | 32 |  |  |  | 5.4338 | 18.1692 | 12.7354
2002 | 2 | 10 | 3 | 15 |  | 75 | 32 |  |  |  | 6.3571 | 21.2566 | 14.8995
2002 | 2 | 10 | 3 | 30 |  | 75 | 32 |  |  |  | 7.5373 | 25.203 | 17.6657
2002 | 2 | 10 | 3 | 45 |  | 75 | 32 |  |  |  | 6.9578 | 23.2653 | 16.3074
2002 | 2 | 10 | 4 | 0 |  | 75 | 32 |  |  |  | 6.9499 | 23.2386 | 16.2887
2002 | 2 | 10 | 4 | 15 |  | 75 | 32 |  |  |  | 7.0387 | 23.5356 | 16.4969
2002 | 2 | 10 | 4 | 30 |  | 75 | 32 |  |  |  | 7.7165 | 25.8022 | 18.0856
2002 | 2 | 10 | 4 | 45 |  | 75 | 32 |  |  |  | 7.6191 | 25.4765 | 17.8574
2002 | 2 | 10 | 5 | 0 |  | 75 | 32 |  |  |  | 8.3235 | 27.8316 | 19.5081
2002 | 2 | 10 | 5 | 15 |  | 75 | 32 |  |  |  | 8.7137 | 29.1364 | 20.4227
2002 | 2 | 10 | 5 | 30 |  | 75 | 32 |  |  |  | 8.3039 | 27.766 | 19.4622
2002 | 2 | 10 | 5 | 45 |  | 75 | 32 |  |  |  | 8.5682 | 28.6501 | 20.0818
2002 | 2 | 10 | 6 | 0 |  | 75 | 32 |  |  |  | 9.1619 | 30.6352 | 21.4732
2002 | 2 | 10 | 6 | 15 |  | 75 | 32 |  |  |  | 8.4703 | 28.3226 | 19.8523
2002 | 2 | 10 | 6 | 30 |  | 75 | 32 |  |  |  | 7.3489 | 24.5729 | 17.224
2002 | 2 | 10 | 6 | 45 |  | 75 | 32 |  |  |  | 6.5585 | 21.9298 | 15.3714
2002 | 2 | 10 | 7 | 0 |  | 75 | 32 |  |  |  | 6.3643 | 21.2807 | 14.9163
2002 | 2 | 10 | 7 | 15 |  | 75 | 32 |  |  |  | 6.0923 | 20.3712 | 14.2789
2002 | 2 | 10 | 7 | 30 |  | 75 | 32 |  |  |  | 5.7922 | 19.3676 | 13.5755
2002 | 2 | 10 | 7 | 45 |  | 75 | 32 |  |  |  | 5.4385 | 18.1851 | 12.7465
2002 | 2 | 10 | 8 | 0 |  | 75 | 32 |  |  |  | 5.1122 | 17.0939 | 11.9817
2002 | 2 | 10 | 8 | 15 |  | 75 | 32 |  |  |  | 5.8518 | 19.5669 | 13.7151
2002 | 2 | 10 | 8 | 30 |  | 75 | 32 |  |  |  | 6.541 | 21.8716 | 15.3305
2002 | 2 | 10 | 10 | 45 | 1.75 | 8 | 99 |  |  |  | 21.557 | 23.2989 | 1.742 | 12051.7785
2002 | 2 | 10 | 11 | 0 |  | 8 | 99 |  |  |  | 20.9282 | 22.6194 | 1.6912
2002 | 2 | 10 | 11 | 15 |  | 8 | 99 |  |  |  | 20.6899 | 22.3618 | 1.6719
2002 | 2 | 10 | 11 | 30 |  | 8 | 99 |  |  |  | 21.5766 | 23.3201 | 1.7436
2002 | 2 | 10 | 11 | 45 |  | 8 | 99 |  |  |  | 21.3317 | 23.0555 | 1.7238
2002 | 2 | 10 | 12 | 0 |  | 8 | 99 |  |  |  | 22.0034 | 23.7815 | 1.7781
2002 | 2 | 10 | 12 | 15 |  | 8 | 99 |  |  |  | 21.054 | 22.7553 | 1.7013
2002 | 2 | 14 | 7 | 0 | 17 | 61 | 46 |  |  |  | 21.6338 | 50.322 | 28.6883 | 1586719.2231
2002 | 2 | 14 | 7 | 15 |  | 61 | 46 |  |  |  | 15.7943 | 36.7388 | 20.9446
2002 | 2 | 14 | 7 | 30 |  | 61 | 46 |  |  |  | 14.0926 | 32.7806 | 18.688
2002 | 2 | 14 | 7 | 45 |  | 61 | 46 |  |  |  | 14.8475 | 34.5365 | 19.689
2002 | 2 | 14 | 8 | 0 |  | 61 | 46 |  |  |  | 15.1958 | 35.3469 | 20.151
2002 | 2 | 14 | 8 | 15 |  | 61 | 46 |  |  |  | 14.9505 | 34.7761 | 19.8256
2002 | 2 | 14 | 8 | 30 |  | 61 | 46 |  |  |  | 15.1997 | 35.3557 | 20.1561
2002 | 2 | 14 | 8 | 45 |  | 61 | 46 |  |  |  | 15.4718 | 35.9887 | 20.5169
2002 | 2 | 14 | 9 | 0 |  | 61 | 46 |  |  |  | 15.7494 | 36.6345 | 20.8851
2002 | 2 | 14 | 9 | 15 |  | 61 | 46 |  |  |  | 13.3636 | 31.085 | 17.7214
2002 | 2 | 14 | 9 | 30 |  | 61 | 46 |  |  |  | 11.4797 | 26.7028 | 15.2231
2002 | 2 | 14 | 9 | 45 |  | 61 | 46 |  |  |  | 11.9457 | 27.7867 | 15.841
2002 | 2 | 14 | 10 | 0 |  | 61 | 46 |  |  |  | 14.3736 | 33.4343 | 19.0607
2002 | 2 | 14 | 10 | 15 |  | 61 | 46 |  |  |  | 16.8071 | 39.0949 | 22.2877
2002 | 2 | 14 | 10 | 30 |  | 61 | 46 |  |  |  | 17.6092 | 40.9605 | 23.3513
2002 | 2 | 14 | 10 | 45 |  | 61 | 46 |  |  |  | 16.6685 | 38.7724 | 22.1039
2002 | 2 | 14 | 11 | 0 |  | 61 | 46 |  |  |  | 16.2095 | 37.7048 | 21.4952
2002 | 2 | 14 | 11 | 15 |  | 61 | 46 |  |  |  | 15.3962 | 35.8128 | 20.4167
2002 | 2 | 14 | 11 | 30 |  | 61 | 46 |  |  |  | 13.9836 | 32.5271 | 18.5435
2002 | 2 | 14 | 11 | 45 |  | 61 | 46 |  |  |  | 15.142 | 35.2216 | 20.0796
2002 | 2 | 14 | 12 | 0 |  | 61 | 46 |  |  |  | 16.4797 | 38.3331 | 21.8535
2002 | 2 | 14 | 12 | 15 |  | 61 | 46 |  |  |  | 16.5754 | 38.5559 | 21.9805
2002 | 2 | 14 | 12 | 30 |  | 61 | 46 |  |  |  | 17.1523 | 39.8977 | 22.7454
2002 | 2 | 14 | 12 | 45 |  | 61 | 46 |  |  |  | 17.844 | 41.5067 | 23.6627
2002 | 2 | 14 | 13 | 0 |  | 61 | 46 |  |  |  | 15.8299 | 36.8216 | 20.9918
2002 | 2 | 14 | 13 | 15 |  | 61 | 46 |  |  |  | 15.4469 | 35.9308 | 20.4839
2002 | 2 | 14 | 13 | 30 |  | 61 | 46 |  |  |  | 15.2406 | 35.4509 | 20.2103
2002 | 2 | 14 | 13 | 45 |  | 61 | 46 |  |  |  | 14.908 | 34.6773 | 19.7693
2002 | 2 | 14 | 14 | 0 |  | 61 | 46 |  |  |  | 15.1229 | 35.1773 | 20.0543
2002 | 2 | 14 | 14 | 15 |  | 61 | 46 |  |  |  | 14.686 | 34.1608 | 19.4749
2002 | 2 | 14 | 14 | 30 |  | 61 | 46 |  |  |  | 14.4001 | 33.4958 | 19.0957
2002 | 2 | 14 | 14 | 45 |  | 61 | 46 |  |  |  | 14.7564 | 34.3247 | 19.5683
2002 | 2 | 14 | 15 | 0 |  | 61 | 46 |  |  |  | 15.0619 | 35.0353 | 19.9734
2002 | 2 | 14 | 15 | 15 |  | 61 | 46 |  |  |  | 15.3461 | 35.6964 | 20.3503
2002 | 2 | 14 | 15 | 30 |  | 61 | 46 |  |  |  | 15.2066 | 35.3718 | 20.1652
2002 | 2 | 14 | 15 | 45 |  | 61 | 46 |  |  |  | 14.8285 | 34.4923 | 19.6639
2002 | 2 | 14 | 16 | 0 |  | 61 | 46 |  |  |  | 15.1935 | 35.3413 | 20.1478
2002 | 2 | 14 | 16 | 15 |  | 61 | 46 |  |  |  | 14.789 | 34.4006 | 19.6116
2002 | 2 | 14 | 16 | 30 |  | 61 | 46 |  |  |  | 15.1195 | 35.1694 | 20.0498
2002 | 2 | 14 | 16 | 45 |  | 61 | 46 |  |  |  | 15.138 | 35.2123 | 20.0743
2002 | 2 | 14 | 17 | 0 |  | 61 | 46 |  |  |  | 15.1443 | 35.2269 | 20.0826
2002 | 2 | 14 | 17 | 15 |  | 61 | 46 |  |  |  | 15.3899 | 35.7982 | 20.4083
2002 | 2 | 14 | 17 | 30 |  | 61 | 46 |  |  |  | 15.6977 | 36.5142 | 20.8165
2002 | 2 | 14 | 17 | 45 |  | 61 | 46 |  |  |  | 15.4008 | 35.8237 | 20.4229
2002 | 2 | 14 | 18 | 0 |  | 61 | 46 |  |  |  | 23.0955 | 53.7221 | 30.6266
2002 | 2 | 14 | 18 | 15 |  | 61 | 46 |  |  |  | 33.5847 | 78.121 | 44.5363
2002 | 2 | 14 | 18 | 30 |  | 61 | 46 |  |  |  | 34.0349 | 79.168 | 45.1332
2002 | 2 | 14 | 18 | 45 |  | 61 | 46 |  |  |  | 33.6512 | 78.2755 | 44.6244
2002 | 2 | 14 | 19 | 0 |  | 61 | 46 |  |  |  | 28.1712 | 65.5286 | 37.3574
2002 | 2 | 14 | 19 | 15 |  | 61 | 46 |  |  |  | 24.9355 | 58.0022 | 33.0667
2002 | 2 | 14 | 19 | 30 |  | 61 | 46 |  |  |  | 23.9308 | 55.665 | 31.7343
2002 | 2 | 14 | 19 | 45 |  | 61 | 46 |  |  |  | 24.1052 | 56.0709 | 31.9656
2002 | 2 | 14 | 20 | 0 |  | 61 | 46 |  |  |  | 24.3147 | 56.5582 | 32.2434
2002 | 2 | 14 | 20 | 15 |  | 61 | 46 |  |  |  | 24.3115 | 56.5507 | 32.2392
2002 | 2 | 14 | 20 | 30 |  | 61 | 46 |  |  |  | 24.0442 | 55.929 | 31.8847
2002 | 2 | 14 | 20 | 45 |  | 61 | 46 |  |  |  | 23.8266 | 55.4228 | 31.5962
2002 | 2 | 14 | 21 | 0 |  | 61 | 46 |  |  |  | 21.9319 | 51.0154 | 29.0835
2002 | 2 | 14 | 21 | 15 |  | 61 | 46 |  |  |  | 21.4769 | 49.9571 | 28.4802
2002 | 2 | 14 | 21 | 30 |  | 61 | 46 |  |  |  | 15.8656 | 36.9048 | 21.0392
2002 | 2 | 14 | 21 | 45 |  | 61 | 46 |  |  |  | 13.8081 | 32.1187 | 18.3107
2002 | 2 | 14 | 22 | 0 |  | 61 | 46 |  |  |  | 14.8347 | 34.5069 | 19.6722
2002 | 2 | 14 | 22 | 15 |  | 61 | 46 |  |  |  | 15.88 | 36.9382 | 21.0583
2002 | 2 | 14 | 22 | 30 |  | 61 | 46 |  |  |  | 16.4322 | 38.2227 | 21.7905
2002 | 2 | 14 | 22 | 45 |  | 61 | 46 |  |  |  | 15.5158 | 36.0912 | 20.5753
2002 | 2 | 14 | 23 | 0 |  | 61 | 46 |  |  |  | 15.633 | 36.3637 | 20.7307
2002 | 2 | 14 | 23 | 15 |  | 61 | 46 |  |  |  | 15.3073 | 35.6062 | 20.2989
2002 | 2 | 14 | 23 | 30 |  | 61 | 46 |  |  |  | 15.5045 | 36.0649 | 20.5604
2002 | 2 | 14 | 23 | 45 |  | 61 | 46 |  |  |  | 15.6743 | 36.4599 | 20.7855
2002 | 2 | 15 | 0 | 0 | 6 | 61 | 46 |  |  |  | 15.5989 | 36.2844 | 20.6855 | 405464.7364
2002 | 2 | 15 | 0 | 15 |  | 61 | 46 |  |  |  | 15.6388 | 36.3771 | 20.7384
2002 | 2 | 15 | 0 | 30 |  | 61 | 46 |  |  |  | 15.1633 | 35.2711 | 20.1078
2002 | 2 | 15 | 0 | 45 |  | 61 | 46 |  |  |  | 15.1215 | 35.1739 | 20.0524
2002 | 2 | 15 | 1 | 0 |  | 61 | 46 |  |  |  | 14.7295 | 34.2622 | 19.5326
2002 | 2 | 15 | 1 | 15 |  | 61 | 46 |  |  |  | 14.2912 | 33.2426 | 18.9514
2002 | 2 | 15 | 1 | 30 |  | 61 | 46 |  |  |  | 13.8414 | 32.1963 | 18.3549
2002 | 2 | 15 | 1 | 45 |  | 61 | 46 |  |  |  | 13.4042 | 31.1793 | 17.7751
2002 | 2 | 15 | 2 | 0 |  | 61 | 46 |  |  |  | 12.1332 | 28.2229 | 16.0897
2002 | 2 | 15 | 2 | 15 |  | 61 | 46 |  |  |  | 11.3328 | 26.3611 | 15.0283
2002 | 2 | 15 | 2 | 30 |  | 61 | 46 |  |  |  | 11.2348 | 26.1332 | 14.8984
2002 | 2 | 15 | 2 | 45 |  | 61 | 46 |  |  |  | 11.2347 | 26.1328 | 14.8981
2002 | 2 | 15 | 3 | 0 |  | 61 | 46 |  |  |  | 10.584 | 24.6193 | 14.0353
2002 | 2 | 15 | 3 | 15 |  | 61 | 46 |  |  |  | 11.3758 | 26.4612 | 15.0853
2002 | 2 | 15 | 3 | 30 |  | 61 | 46 |  |  |  | 17.0832 | 39.7369 | 22.6538
2002 | 2 | 15 | 3 | 45 |  | 61 | 46 |  |  |  | 18.1253 | 42.161 | 24.0357
2002 | 2 | 15 | 4 | 0 |  | 61 | 46 |  |  |  | 16.8556 | 39.2075 | 22.352
2002 | 2 | 15 | 4 | 15 |  | 61 | 46 |  |  |  | 15.3556 | 35.7185 | 20.3629
2002 | 2 | 15 | 4 | 30 |  | 61 | 46 |  |  |  | 14.3038 | 33.2718 | 18.9681
2002 | 2 | 15 | 4 | 45 |  | 61 | 46 |  |  |  | 12.2514 | 28.4979 | 16.2465
2002 | 2 | 15 | 5 | 0 |  | 61 | 46 |  |  |  | 10.1904 | 23.7038 | 13.5134
2002 | 2 | 15 | 5 | 15 |  | 61 | 46 |  |  |  | 5.0697 | 11.7926 | 6.7229
2002 | 2 | 15 | 5 | 30 |  | 61 | 46 |  |  |  | 4.4665 | 10.3894 | 5.923
2002 | 2 | 15 | 5 | 45 |  | 61 | 46 |  |  |  | 6.3747 | 14.8281 | 8.4534
2002 | 2 | 15 | 6 | 0 | 2 | 13 | 94 |  |  |  | 15.9368 | 18.1408 | 2.204 | 25167.2673
2002 | 2 | 15 | 6 | 15 |  | 13 | 94 |  |  |  | 25.58 | 29.1176 | 3.5377
2002 | 2 | 15 | 6 | 30 |  | 13 | 94 |  |  |  | 25.3667 | 28.8749 | 3.5082
2002 | 2 | 15 | 6 | 45 |  | 13 | 94 |  |  |  | 26.1203 | 29.7327 | 3.6124
2002 | 2 | 15 | 7 | 0 |  | 13 | 94 |  |  |  | 24.1189 | 27.4545 | 3.3356
2002 | 2 | 15 | 7 | 15 |  | 13 | 94 |  |  |  | 21.2187 | 24.1532 | 2.9345
2002 | 2 | 15 | 7 | 30 |  | 13 | 94 |  |  |  | 20.1166 | 22.8987 | 2.7821
2002 | 2 | 15 | 7 | 45 |  | 13 | 94 |  |  |  | 23.5207 | 26.7735 | 3.2529
2002 | 2 | 16 | 21 | 15 | 2.5 | 75 | 32 |  |  |  | 15.7871 | 52.7882 | 37.0011 | 248282.8781
2002 | 2 | 16 | 21 | 30 |  | 75 | 32 |  |  |  | 11.7964 | 39.4442 | 27.6478
2002 | 2 | 16 | 21 | 45 |  | 75 | 32 |  |  |  | 8.6833 | 29.0348 | 20.3515
2002 | 2 | 16 | 22 | 0 |  | 75 | 32 |  |  |  | 9.0312 | 30.1979 | 21.1668
2002 | 2 | 16 | 22 | 15 |  | 75 | 32 |  |  |  | 9.7171 | 32.4917 | 22.7745
2002 | 2 | 16 | 22 | 30 |  | 75 | 32 |  |  |  | 9.8767 | 33.0253 | 23.1485
2002 | 2 | 16 | 22 | 45 |  | 75 | 32 |  |  |  | 9.6265 | 32.1887 | 22.5622
2002 | 2 | 16 | 23 | 0 |  | 75 | 32 |  |  |  | 10.5624 | 35.3181 | 24.7557
2002 | 2 | 16 | 23 | 15 |  | 75 | 32 |  |  |  | 10.5017 | 35.1152 | 24.6134
2002 | 2 | 16 | 23 | 30 |  | 75 | 32 |  |  |  | 10.3515 | 34.6128 | 24.2613
2002 | 2 | 18 | 19 | 45 | 3.5 | 33 | 74 |  |  |  | 13.5795 | 19.6352 | 6.0557 | 60822.2385
2002 | 2 | 18 | 20 | 0 |  | 33 | 74 |  |  |  | 13.4917 | 19.5083 | 6.0166
2002 | 2 | 18 | 20 | 15 |  | 33 | 74 |  |  |  | 13.3347 | 19.2812 | 5.9465
2002 | 2 | 18 | 20 | 30 |  | 33 | 74 |  |  |  | 13.1575 | 19.025 | 5.8675
2002 | 2 | 18 | 20 | 45 |  | 33 | 74 |  |  |  | 13.3398 | 19.2887 | 5.9488
2002 | 2 | 18 | 21 | 0 |  | 33 | 74 |  |  |  | 13.021 | 18.8277 | 5.8067
2002 | 2 | 18 | 21 | 15 |  | 33 | 74 |  |  |  | 12.2875 | 17.7671 | 5.4796
2002 | 2 | 18 | 21 | 30 |  | 33 | 74 |  |  |  | 3.8807 | 5.6114 | 1.7306
2002 | 2 | 18 | 21 | 45 |  | 33 | 74 |  |  |  | 5.8633 | 8.478 | 2.6147
2002 | 2 | 18 | 22 | 0 |  | 33 | 74 |  |  |  | 7.7848 | 11.2563 | 3.4716
2002 | 2 | 18 | 22 | 15 |  | 33 | 74 |  |  |  | 9.2001 | 13.3028 | 4.1027
2002 | 2 | 18 | 22 | 30 |  | 33 | 74 |  |  |  | 9.1718 | 13.2619 | 4.0901
2002 | 2 | 18 | 22 | 45 |  | 33 | 74 |  |  |  | 8.2769 | 11.968 | 3.6911
2002 | 2 | 18 | 23 | 0 | 1 | 11 | 96 |  |  |  | 10.2807 | 11.4587 | 1.178 | 3427.1665
2002 | 2 | 18 | 23 | 15 |  | 11 | 96 |  |  |  | 9.2218 | 10.2784 | 1.0567
2002 | 2 | 18 | 23 | 30 |  | 11 | 96 |  |  |  | 6.4037 | 7.1374 | 0.73375
2002 | 2 | 18 | 23 | 45 |  | 11 | 96 |  |  |  | 4.0037 | 4.4624 | 0.45876
2002 | 2 | 19 | 2 | 0 | 2.5 | 46 | 61 |  |  |  | 23.7865 | 41.7238 | 17.9373 | 131495.9936
2002 | 2 | 19 | 2 | 15 |  | 46 | 61 |  |  |  | 21.8156 | 38.2666 | 16.4511
2002 | 2 | 19 | 2 | 30 |  | 46 | 61 |  |  |  | 15.6989 | 27.5375 | 11.8385
2002 | 2 | 19 | 2 | 45 |  | 46 | 61 |  |  |  | 14.6388 | 25.6779 | 11.0391
2002 | 2 | 19 | 3 | 0 |  | 46 | 61 |  |  |  | 15.3166 | 26.8669 | 11.5503
2002 | 2 | 19 | 3 | 15 |  | 46 | 61 |  |  |  | 15.2037 | 26.6689 | 11.4651
2002 | 2 | 19 | 3 | 30 |  | 46 | 61 |  |  |  | 16.4891 | 28.9235 | 12.4344
2002 | 2 | 19 | 3 | 45 |  | 46 | 61 |  |  |  | 16.8979 | 29.6406 | 12.7427
2002 | 2 | 19 | 4 | 0 |  | 46 | 61 |  |  |  | 17.4861 | 30.6724 | 13.1863
2002 | 2 | 19 | 4 | 15 |  | 46 | 61 |  |  |  | 17.0418 | 29.893 | 12.8512
2002 | 2 | 19 | 4 | 30 | 4 | 52 | 55 |  |  |  | 15.6242 | 30.3962 | 14.772 | 241364.3232
2002 | 2 | 19 | 4 | 45 |  | 52 | 55 |  |  |  | 20.7968 | 40.4593 | 19.6625
2002 | 2 | 19 | 5 | 0 |  | 52 | 55 |  |  |  | 22.709 | 44.1793 | 21.4703
2002 | 2 | 19 | 5 | 15 |  | 52 | 55 |  |  |  | 15.1563 | 29.4859 | 14.3296
2002 | 2 | 19 | 5 | 30 |  | 52 | 55 |  |  |  | 15.4174 | 29.9938 | 14.5764
2002 | 2 | 19 | 5 | 45 |  | 52 | 55 |  |  |  | 15.4496 | 30.0565 | 14.6069
2002 | 2 | 19 | 6 | 0 |  | 52 | 55 |  |  |  | 15.3928 | 29.946 | 14.5532
2002 | 2 | 19 | 6 | 15 |  | 52 | 55 |  |  |  | 15.0082 | 29.1978 | 14.1896
2002 | 2 | 19 | 6 | 30 |  | 52 | 55 |  |  |  | 14.0122 | 27.2601 | 13.2479
2002 | 2 | 19 | 6 | 45 |  | 52 | 55 |  |  |  | 13.4084 | 26.0854 | 12.677
2002 | 2 | 19 | 7 | 0 |  | 52 | 55 |  |  |  | 14.2259 | 27.6758 | 13.4499
2002 | 2 | 19 | 7 | 15 |  | 52 | 55 |  |  |  | 14.8656 | 28.9203 | 14.0547
2002 | 2 | 19 | 7 | 30 |  | 52 | 55 |  |  |  | 15.178 | 29.5282 | 14.3501
2002 | 2 | 19 | 7 | 45 |  | 52 | 55 |  |  |  | 15.3246 | 29.8133 | 14.4887
2002 | 2 | 19 | 8 | 0 |  | 52 | 55 |  |  |  | 16.0573 | 31.2387 | 15.1814
2002 | 2 | 19 | 8 | 15 |  | 52 | 55 |  |  |  | 16.6629 | 32.4168 | 15.754
2002 | 2 | 19 | 8 | 30 | 1.75 | 65 | 42 |  |  |  | 17.3189 | 44.122 | 26.8031 | 154980.0525
2002 | 2 | 19 | 8 | 45 |  | 65 | 42 |  |  |  | 14.2952 | 36.4188 | 22.1236
2002 | 2 | 19 | 9 | 0 |  | 65 | 42 |  |  |  | 13.311 | 33.9115 | 20.6004
2002 | 2 | 19 | 9 | 15 |  | 65 | 42 |  |  |  | 13.8203 | 35.2089 | 21.3886
2002 | 2 | 19 | 9 | 30 |  | 65 | 42 |  |  |  | 13.824 | 35.2184 | 21.3943
2002 | 2 | 19 | 9 | 45 |  | 65 | 42 |  |  |  | 13.8132 | 35.1907 | 21.3775
2002 | 2 | 19 | 10 | 0 |  | 65 | 42 |  |  |  | 13.7582 | 35.0507 | 21.2925
2002 | 2 | 19 | 10 | 15 | 4 | 68 | 39 |  |  |  | 15.0302 | 41.2367 | 26.2065 | 439851.3168
2002 | 2 | 19 | 10 | 30 |  | 68 | 39 |  |  |  | 16.1349 | 44.2676 | 28.1327
2002 | 2 | 19 | 10 | 45 |  | 68 | 39 |  |  |  | 16.4493 | 45.1303 | 28.6809
2002 | 2 | 19 | 11 | 0 |  | 68 | 39 |  |  |  | 16.4602 | 45.1601 | 28.6998
2002 | 2 | 19 | 11 | 15 |  | 68 | 39 |  |  |  | 16.7132 | 45.8542 | 29.141
2002 | 2 | 19 | 11 | 30 |  | 68 | 39 |  |  |  | 16.7788 | 46.0341 | 29.2553
2002 | 2 | 19 | 11 | 45 |  | 68 | 39 |  |  |  | 16.513 | 45.3048 | 28.7918
2002 | 2 | 19 | 12 | 0 |  | 68 | 39 |  |  |  | 17.1951 | 47.1763 | 29.9812
2002 | 2 | 19 | 12 | 15 |  | 68 | 39 |  |  |  | 16.9469 | 46.4954 | 29.5485
2002 | 2 | 19 | 12 | 30 |  | 68 | 39 |  |  |  | 16.5973 | 45.5361 | 28.9388
2002 | 2 | 19 | 12 | 45 |  | 68 | 39 |  |  |  | 16.0454 | 44.022 | 27.9766
2002 | 2 | 19 | 13 | 0 |  | 68 | 39 |  |  |  | 15.6802 | 43.0201 | 27.3399
2002 | 2 | 19 | 13 | 15 |  | 68 | 39 |  |  |  | 13.848 | 37.9931 | 24.1451
2002 | 2 | 19 | 13 | 30 |  | 68 | 39 |  |  |  | 14.3546 | 39.3832 | 25.0286
2002 | 2 | 19 | 13 | 45 |  | 68 | 39 |  |  |  | 13.8102 | 37.8896 | 24.0794
2002 | 2 | 19 | 14 | 0 |  | 68 | 39 |  |  |  | 13.7103 | 37.6154 | 23.9051
2002 | 2 | 19 | 14 | 15 | 1.75 | 61 | 46 |  |  |  | 13.4417 | 31.2665 | 17.8248 | 147021.6059
2002 | 2 | 19 | 14 | 30 |  | 61 | 46 |  |  |  | 15.47 | 35.9846 | 20.5146
2002 | 2 | 19 | 14 | 45 |  | 61 | 46 |  |  |  | 16.7758 | 39.0219 | 22.2461
2002 | 2 | 19 | 15 | 0 |  | 61 | 46 |  |  |  | 16.7747 | 39.0193 | 22.2446
2002 | 2 | 19 | 15 | 15 |  | 61 | 46 |  |  |  | 17.294 | 40.2274 | 22.9334
2002 | 2 | 19 | 15 | 30 |  | 61 | 46 |  |  |  | 16.5678 | 38.5381 | 21.9703
2002 | 2 | 19 | 15 | 45 |  | 61 | 46 |  |  |  | 14.5449 | 33.8327 | 19.2878
2002 | 2 | 19 | 16 | 0 | 6.75 | 70 | 37 |  |  |  | 14.642 | 42.343 | 27.701 | 761310.3022
2002 | 2 | 19 | 16 | 15 |  | 70 | 37 |  |  |  | 14.7337 | 42.6081 | 27.8745
2002 | 2 | 19 | 16 | 30 |  | 70 | 37 |  |  |  | 15.2367 | 44.0628 | 28.8261
2002 | 2 | 19 | 16 | 45 |  | 70 | 37 |  |  |  | 14.5957 | 42.2091 | 27.6134
2002 | 2 | 19 | 17 | 0 |  | 70 | 37 |  |  |  | 15.9232 | 46.0481 | 30.1249
2002 | 2 | 19 | 17 | 15 |  | 70 | 37 |  |  |  | 14.5143 | 41.9737 | 27.4594
2002 | 2 | 19 | 17 | 30 |  | 70 | 37 |  |  |  | 15.1027 | 43.6753 | 28.5726
2002 | 2 | 19 | 17 | 45 |  | 70 | 37 |  |  |  | 15.1547 | 43.8257 | 28.671
2002 | 2 | 19 | 18 | 0 |  | 70 | 37 |  |  |  | 13.0938 | 37.8657 | 24.772
2002 | 2 | 19 | 18 | 15 |  | 70 | 37 |  |  |  | 11.4038 | 32.9786 | 21.5748
2002 | 2 | 19 | 18 | 30 |  | 70 | 37 |  |  |  | 10.3728 | 29.9971 | 19.6242
2002 | 2 | 19 | 18 | 45 |  | 70 | 37 |  |  |  | 10.1357 | 29.3113 | 19.1756
2002 | 2 | 19 | 19 | 0 |  | 70 | 37 |  |  |  | 8.5227 | 24.6466 | 16.124
2002 | 2 | 19 | 19 | 15 |  | 70 | 37 |  |  |  | 10.1049 | 29.2223 | 19.1174
2002 | 2 | 19 | 19 | 30 |  | 70 | 37 |  |  |  | 10.3838 | 30.0288 | 19.645
2002 | 2 | 19 | 19 | 45 |  | 70 | 37 |  |  |  | 9.8767 | 28.5623 | 18.6856
2002 | 2 | 19 | 20 | 0 |  | 70 | 37 |  |  |  | 9.3319 | 26.9868 | 17.6549
2002 | 2 | 19 | 20 | 15 |  | 70 | 37 |  |  |  | 10.2717 | 29.7047 | 19.433
2002 | 2 | 19 | 20 | 30 |  | 70 | 37 |  |  |  | 11.8458 | 34.2568 | 22.411
2002 | 2 | 19 | 20 | 45 |  | 70 | 37 |  |  |  | 17.3784 | 50.2564 | 32.878
2002 | 2 | 19 | 21 | 0 |  | 70 | 37 |  |  |  | 21.9324 | 63.4261 | 41.4937
2002 | 2 | 19 | 21 | 15 |  | 70 | 37 |  |  |  | 22.7745 | 65.8614 | 43.0869
2002 | 2 | 19 | 21 | 30 |  | 70 | 37 |  |  |  | 20.0531 | 57.9915 | 37.9384
2002 | 2 | 19 | 21 | 45 |  | 70 | 37 |  |  |  | 18.393 | 53.1905 | 34.7975
2002 | 2 | 19 | 22 | 0 |  | 70 | 37 |  |  |  | 18.2153 | 52.6766 | 34.4613
2002 | 2 | 19 | 22 | 15 |  | 70 | 37 |  |  |  | 18.4507 | 53.3574 | 34.9067
2002 | 2 | 19 | 22 | 30 |  | 70 | 37 |  |  |  | 17.924 | 51.8343 | 33.9103
2002 | 2 | 19 | 22 | 45 |  | 70 | 37 |  |  |  | 12.0392 | 34.816 | 22.7768
2002 | 2 | 21 | 0 | 0 | 2 | 9 | 98 |  |  |  | 13.5789 | 14.826 | 1.247 | 10079.8851
2002 | 2 | 21 | 0 | 15 |  | 9 | 98 |  |  |  | 12.8126 | 13.9893 | 1.1767
2002 | 2 | 21 | 0 | 30 |  | 9 | 98 |  |  |  | 11.8969 | 12.9895 | 1.0926
2002 | 2 | 21 | 0 | 45 |  | 9 | 98 |  |  |  | 11.3577 | 12.4008 | 1.0431
2002 | 2 | 21 | 1 | 0 |  | 9 | 98 |  |  |  | 12.8264 | 14.0043 | 1.1779
2002 | 2 | 21 | 1 | 15 |  | 9 | 98 |  |  |  | 17.6649 | 19.2872 | 1.6223
2002 | 2 | 21 | 1 | 30 |  | 9 | 98 |  |  |  | 15.839 | 17.2936 | 1.4546
2002 | 2 | 21 | 1 | 45 |  | 9 | 98 |  |  |  | 13.7823 | 15.048 | 1.2657
2002 | 2 | 21 | 2 | 0 | 4 | 26 | 81 |  |  |  | 14.1159 | 18.6469 | 4.531 | 58197.7169
2002 | 2 | 21 | 2 | 15 |  | 26 | 81 |  |  |  | 12.3314 | 16.2896 | 3.9582
2002 | 2 | 21 | 2 | 30 |  | 26 | 81 |  |  |  | 11.5417 | 15.2464 | 3.7047
2002 | 2 | 21 | 2 | 45 |  | 26 | 81 |  |  |  | 9.3356 | 12.3322 | 2.9966
2002 | 2 | 21 | 3 | 0 |  | 26 | 81 |  |  |  | 8.2065 | 10.8407 | 2.6342
2002 | 2 | 21 | 3 | 15 |  | 26 | 81 |  |  |  | 7.98 | 10.5414 | 2.5615
2002 | 2 | 21 | 3 | 30 |  | 26 | 81 |  |  |  | 8.1767 | 10.8014 | 2.6246
2002 | 2 | 21 | 3 | 45 |  | 26 | 81 |  |  |  | 9.9927 | 13.2003 | 3.2075
2002 | 2 | 21 | 4 | 0 |  | 26 | 81 |  |  |  | 12.3061 | 16.2561 | 3.9501
2002 | 2 | 21 | 4 | 15 |  | 26 | 81 |  |  |  | 13.0448 | 17.232 | 4.1872
2002 | 2 | 21 | 4 | 30 |  | 26 | 81 |  |  |  | 12.6107 | 16.6586 | 4.0479
2002 | 2 | 21 | 4 | 45 |  | 26 | 81 |  |  |  | 13.7257 | 18.1315 | 4.4058
2002 | 2 | 21 | 5 | 0 |  | 26 | 81 |  |  |  | 16.7738 | 22.158 | 5.3842
2002 | 2 | 21 | 5 | 15 |  | 26 | 81 |  |  |  | 11.7939 | 15.5795 | 3.7857
2002 | 2 | 21 | 5 | 30 |  | 26 | 81 |  |  |  | 10.2736 | 13.5713 | 3.2977
2002 | 2 | 21 | 5 | 45 |  | 26 | 81 |  |  |  | 9.0994 | 12.0202 | 2.9208
2002 | 2 | 21 | 6 | 0 | 0.5 | 39 | 68 |  |  |  | 8.7882 | 13.8285 | 5.0403 | 10613.8228
2002 | 2 | 21 | 6 | 15 |  | 39 | 68 |  |  |  | 9.7179 | 15.2915 | 5.5735
2002 | 2 | 21 | 6 | 30 | 2 | 31 | 76 |  |  |  | 8.5977 | 12.1046 | 3.5069 | 33401.8797
2002 | 2 | 21 | 6 | 45 |  | 31 | 76 |  |  |  | 9.4009 | 13.2355 | 3.8346
2002 | 2 | 21 | 7 | 0 |  | 31 | 76 |  |  |  | 11.4098 | 16.0637 | 4.654
2002 | 2 | 21 | 7 | 15 |  | 31 | 76 |  |  |  | 9.6734 | 13.6191 | 3.9457
2002 | 2 | 21 | 7 | 30 |  | 31 | 76 |  |  |  | 9.0187 | 12.6973 | 3.6787
2002 | 2 | 21 | 7 | 45 |  | 31 | 76 |  |  |  | 12.8333 | 18.0679 | 5.2346
2002 | 2 | 21 | 8 | 0 |  | 31 | 76 |  |  |  | 11.3549 | 15.9865 | 4.6316
2002 | 2 | 21 | 8 | 15 |  | 31 | 76 |  |  |  | 9.6 | 13.5158 | 3.9158
2002 | 2 | 21 | 9 | 45 | 1 | 11 | 96 |  |  |  | 15.7316 | 17.5342 | 1.8026 | 7720.6697
2002 | 2 | 21 | 10 | 0 |  | 11 | 96 |  |  |  | 15.8346 | 17.649 | 1.8144
2002 | 2 | 21 | 10 | 15 |  | 11 | 96 |  |  |  | 18.5775 | 20.7062 | 2.1287
2002 | 2 | 21 | 10 | 30 |  | 11 | 96 |  |  |  | 17.2366 | 19.2117 | 1.975
2002 | 2 | 21 | 10 | 45 | 1.25 | 27 | 80 |  |  |  | 11.0736 | 14.811 | 3.7373 | 30135.3444
2002 | 2 | 21 | 11 | 0 |  | 27 | 80 |  |  |  | 16.5557 | 22.1433 | 5.5876
2002 | 2 | 21 | 11 | 15 |  | 27 | 80 |  |  |  | 19.0431 | 25.4701 | 6.427
2002 | 2 | 21 | 11 | 30 |  | 27 | 80 |  |  |  | 22.257 | 29.7688 | 7.5117
2002 | 2 | 21 | 11 | 45 |  | 27 | 80 |  |  |  | 20.3605 | 27.2321 | 6.8717
2002 | 2 | 21 | 12 | 0 | 4.25 | 53 | 54 |  |  |  | 16.1721 | 32.0448 | 15.8727 | 213415.134
2002 | 2 | 21 | 12 | 15 |  | 53 | 54 |  |  |  | 14.8069 | 29.3396 | 14.5327
2002 | 2 | 21 | 12 | 30 |  | 53 | 54 |  |  |  | 14.2787 | 28.293 | 14.0143
2002 | 2 | 21 | 12 | 45 |  | 53 | 54 |  |  |  | 12.0661 | 23.9087 | 11.8426
2002 | 2 | 21 | 13 | 0 |  | 53 | 54 |  |  |  | 13.0319 | 25.8225 | 12.7906
2002 | 2 | 21 | 13 | 15 |  | 53 | 54 |  |  |  | 13.1768 | 26.1095 | 12.9328
2002 | 2 | 21 | 13 | 30 |  | 53 | 54 |  |  |  | 13.4314 | 26.614 | 13.1826
2002 | 2 | 21 | 13 | 45 |  | 53 | 54 |  |  |  | 13.281 | 26.3161 | 13.0351
2002 | 2 | 21 | 14 | 0 |  | 53 | 54 |  |  |  | 13.242 | 26.2388 | 12.9968
2002 | 2 | 21 | 14 | 15 |  | 53 | 54 |  |  |  | 13.3035 | 26.3605 | 13.0571
2002 | 2 | 21 | 14 | 30 |  | 53 | 54 |  |  |  | 13.2961 | 26.346 | 13.0499
2002 | 2 | 21 | 14 | 45 |  | 53 | 54 |  |  |  | 13.1133 | 25.9837 | 12.8705
2002 | 2 | 21 | 15 | 0 |  | 53 | 54 |  |  |  | 13.011 | 25.781 | 12.77
2002 | 2 | 21 | 15 | 15 |  | 53 | 54 |  |  |  | 12.8272 | 25.4169 | 12.5897
2002 | 2 | 21 | 15 | 30 |  | 53 | 54 |  |  |  | 11.8656 | 23.5114 | 11.6458
2002 | 2 | 21 | 15 | 45 |  | 53 | 54 |  |  |  | 9.5597 | 18.9423 | 9.3826
2002 | 2 | 21 | 16 | 0 |  | 53 | 54 |  |  |  | 6.9786 | 13.8279 | 6.8494
2002 | 2 | 21 | 16 | 15 | 1.75 | 27 | 80 |  |  |  | 12.2468 | 16.3801 | 4.1333 | 29093.9858
2002 | 2 | 21 | 16 | 30 |  | 27 | 80 |  |  |  | 17.5514 | 23.4749 | 5.9236
2002 | 2 | 21 | 16 | 45 |  | 27 | 80 |  |  |  | 18.5027 | 24.7473 | 6.2447
2002 | 2 | 21 | 17 | 0 |  | 27 | 80 |  |  |  | 13.0336 | 17.4325 | 4.3988
2002 | 2 | 21 | 17 | 15 |  | 27 | 80 |  |  |  | 9.6103 | 12.8538 | 3.2435
2002 | 2 | 21 | 17 | 30 |  | 27 | 80 |  |  |  | 7.5544 | 10.1039 | 2.5496
2002 | 2 | 21 | 17 | 45 |  | 27 | 80 |  |  |  | 7.7053 | 10.3058 | 2.6005
2002 | 2 | 23 | 20 | 15 | 3.75 | 58 | 49 |  |  |  | 31.2652 | 68.273 | 37.0078 | 420326.7197
2002 | 2 | 23 | 20 | 30 |  | 58 | 49 |  |  |  | 23.1709 | 50.5976 | 27.4268
2002 | 2 | 23 | 20 | 45 |  | 58 | 49 |  |  |  | 22.044 | 48.137 | 26.0929
2002 | 2 | 23 | 21 | 0 |  | 58 | 49 |  |  |  | 22.6585 | 49.4788 | 26.8203
2002 | 2 | 23 | 21 | 15 |  | 58 | 49 |  |  |  | 22.4782 | 49.085 | 26.6068
2002 | 2 | 23 | 21 | 30 |  | 58 | 49 |  |  |  | 22.3456 | 48.7956 | 26.4499
2002 | 2 | 23 | 21 | 45 |  | 58 | 49 |  |  |  | 23.0902 | 50.4215 | 27.3313
2002 | 2 | 23 | 22 | 0 |  | 58 | 49 |  |  |  | 22.9388 | 50.0909 | 27.1521
2002 | 2 | 23 | 22 | 15 |  | 58 | 49 |  |  |  | 23.0089 | 50.244 | 27.235
2002 | 2 | 23 | 22 | 30 |  | 58 | 49 |  |  |  | 23.4537 | 51.2153 | 27.7616
2002 | 2 | 23 | 22 | 45 |  | 58 | 49 |  |  |  | 23.7577 | 51.879 | 28.1213
2002 | 2 | 23 | 23 | 0 |  | 58 | 49 |  |  |  | 24.168 | 52.7751 | 28.6071
2002 | 2 | 23 | 23 | 15 |  | 58 | 49 |  |  |  | 23.8043 | 51.9808 | 28.1765
2002 | 2 | 23 | 23 | 30 |  | 58 | 49 |  |  |  | 23.6845 | 51.7192 | 28.0347
2002 | 2 | 23 | 23 | 45 |  | 58 | 49 |  |  |  | 23.235 | 50.7376 | 27.5026
2002 | 2 | 24 | 0 | 0 | 18.5 | 58 | 49 |  |  |  | 23.4364 | 51.1775 | 27.7411 | 1322921.201
2002 | 2 | 24 | 0 | 15 | (6.5) | 58 | 49 |  |  |  | 23.3985 | 51.0946 | 27.6962
2002 | 2 | 24 | 0 | 30 |  | 58 | 49 |  |  |  | 23.9301 | 52.2554 | 28.3254
2002 | 2 | 24 | 0 | 45 |  | 58 | 49 |  |  |  | 24.0297 | 52.4731 | 28.4433
2002 | 2 | 24 | 1 | 0 |  | 58 | 49 |  |  |  | 24.1018 | 52.6304 | 28.5286
2002 | 2 | 24 | 1 | 15 |  | 58 | 49 |  |  |  | 23.9734 | 52.3501 | 28.3767
2002 | 2 | 24 | 1 | 30 |  | 58 | 49 |  |  |  | 24.2255 | 52.9006 | 28.6751
2002 | 2 | 24 | 1 | 45 |  | 58 | 49 |  |  |  | 24.2425 | 52.9376 | 28.6952
2002 | 2 | 24 | 2 | 0 |  | 58 | 49 |  |  |  | 23.8333 | 52.0441 | 28.2108
2002 | 2 | 24 | 2 | 15 |  | 58 | 49 |  |  |  | 23.9855 | 52.3765 | 28.391
2002 | 2 | 24 | 2 | 30 |  | 58 | 49 |  |  |  | 24.2629 | 52.9823 | 28.7194
2002 | 2 | 24 | 2 | 45 |  | 58 | 49 |  |  |  | 24.058 | 52.5349 | 28.4769
2002 | 2 | 24 | 3 | 0 |  | 58 | 49 |  |  |  | 23.8938 | 52.1764 | 28.2825
2002 | 2 | 24 | 3 | 15 |  | 58 | 49 |  |  |  | 23.6575 | 51.6604 | 28.0028
2002 | 2 | 24 | 3 | 30 |  | 58 | 49 |  |  |  | 23.8923 | 52.1729 | 28.2807
2002 | 2 | 24 | 3 | 45 |  | 58 | 49 |  |  |  | 23.4992 | 51.3147 | 27.8154
2002 | 2 | 24 | 4 | 0 |  | 58 | 49 |  |  |  | 23.511 | 51.3404 | 27.8294
2002 | 2 | 24 | 4 | 15 |  | 58 | 49 |  |  |  | 23.9527 | 52.305 | 28.3522
2002 | 2 | 24 | 4 | 30 |  | 58 | 49 |  |  |  | 23.7431 | 51.8472 | 28.1041
2002 | 2 | 24 | 4 | 45 |  | 58 | 49 |  |  |  | 23.6479 | 51.6393 | 27.9914
2002 | 2 | 24 | 5 | 0 |  | 58 | 49 |  |  |  | 22.5728 | 49.2917 | 26.7188
2002 | 2 | 24 | 5 | 15 |  | 58 | 49 |  |  |  | 23.5009 | 51.3184 | 27.8174
2002 | 2 | 24 | 5 | 30 |  | 58 | 49 |  |  |  | 23.976 | 52.3558 | 28.3798
2002 | 2 | 24 | 5 | 45 |  | 58 | 49 |  |  |  | 23.7126 | 51.7806 | 28.068
2002 | 2 | 24 | 6 | 0 |  | 58 | 49 |  |  |  | 24.1704 | 52.7803 | 28.6099
2002 | 2 | 24 | 6 | 15 |  | 58 | 49 |  |  |  | 23.4502 | 51.2076 | 27.7574
2002 | 2 | 24 | 6 | 30 |  | 58 | 49 |  |  |  | 21.405 | 46.7416 | 25.3366
2002 | 2 | 24 | 6 | 45 |  | 58 | 49 |  |  |  | 14.5101 | 31.6853 | 17.1752
2002 | 2 | 24 | 7 | 0 |  | 58 | 49 |  |  |  | 13.7801 | 30.0912 | 16.3111
2002 | 2 | 24 | 7 | 15 |  | 58 | 49 |  |  |  | 12.9382 | 28.2528 | 15.3146
2002 | 2 | 24 | 7 | 30 |  | 58 | 49 |  |  |  | 13.8094 | 30.1553 | 16.3459
2002 | 2 | 24 | 7 | 45 |  | 58 | 49 |  |  |  | 13.0817 | 28.5663 | 15.4845
2002 | 2 | 24 | 8 | 0 |  | 58 | 49 |  |  |  | 12.8893 | 28.1461 | 15.2568
2002 | 2 | 24 | 8 | 15 |  | 58 | 49 |  |  |  | 12.5132 | 27.3248 | 14.8116
2002 | 2 | 24 | 8 | 30 |  | 58 | 49 |  |  |  | 12.555 | 27.416 | 14.861
2002 | 2 | 24 | 8 | 45 |  | 58 | 49 |  |  |  | 13.0211 | 28.4339 | 15.4127
2002 | 2 | 24 | 9 | 0 |  | 58 | 49 |  |  |  | 13.1296 | 28.6707 | 15.5411
2002 | 2 | 24 | 9 | 15 |  | 58 | 49 |  |  |  | 12.809 | 27.9706 | 15.1617
2002 | 2 | 24 | 9 | 30 |  | 58 | 49 |  |  |  | 12.2742 | 26.8028 | 14.5286
2002 | 2 | 24 | 9 | 45 |  | 58 | 49 |  |  |  | 12.3005 | 26.8603 | 14.5598
2002 | 2 | 24 | 10 | 0 |  | 58 | 49 |  |  |  | 12.3334 | 26.9322 | 14.5987
2002 | 2 | 24 | 10 | 15 |  | 58 | 49 |  |  |  | 12.26 | 26.7719 | 14.5119
2002 | 2 | 24 | 10 | 30 |  | 58 | 49 |  |  |  | 11.4904 | 25.0912 | 13.6009
2002 | 2 | 24 | 10 | 45 |  | 58 | 49 |  |  |  | 11.1746 | 24.4017 | 13.2271
2002 | 2 | 24 | 11 | 0 |  | 58 | 49 |  |  |  | 10.0256 | 21.8926 | 11.867
2002 | 2 | 24 | 11 | 15 |  | 58 | 49 |  |  |  | 9.1199 | 19.9149 | 10.795
2002 | 2 | 24 | 11 | 30 |  | 58 | 49 |  |  |  | 8.6265 | 18.8374 | 10.2109
2002 | 2 | 24 | 11 | 45 |  | 58 | 49 |  |  |  | 6.3219 | 13.805 | 7.4831
2002 | 2 | 24 | 12 | 0 |  | 58 | 49 |  |  |  | 5.9542 | 13.002 | 7.0478
2002 | 2 | 24 | 12 | 15 |  | 58 | 49 |  |  |  | 6.6117 | 14.4378 | 7.8261
2002 | 2 | 24 | 12 | 30 |  | 58 | 49 |  |  |  | 6.3698 | 13.9096 | 7.5398
2002 | 2 | 24 | 12 | 45 |  | 58 | 49 |  |  |  | 8.6071 | 18.7951 | 10.188
2002 | 2 | 24 | 13 | 0 |  | 58 | 49 |  |  |  | 7.1973 | 15.7166 | 8.5193
2002 | 2 | 24 | 13 | 15 |  | 58 | 49 |  |  |  | 5.3197 | 11.6165 | 6.2968
2002 | 2 | 24 | 13 | 30 |  | 58 | 49 |  |  |  | 4.5199 | 9.8701 | 5.3501
2002 | 2 | 24 | 13 | 45 |  | 58 | 49 |  |  |  | 5.3887 | 11.7671 | 6.3784
2002 | 2 | 24 | 14 | 0 |  | 58 | 49 |  |  |  | 7.6393 | 16.6818 | 9.0425
2002 | 2 | 24 | 14 | 15 |  | 58 | 49 |  |  |  | 10.5053 | 22.9402 | 12.4349
2002 | 2 | 24 | 14 | 30 |  | 58 | 49 |  |  |  | 11.985 | 26.1713 | 14.1863
2002 | 2 | 24 | 14 | 45 |  | 58 | 49 |  |  |  | 10.7653 | 23.508 | 12.7426
2002 | 2 | 24 | 15 | 0 |  | 58 | 49 |  |  |  | 10.8276 | 23.6439 | 12.8163
2002 | 2 | 24 | 15 | 15 |  | 58 | 49 |  |  |  | 8.2748 | 18.0695 | 9.7947
2002 | 2 | 24 | 15 | 30 |  | 58 | 49 |  |  |  | 8.2812 | 18.0835 | 9.8023
2002 | 2 | 24 | 15 | 45 |  | 58 | 49 |  |  |  | 10.7702 | 23.5186 | 12.7484
2002 | 2 | 24 | 16 | 0 |  | 58 | 49 |  |  |  | 10.4992 | 22.9268 | 12.4276
2002 | 2 | 24 | 16 | 15 |  | 58 | 49 |  |  |  | 9.5642 | 20.8851 | 11.3209
2002 | 2 | 24 | 16 | 30 |  | 58 | 49 |  |  |  | 8.3295 | 18.1888 | 9.8594
2002 | 2 | 24 | 16 | 45 |  | 58 | 49 |  |  |  | 9.5967 | 20.9561 | 11.3594
2002 | 2 | 24 | 17 | 0 |  | 58 | 49 |  |  |  | 9.2086 | 20.1085 | 10.9
2002 | 2 | 24 | 17 | 15 |  | 58 | 49 |  |  |  | 8.3344 | 18.1997 | 9.8652
2002 | 2 | 24 | 17 | 30 |  | 58 | 49 |  |  |  | 7.9758 | 17.4166 | 9.4408
2002 | 2 | 24 | 17 | 45 |  | 58 | 49 |  |  |  | 8.328 | 18.1856 | 9.8576
2002 | 2 | 24 | 18 | 0 |  | 58 | 49 |  |  |  | 10.0715 | 21.9928 | 11.9213
2002 | 2 | 24 | 18 | 15 |  | 58 | 49 |  |  |  | 15.688 | 34.2575 | 18.5695
2002 | 2 | 25 | 4 | 30 | 4 | 30 | 77 |  |  |  | 14.5039 | 20.1548 | 5.6509 | 1129984.2536
2002 | 2 | 25 | 4 | 45 |  | 30 | 77 |  |  |  | 9.1374 | 12.6975 | 3.56
2002 | 2 | 25 | 5 | 0 |  | 30 | 77 |  |  |  | 6.114 | 8.4961 | 2.3821
2002 | 2 | 25 | 5 | 15 |  | 30 | 77 |  |  |  | 5.2013 | 7.2277 | 2.0265
2002 | 2 | 25 | 5 | 30 |  | 30 | 77 |  |  |  | 6.1924 | 8.6051 | 2.4126
2002 | 2 | 25 | 5 | 45 |  | 30 | 77 |  |  |  | 5.8127 | 8.0773 | 2.2647
2002 | 2 | 25 | 6 | 0 |  | 30 | 77 |  |  |  | 8.1264 | 11.2925 | 3.1661
2002 | 2 | 25 | 6 | 15 |  | 30 | 77 |  |  |  | 8.9046 | 12.3739 | 3.4693
2002 | 2 | 25 | 6 | 30 |  | 30 | 77 |  |  |  | 7.7128 | 10.7178 | 3.005
2002 | 2 | 25 | 6 | 45 |  | 30 | 77 |  |  |  | 7.6269 | 10.5985 | 2.9715
2002 | 2 | 25 | 7 | 0 |  | 30 | 77 |  |  |  | 7.1222 | 9.897 | 2.7749
2002 | 2 | 25 | 7 | 15 |  | 30 | 77 |  |  |  | 7.4423 | 10.342 | 2.8996
2002 | 2 | 25 | 7 | 30 |  | 30 | 77 |  |  |  | 6.7134 | 9.329 | 2.6156
2002 | 2 | 25 | 7 | 45 |  | 30 | 77 |  |  |  | 5.2193 | 7.2528 | 2.0335
2002 | 2 | 25 | 8 | 0 |  | 30 | 77 |  |  |  | 5.3046 | 7.3713 | 2.0667
2002 | 2 | 25 | 8 | 15 |  | 30 | 77 |  |  |  | 4.1757 | 5.8026 | 1.6269
2002 | 2 | 25 | 21 | 45 | 1.25 | 91 | 16 |  |  |  | 14.8783 | 99.4986 | 84.6203 | 184673.1022
2002 | 2 | 25 | 22 | 0 |  | 91 | 16 |  |  |  | 4.2805 | 28.6261 | 24.3456
2002 | 2 | 25 | 22 | 15 |  | 91 | 16 |  |  |  | 4.5061 | 30.1345 | 25.6284
2002 | 2 | 25 | 22 | 30 |  | 91 | 16 |  |  |  | 4.5299 | 30.2938 | 25.7638
2002 | 2 | 25 | 22 | 45 |  | 91 | 16 |  |  |  | 4.2752 | 28.5902 | 24.315
2002 | 2 | 25 | 23 | 0 | 1 | 74 | 33 |  |  |  | 6.5576 | 21.2625 | 14.7049 | 73801.7204
2002 | 2 | 25 | 23 | 15 |  | 74 | 33 |  |  |  | 8.5029 | 27.57 | 19.0671
2002 | 2 | 25 | 23 | 30 |  | 74 | 33 |  |  |  | 8.8403 | 28.6639 | 19.8236
2002 | 2 | 25 | 23 | 45 |  | 74 | 33 |  |  |  | 9.0108 | 29.217 | 20.2061
2002 | 2 | 26 | 0 | 0 | 2.25 | 62 | 45 |  |  |  | 11.4696 | 27.2722 | 15.8026 | 149734.174
2002 | 2 | 26 | 0 | 15 |  | 62 | 45 |  |  |  | 13.3316 | 31.6997 | 18.368
2002 | 2 | 26 | 0 | 30 |  | 62 | 45 |  |  |  | 13.6213 | 32.3883 | 18.7671
2002 | 2 | 26 | 0 | 45 |  | 62 | 45 |  |  |  | 13.0965 | 31.1405 | 18.044
2002 | 2 | 26 | 1 | 0 |  | 62 | 45 |  |  |  | 12.4149 | 29.5199 | 17.105
2002 | 2 | 26 | 1 | 15 |  | 62 | 45 |  |  |  | 12.4482 | 29.5991 | 17.1509
2002 | 2 | 26 | 1 | 30 |  | 62 | 45 |  |  |  | 12.2384 | 29.1001 | 16.8618
2002 | 2 | 26 | 1 | 45 |  | 62 | 45 |  |  |  | 10.6306 | 25.2772 | 14.6466
2002 | 2 | 26 | 2 | 0 |  | 62 | 45 |  |  |  | 9.4269 | 22.4152 | 12.9882
2002 | 2 | 26 | 2 | 15 | 2.75 | 20 | 87 |  |  |  | 9.5839 | 11.7871 | 2.2032 | 24091.0746
2002 | 2 | 26 | 2 | 30 |  | 20 | 87 |  |  |  | 9.2635 | 11.393 | 2.1295
2002 | 2 | 26 | 2 | 45 |  | 20 | 87 |  |  |  | 9.1209 | 11.2177 | 2.0968
2002 | 2 | 26 | 3 | 0 |  | 20 | 87 |  |  |  | 10.0302 | 12.3359 | 2.3058
2002 | 2 | 26 | 3 | 15 |  | 20 | 87 |  |  |  | 12.0686 | 14.843 | 2.7744
2002 | 2 | 26 | 3 | 30 |  | 20 | 87 |  |  |  | 9.7421 | 11.9816 | 2.2396
2002 | 2 | 26 | 3 | 45 |  | 20 | 87 |  |  |  | 9.1603 | 11.2661 | 2.1058
2002 | 2 | 26 | 4 | 0 |  | 20 | 87 |  |  |  | 8.1061 | 9.9696 | 1.8635
2002 | 2 | 26 | 4 | 15 |  | 20 | 87 |  |  |  | 9.7621 | 12.0063 | 2.2442
2002 | 2 | 26 | 4 | 30 |  | 20 | 87 |  |  |  | 10.1815 | 12.522 | 2.3406
2002 | 2 | 26 | 4 | 45 |  | 20 | 87 |  |  |  | 7.7771 | 9.5649 | 1.7878
2002 | 2 | 26 | 5 | 0 | 1.5 | 20 | 87 |  |  |  | 7.8801 | 9.6916 | 1.8115 | 17037.8761
2002 | 2 | 26 | 5 | 15 |  | 20 | 87 |  |  |  | 11.8298 | 14.5493 | 2.7195
2002 | 2 | 26 | 5 | 30 |  | 20 | 87 |  |  |  | 10.2758 | 12.638 | 2.3622
2002 | 2 | 26 | 5 | 45 |  | 20 | 87 |  |  |  | 10.5156 | 12.9329 | 2.4174
2002 | 2 | 26 | 6 | 0 |  | 20 | 87 |  |  |  | 16.5764 | 20.3871 | 3.8107
2002 | 2 | 26 | 6 | 15 |  | 20 | 87 |  |  |  | 17.0372 | 20.9537 | 3.9166
2002 | 2 | 26 | 6 | 30 | 2.5 | 38 | 69 |  |  |  | 11.5414 | 17.8975 | 6.3561 | 43994.7458
2002 | 2 | 26 | 6 | 45 |  | 38 | 69 |  |  |  | 11.0402 | 17.1203 | 6.0801
2002 | 2 | 26 | 7 | 0 |  | 38 | 69 |  |  |  | 11.4948 | 17.8252 | 6.3304
2002 | 2 | 26 | 7 | 15 |  | 38 | 69 |  |  |  | 7.4692 | 11.5827 | 4.1135
2002 | 2 | 26 | 7 | 30 |  | 38 | 69 |  |  |  | 6.9511 | 10.7792 | 3.8281
2002 | 2 | 26 | 7 | 45 |  | 38 | 69 |  |  |  | 9.3604 | 14.5154 | 5.155
2002 | 2 | 26 | 8 | 0 |  | 38 | 69 |  |  |  | 8.6953 | 13.484 | 4.7887
2002 | 2 | 26 | 8 | 15 |  | 38 | 69 |  |  |  | 11.8505 | 18.3768 | 6.5263
2002 | 2 | 26 | 8 | 30 |  | 38 | 69 |  |  |  | 1.2026 | 1.8648 | 0.66228
2002 | 2 | 26 | 8 | 45 |  | 38 | 69 |  |  |  | 0.27982 | 0.43393 | 0.15411
2002 | 2 | 26 | 9 | 0 | 12.25 | 107 | 0 |  |  |  | 0.28609 | 30.6115 | 30.3254 | 591725.6195
2002 | 2 | 26 | 9 | 15 |  | 107 | 0 |  |  |  | 0.16776 | 17.9501 | 17.7823
2002 | 2 | 26 | 9 | 30 |  | 107 | 0 |  |  |  | 0.326 | 34.8817 | 34.5557
2002 | 2 | 26 | 9 | 45 |  | 107 | 0 |  |  |  | 0.61954 | 66.2904 | 65.6709
2002 | 2 | 26 | 10 | 0 |  | 107 | 0 |  |  |  | 0.78431 | 83.9217 | 83.1374
2002 | 2 | 26 | 10 | 15 |  | 107 | 0 |  |  |  | 0.51138 | 54.7174 | 54.206
2002 | 2 | 26 | 10 | 30 |  | 107 | 0 |  |  |  | 0.43894 | 46.9663 | 46.5274
2002 | 2 | 26 | 10 | 45 |  | 107 | 0 |  |  |  | 0.45441 | 48.6217 | 48.1673
2002 | 2 | 26 | 11 | 0 |  | 107 | 0 |  |  |  | 0.46555 | 49.8142 | 49.3486
2002 | 2 | 26 | 11 | 15 |  | 107 | 0 |  |  |  | 0.71926 | 76.961 | 76.2417
2002 | 2 | 26 | 11 | 30 |  | 107 | 0 |  |  |  | 0.35392 | 37.8691 | 37.5151
2002 | 2 | 26 | 11 | 45 |  | 107 | 0 |  |  |  | 0.011769 | 1.2592 | 1.2475
2002 | 2 | 26 | 12 | 0 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 12 | 15 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 12 | 30 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 12 | 45 |  | 107 | 0 |  |  |  | 0.00063021 | 0.067432 | 0.066802
2002 | 2 | 26 | 13 | 0 |  | 107 | 0 |  |  |  | 0.073181 | 7.8304 | 7.7572
2002 | 2 | 26 | 13 | 15 |  | 107 | 0 |  |  |  | 0.053049 | 5.6762 | 5.6232
2002 | 2 | 26 | 13 | 30 |  | 107 | 0 |  |  |  | 0.10426 | 11.1557 | 11.0515
2002 | 2 | 26 | 13 | 45 |  | 107 | 0 |  |  |  | 4.8734e-05 | 0.0052145 | 0.0051658
2002 | 2 | 26 | 14 | 0 |  | 107 | 0 |  |  |  | 0.13106 | 14.0234 | 13.8923
2002 | 2 | 26 | 14 | 15 |  | 107 | 0 |  |  |  | 0.075676 | 8.0973 | 8.0216
2002 | 2 | 26 | 14 | 30 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 14 | 45 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 15 | 0 |  | 107 | 0 |  |  |  | 0.00094355 | 0.10096 | 0.10002
2002 | 2 | 26 | 15 | 15 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 15 | 30 |  | 107 | 0 |  |  |  | 0.0045523 | 0.4871 | 0.48254
2002 | 2 | 26 | 15 | 45 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 16 | 0 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 16 | 15 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 16 | 30 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 16 | 45 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 17 | 0 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 17 | 15 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 17 | 30 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 17 | 45 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 18 | 0 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 18 | 15 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 18 | 30 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 18 | 45 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 19 | 0 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 19 | 15 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 19 | 30 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 19 | 45 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 20 | 0 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 20 | 15 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 20 | 30 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 20 | 45 |  | 107 | 0 |  |  |  | 0 | 0 | 0
2002 | 2 | 26 | 21 | 0 |  | 107 | 0 |  |  |  | 0 | 0 | 0

## Curtailment Period Totals
Clear Sky Curtailments February 2001
Date curtailment started | Time started | Date curtailment lifted | Time lifted | Total hours | Turbines curtailed | # of turbines curtailed | Target turbine readings-start (kWH since commissioning) | Target turbine readings-finish (kWH since commissioning) | Target turbine yield (kWH) | Projected total loss (kWH) | Comments | Est total curtailed production (kWh) using 10-minute data | Est total curtailed production (kWh) using 15-minute data
2002-01-31 | 2400 | 2002-02-01 | 1000 | 10 | ? | 9 | 338090 | 341090 | 3000 | 27000 | CPS wanted 10 MW on 138 kV side, 5 MW on 69 kV side. 70 turbines were down due to sitewide cable splice retrofit. | 5518.4464 | 3593.6962
2002-02-05 | 600 | 2002-02-05 | 1900 | 13 | 1,2,3,4,8,13,14,15,114. | 9 | 286051 | 302004 | 15953 | 143577 | CPS wanted 15 MW on 69 kV side. 20 turbines were down due to sitewide cable splice retrofit. | 25607.602 | 36686.8524
2002-02-05 | 1730 | 2002-02-05 | 2200 | 4.5 | 65,71,78,81,100,103,105,115,116,106,107,121,122,72-77,69,70. | 21 | 424115 | 427271 | 3156 | 66276 | CPS wanted 15 MW on 69 kV side. | 25364.561 | 61025.3837
2002-02-05 | 1900 | 2002-02-05 | 2200 | 3 | 1-5,7-9,13,14,17,18,20-23,25-30,56,59. | 24 | 28376 | 30478 | 2102 | 50448 | CPS wanted 20 MW on 138 kV side. | 19724.6169 | 41454.9424
2002-02-09 | 2300 | 2002-02-10 | 830 | 9.5 | ? | 75 | 367478 | 383628 | 16150 | 1211250 | CPS wanted 20 MW each side | 800419.4141 | 582487.0711
2002-02-10 | 1045 | 2002-02-10 | 1230 | 1.75 | 2,3,4,6,9,14,15,114 | 8 | 355830 | 357580 | 1750 | 14000 | CPS wanted 45 MW on 138 kV side. | 6216.3529 | 12051.7785
2002-02-14 | 700 | 2002-02-14 | 2400 | 17 | 1-5, 7-9, 13-15, 17-27, 29-40, 60-70, 78-93. | 61 | 669369 | 692659 | 23290 | 1420690 | CPS wanted 30 MW per line. | 1026324.6906 | 1586719.2231
2002-02-14 | 2400 | 2002-02-15 | 600 | 6 | 1-5, 7-9, 13-15, 17-27, 29-40, 60-70, 78-93. | 61 | 692659 | 706260 | 13601 | 829661 | CPS wanted 30 MW per line. | 478482.4529 | 405464.7364
2002-02-15 | 600 | 2002-02-15 | 800 | 2 | 81-93 | 13 | 439707 | 441908 | 2201 | 28613 | CPS wanted 40 MW per line. | 15285.1349 | 25167.2673
2002-02-16 | 2115 | 2002-02-16 | 2345 | 2.5 | 1-5, 7-9, 13-15, 17-31, 49-93, 108, 114, 115, 117, 118 | 75 | 132731 | 136643 | 3912 | 293400 | CPS wanted 10 MW per line | 149241.5234 | 248282.8781
2002-02-18 | 1950 | 2002-02-18 | 2300 | 3.5 | 60,61,63-93,96 | 33 | 345600 | 351725 | 6125 | 202125 | CPS wanted 25 MW on 69kV side | 99086.6399 | 60822.2385
2002-02-18 | 2300 | 2002-02-18 | 2400 | 1 | 84-93,96 | 11 | 351725 | 353425 | 1700 | 18700 | CPS wanted 30 MW per line. | 7529.5038 | 3427.1665
2002-02-19 | 200 | 2002-02-19 | 430 | 2.5 | 26,27,28-32,34,36,38,40,42,45-47,51-58,80,81,83-87,89-93,96,106-108,115,117-122 | 46 | 320400 | 324650 | 4250 | 195500 | CPS wanted 30MW per line | 93702.7918 | 131495.9936
2002-02-19 | 430 | 2002-02-19 | 830 | 4 | 26,27,28-32,34,36,38,40,42,45-47,51-58,80,81,83-87,89-93,96,106-108,115,117-122, 74-79 | 52 | 324650 | 331634 | 6984 | 363168 | Maintain 30MW per line | 140430.223 | 241364.3232
2002-02-19 | 830 | 2002-02-19 | 1015 | 1.75 | 26,27,28-32,34,36,38,40,42,45-47,51-58,80,81,83-87,89-93,96,106-108,115,117-122, 74-80, 2-4, 5, 7-9, 14, 21, 23, 25,26,60 | 65 | 571712 | 574261 | 2549 | 165685 | Maintain 30MW per line | 180675.754 | 154980.0525
2002-02-19 | 1015 | 2002-02-19 | 1415 | 4 | 26,27,28-32,34,36,38,40,42,45-47,51-58,80,81,83-87,89-93,96,106-108,115,117-122, 74-80, 2-4, 5, 7-9, 14, 21, 23, 25,26,61,108,114,115 | 68 | 574261 | 578629 | 4368 | 297024 | Maintain 30MW per line | 455441.2171 | 439851.3168
2002-02-19 | 1415 | 2002-02-19 | 1600 | 1.75 | 26,27,28-32,34,36,38,40,42,45-47,51-58,80,81,83-87,89-93,96,106-108,115,117-122, 2-4, 5, 7-9, 14, 21, 23, 25,26,61,108,114,116 | 61 | 480101 | 481724 | 1623 | 99003 | Maintain 30MW per line | 132727.7341 | 147021.6059
2002-02-19 | 1600 | 2002-02-19 | 2250 | 6.5 | 26,27,28-32,34,36,38,40,42,45-47,51-58,80,81,83-87,89-93,96,106-108,115,117-122, 2-4, 5, 7-9, 14, 21, 23, 25,26,61,108,114,117,41,43, 44,62,63,65,66,68,69 | 70 | 481724 | 491188 | 9464 | 662480 | Maintain 30MW per line | 679762.7793 | 761310.3022
2/20/02 | 2400 | 2/21/02 | 200 | 2 | 108,109,113,114,115,118,119,121,122 | 9 | 502072 | 503699 | 1627 | 14643 | CPS wanted 30MW per line | 1837.0026 | 10079.8851
2002-02-21 | 200 | 2002-02-21 | 600 | 4 | 108,109,113,114,115,118,119,121,102,122,107,100,96,93,88-91,1-5,7-9 | 26 | 503699 | 506242 | 2543 | 66118 | Maintain 30MW per line | 39317.3444 | 58197.7169
2002-02-21 | 600 | 2002-02-21 | 630 | 0.5 | 108,109,113,114,115,118,119,121,102,122,107,100,96,93, 88-91,1-5, 7-9,13,14,15,17,18,21,23,25 27-31 | 39 | 506242 | 507194 | 952 | 37128 | Maintain 30MW per line | 13892.4213 | 10613.8228
2002-02-21 | 630 | 2002-02-21 | 830 | 2 | 108,109,113,114,115,118,119,121,102,122,107,100,96,93, 1-5, 7-9,13,14,15,17,18,21,23,25,24 | 31 | 507194 | 508788 | 1594 | 49414 | Maintain 30MW per line | 41300.6406 | 33401.8797
2002-02-21 | 945 | 2002-02-21 | 1045 | 1 | 1,2,3,5,7,8,9,13,14,15,18 | 11 | 683503 | 685003 | 1500 | 16500 | CPS wanted 30MW on 138kV side. | 4390.6576 | 7720.6697
2002-02-21 | 1045 | 2002-02-21 | 1200 | 1.25 | 1,2,3,5,7,8,9,13,14,15,18,20-24,28,29,31-41,60-63,65,66,6869-70 | 27 | 685003 | 686512 | 1509 | 40743 | CPS wanted 30MW on 138kV side. | 22021.9031 | 30135.3444
2002-02-21 | 1200 | 2002-02-21 | 1615 | 4.25 | 1,2,3,5,7,8,9,13,14,15,18,20-24,28,29,31-41,60-63,65,66,6869-70, 71-90,25,27,42,89,92,93 | 53 | 686512 | 691573 | 5061 | 268233 | CPS wanted 30 MW per line. | 191338.0481 | 213415.134
2002-02-21 | 1615 | 2/2/102 | 1800 | 1.75 | 31-41,81-90,25,27,42,89,92,93 | 27 | 691573 | 693663 | 2090 | 56430 | Curtailment lifted at 1800 | 39386.1825 | 29093.9858
2002-02-23 | 2015 | 2002-02-23 | 2400 | 3.75 | 1-5,7,8,13-15,17,19,20-22,24-27,29-42,61-66,69-71,73-76,79-86,89-93 | 58 | 573961 | 579698 | 5737 | 332746 | CPS wanted 30 MW per line. | 123499.2816 | 420326.7197
2002-02-23 | 2400 | 2002-02-24 | 1830 | 6.5 | 1-5,7,8,13-15,17,19,20-22,24-27,29-42,61-66,69-71,73-76,79-86,89-93 | 58 | 579698 | 608003 | 28305 | 1641690 | Curtailment lifted at 1830 | 1687565.0803 | 1322921.201
2002-02-25 | 430 | 2002-02-25 | 830 | 4 | 49-59,39-47,105,107,88-93,96,100 | 30 | 574830 | 577390 | 2560 | 76800 | CPS wanted 20MW per line | 91285.8442 | 1129984.2536
2002-02-25 | 2145 | 2002-02-25 | 2300 | 1.25 | 9,13-15,17-47,49-59,69-75,77-90,93,96,100,102-109,133-122 | 91 | 178487 | 179892 | 1405 | 127855 | CPS wanted 10MW per line | 14661.6167 | 184673.1022
2002-02-25 | 2300 | 2002-02-25 | 2400 | 1 | 19-47,49-59,79-90,93,96,100,102-109,113-122 | 74 | 179892 | 180534 | 642 | 47508 | CPS wanted 20MW per line | 3318.6384 | 73801.7204
2002-02-25 | 2400 | 2002-02-26 | 215 | 2.25 | 39-47,49-59,96,100,102-109,113-122 | 62 | 180534 | 183548 | 3014 | 186868 | Maintain 20MW per line | 58877.083 | 149734.174
2002-02-26 | 215 | 2/26/02 | 500 | 2.75 | 39-47,49-59 | 20 | 183548 | 186581 | 3033 | 60660 | CPS wanted 30 MW per line. | 27924.6437 | 24091.0746
2002-02-26 | 500 | 2002-02-26 | 630 | 1.5 | 39-47,49-59 | 20 | 186581 | 187612 | 1031 | 20620 | Maintain 30MW per line | 12035.0805 | 17037.8761
2002-02-26 | 630 | 2002-02-26 | 900 | 2.5 | 39-47,49-59,4,5,7,8,113-119,121,122,9,13,14,15,17 | 38 | 187612 | 189737 | 2125 | 80750 | CPS wanted 20MW per line | 62450.3565 | 43994.7458
2002-02-26 | 900 | 2002-02-26 | 2115 | 12.25 | ENTIRE SITE | 107 | N/A | N/A | N/A | N/A | CPS needed the entire site down, they agreed to pay us as if each turbine was at full power the entire time | 594003.2826 | 591725.6195
[10 empty] | 9213306 | Total of curtailment periods: | 7370646.5457 | 9294155.7537

## Problems-Limitations
Notes on database production provided by vendor:
Time stamps for each 10-minute period didn't match across all turbines.
Time stamps for each 10-minute period varied as to interval. Usually they were 10-min, often 9-min, and sometimes less.
No turbines have a record for every 10-minute period during the month.
---The minimum number of turbines reporting for any 10-minute period in the month was 3, the maximum was 103
Database provided with: Turbine #, Date/Time stamp, kW, Nacelle Wind Speed. No indication of turbine status.
Example of problem period: The entire wind farm was listed as curtailed (see previous worksheet, Row 38), but you can see there was production for several hours after curtailment was scheduled to begin.
Year | Mo | Day | Hour | Min | Hours of curtailment | No of turbines curtailed | No of turbines not curtailed | Wind speed at Site 653 (mph) | Wind speed adjusted to hub-height (mps) | Est production per turbine, (kWh) | Actual Total Production(kWh) | Pro-Rated Total Production(kWh) | Est total curtailed production (kWh)
2002 | 2 | 26 | 9 | 0 | 12.25 | 107 | 0 |  |  |  | 5936.85 | 635242.95 | 629306.1 | Note the production when all turbines were reported curtailed
2002 | 2 | 26 | 9 | 10 |  | 107 | 0 |  |  |  | 5790.6 | 619594.2 | 613803.6 | Checking individual records, approximately 49 turbines were operating from 0900-1450
2002 | 2 | 26 | 9 | 20 |  | 107 | 0 |  |  |  | 5794.5667 | 620018.6333 | 614224.0667
2002 | 2 | 26 | 9 | 30 |  | 107 | 0 |  |  |  | 7486.9 | 801098.3 | 793611.4
2002 | 2 | 26 | 9 | 40 |  | 107 | 0 |  |  |  | 7707.15 | 824665.05 | 816957.9
2002 | 2 | 26 | 9 | 50 |  | 107 | 0 |  |  |  | 6596.5833 | 705834.4167 | 699237.8333
2002 | 2 | 26 | 10 | 0 |  | 107 | 0 |  |  |  | 6316.6667 | 675883.3333 | 669566.6667
2002 | 2 | 26 | 10 | 10 |  | 107 | 0 |  |  |  | 5742.8667 | 614486.7333 | 608743.8667
2002 | 2 | 26 | 10 | 20 |  | 107 | 0 |  |  |  | 5513.5667 | 589951.6333 | 584438.0667
2002 | 2 | 26 | 10 | 30 |  | 107 | 0 |  |  |  | 5350.2833 | 572480.3167 | 567130.0333
2002 | 2 | 26 | 10 | 40 |  | 107 | 0 |  |  |  | 6549.1333 | 700757.2667 | 694208.1333
2002 | 2 | 26 | 10 | 50 |  | 107 | 0 |  |  |  | 6974.9833 | 746323.2167 | 739348.2333
2002 | 2 | 26 | 11 | 0 |  | 107 | 0 |  |  |  | 6091.8167 | 651824.3833 | 645732.5667
2002 | 2 | 26 | 11 | 10 |  | 107 | 0 |  |  |  | 5018.75 | 537006.25 | 531987.5
2002 | 2 | 26 | 11 | 20 |  | 107 | 0 |  |  |  | 4735.2 | 506666.4 | 501931.2
2002 | 2 | 26 | 11 | 30 |  | 107 | 0 |  |  |  | 5891.7333 | 630415.4667 | 624523.7333
2002 | 2 | 26 | 11 | 40 |  | 107 | 0 |  |  |  | 7506.2333 | 803166.9667 | 795660.7333
2002 | 2 | 26 | 11 | 50 |  | 107 | 0 |  |  |  | 6807.6833 | 728422.1167 | 721614.4333
2002 | 2 | 26 | 12 | 0 |  | 107 | 0 |  |  |  | 6266.5 | 670515.5 | 664249
2002 | 2 | 26 | 12 | 10 |  | 107 | 0 |  |  |  | 6607.1 | 706959.7 | 700352.6
2002 | 2 | 26 | 12 | 20 |  | 107 | 0 |  |  |  | 9229.2333 | 987527.9667 | 978298.7333
2002 | 2 | 26 | 12 | 30 |  | 107 | 0 |  |  |  | 11116.15 | 1189428.05 | 1178311.9
2002 | 2 | 26 | 12 | 40 |  | 107 | 0 |  |  |  | 10535.2833 | 1127275.3167 | 1116740.0333
2002 | 2 | 26 | 12 | 50 |  | 107 | 0 |  |  |  | 8359.1667 | 894430.8333 | 886071.6667
2002 | 2 | 26 | 13 | 0 |  | 107 | 0 |  |  |  | 5907.45 | 632097.15 | 626189.7
2002 | 2 | 26 | 13 | 10 |  | 107 | 0 |  |  |  | 7238.7333 | 774544.4667 | 767305.7333
2002 | 2 | 26 | 13 | 20 |  | 107 | 0 |  |  |  | 8401.3 | 898939.1 | 890537.8
2002 | 2 | 26 | 13 | 30 |  | 107 | 0 |  |  |  | 6138.7 | 656840.9 | 650702.2
2002 | 2 | 26 | 13 | 40 |  | 107 | 0 |  |  |  | 5073.2667 | 542839.5333 | 537766.2667
2002 | 2 | 26 | 13 | 50 |  | 107 | 0 |  |  |  | 4681.2833 | 500897.3167 | 496216.0333
2002 | 2 | 26 | 14 | 0 |  | 107 | 0 |  |  |  | 5239.3167 | 560606.8833 | 555367.5667
2002 | 2 | 26 | 14 | 10 |  | 107 | 0 |  |  |  | 6339.1167 | 678285.4833 | 671946.3667
2002 | 2 | 26 | 14 | 20 |  | 107 | 0 |  |  |  | 6552.55 | 701122.85 | 694570.3
2002 | 2 | 26 | 14 | 30 |  | 107 | 0 |  |  |  | 6253.95 | 669172.65 | 662918.7
2002 | 2 | 26 | 14 | 40 |  | 107 | 0 |  |  |  | 7440.7 | 796154.9 | 788714.2
2002 | 2 | 26 | 14 | 50 |  | 107 | 0 |  |  |  | 1886.7833 | 201885.8167 | 199999.0333
2002 | 2 | 26 | 15 | 0 |  | 107 | 0 |  |  |  | 521.2667 | 55775.5333 | 55254.2667
2002 | 2 | 26 | 15 | 10 |  | 107 | 0 |  |  |  | 589.4333 | 63069.3667 | 62479.9333
2002 | 2 | 26 | 15 | 20 |  | 107 | 0 |  |  |  | 448.3167 | 47969.8833 | 47521.5667
2002 | 2 | 26 | 15 | 30 |  | 107 | 0 |  |  |  | 550.8 | 58935.6 | 58384.8
2002 | 2 | 26 | 15 | 40 |  | 107 | 0 |  |  |  | 464.7333 | 49726.4667 | 49261.7333
2002 | 2 | 26 | 15 | 50 |  | 107 | 0 |  |  |  | 467.75 | 50049.25 | 49581.5
2002 | 2 | 26 | 16 | 0 |  | 107 | 0 |  |  |  | 708.4167 | 75800.5833 | 75092.1667
2002 | 2 | 26 | 16 | 10 |  | 107 | 0 |  |  |  | 587.9833 | 62914.2167 | 62326.2333
2002 | 2 | 26 | 16 | 20 |  | 107 | 0 |  |  |  | 515.9833 | 55210.2167 | 54694.2333
2002 | 2 | 26 | 16 | 30 |  | 107 | 0 |  |  |  | 438.45 | 46914.15 | 46475.7
2002 | 2 | 26 | 16 | 40 |  | 107 | 0 |  |  |  | 178.7833 | 19129.8167 | 18951.0333
2002 | 2 | 26 | 16 | 50 |  | 107 | 0 |  |  |  | 169.6333 | 18150.7667 | 17981.1333
2002 | 2 | 26 | 17 | 0 |  | 107 | 0 |  |  |  | 276 | 29532 | 29256
2002 | 2 | 26 | 17 | 10 |  | 107 | 0 |  |  |  | 334.1667 | 35755.8333 | 35421.6667
2002 | 2 | 26 | 17 | 20 |  | 107 | 0 |  |  |  | 299.75 | 32073.25 | 31773.5
2002 | 2 | 26 | 17 | 30 |  | 107 | 0 |  |  |  | 423.25 | 45287.75 | 44864.5
2002 | 2 | 26 | 17 | 40 |  | 107 | 0 |  |  |  | 359.3833 | 38454.0167 | 38094.6333
2002 | 2 | 26 | 17 | 50 |  | 107 | 0 |  |  |  | 204.0833 | 21836.9167 | 21632.8333
2002 | 2 | 26 | 18 | 0 |  | 107 | 0 |  |  |  | -38.3667 | -4105.2333 | -4066.8667 | At this point all turbines were off, though there are only production records for 100
2002 | 2 | 26 | 18 | 10 |  | 107 | 0 |  |  |  | -42.5667 | -4554.6333 | -4512.0667
2002 | 2 | 26 | 18 | 20 |  | 107 | 0 |  |  |  | -44.5667 | -4768.6333 | -4724.0667
2002 | 2 | 26 | 18 | 30 |  | 107 | 0 |  |  |  | -44.4667 | -4757.9333 | -4713.4667
2002 | 2 | 26 | 18 | 40 |  | 107 | 0 |  |  |  | -44.9667 | -4811.4333 | -4766.4667
2002 | 2 | 26 | 18 | 50 |  | 107 | 0 |  |  |  | -45.6 | -4879.2 | -4833.6
2002 | 2 | 26 | 19 | 0 |  | 107 | 0 |  |  |  | -44.2167 | -4731.1833 | -4686.9667
2002 | 2 | 26 | 19 | 10 |  | 107 | 0 |  |  |  | -45.3 | -4847.1 | -4801.8
2002 | 2 | 26 | 19 | 20 |  | 107 | 0 |  |  |  | 30.9833 | 3315.2167 | 3284.2333
2002 | 2 | 26 | 19 | 30 |  | 107 | 0 |  |  |  | 74.7667 | 8000.0333 | 7925.2667
2002 | 2 | 26 | 19 | 40 |  | 107 | 0 |  |  |  | 50.05 | 5355.35 | 5305.3
2002 | 2 | 26 | 19 | 50 |  | 107 | 0 |  |  |  | 91.9 | 9833.3 | 9741.4
2002 | 2 | 26 | 20 | 0 |  | 107 | 0 |  |  |  | 126.4167 | 13526.5833 | 13400.1667
2002 | 2 | 26 | 20 | 10 |  | 107 | 0 |  |  |  | -47.75 | -5109.25 | -5061.5
2002 | 2 | 26 | 20 | 20 |  | 107 | 0 |  |  |  | 93.5667 | 10011.6333 | 9918.0667
2002 | 2 | 26 | 20 | 30 |  | 107 | 0 |  |  |  | 51.0667 | 5464.1333 | 5413.0667
2002 | 2 | 26 | 20 | 40 |  | 107 | 0 |  |  |  | 75.5333 | 8082.0667 | 8006.5333
2002 | 2 | 26 | 20 | 50 |  | 107 | 0 |  |  |  | -45.8833 | -4909.5167 | -4863.6333
2002 | 2 | 26 | 21 | 0 |  | 107 | 0 |  |  |  | -47.7333 | -5107.4667 | -5059.7333
2002 | 2 | 26 | 21 | 10 |  | 107 | 0 |  |  |  | -49.2 | -5264.4 | -5215.2

## Curtailment Periods - Hourly
Clear Sky Curtailment Worksheet
2002-02-01 | [8 empty] | Monthly Totals from columns below: |  |  |  | 6653019.5541 |  |  | 6683511.2068 | 30491.6526 | 0.4562% | The overall result for the whole month
Note that while individual time period differences can range from a few to over 100,000,
[12 empty] | Based on Wind Speed |  |  | Based on Turb Data¦ |  |  |  | the month as a whole is very close. There may be problems with the time stamp or turbine figures.
Year | Mo | Day | Hour | Min | Hours of curtailment | No of turbines curtailed | No of turbines not curtailed | Wind speed at Site 653 (mph) | Wind speed adjusted to hub-height (mps) | Est production per turbine, (kWh) | Actual Total Production (kWh) | Pro-Rated Total Production (kWh) | Est total curtailed production (kWh) | Actual Total Production (kWh) | Pro-Rated Total Production (kWh) | Est total curtailed production (kWh) | Difference between techniques, kWh |  |  | Wind Speed, mps | EWC 1.5 MW Turbine Power Curve, kW
2002 | 2 | 1 | 0 | 0 | 1 | 9 | 98 | 17.46 | 8.6943 | 622.6732 |  |  | 5043.6532 | 7878.45 | 8601.9811 | 723.5311 | -4320.122 |  |  | 0 | 0
2002 | 2 | 1 | 1 | 0 | 1 | 9 | 98 | 18.75 | 9.3367 | 781.2592 |  |  | 6328.1997 | 7110.8333 | 7763.869 | 653.0357 | -5675.164 |  |  | 1 | 0
2002 | 2 | 1 | 2 | 0 | 1 | 9 | 98 | 18.32 | 9.1226 | 722.5898 |  |  | 5852.9775 | 6535.1 | 7135.2622 | 600.1622 | -5252.8152 |  |  | 2 | 0
2002 | 2 | 1 | 3 | 0 | 1 | 9 | 98 | 8.48 | 4.2227 | 45.1383 |  |  | 365.6206 | 5989.8667 | 6539.9565 | 550.0898 | 184.4692 |  |  | 3 | 7
2002 | 2 | 1 | 4 | 0 | 1 | 9 | 98 | 14.52 | 7.2304 | 345.0078 |  |  | 2794.563 | 6458.5833 | 7051.7185 | 593.1352 | -2201.4278 |  |  | 4 | 32
2002 | 2 | 1 | 5 | 0 | 1 | 9 | 98 | 6.39 | 3.182 | 11.5488 |  |  | 93.5452 | 5248.95 | 5730.9964 | 482.0464 | 388.5012 |  |  | 5 | 91
2002 | 2 | 1 | 6 | 0 | 1 | 9 | 98 | 3.4 | 1.6931 | 0 |  |  | 0 | 5843.25 | 6379.875 | 536.625 | 536.625 |  |  | 6 | 182
2002 | 2 | 1 | 7 | 0 | 1 | 9 | 98 | 1.48 | 0.73698 | 0 |  |  | 0 | 5797.9333 | 6330.3966 | 532.4633 | 532.4633 |  |  | 7 | 307
2002 | 2 | 1 | 8 | 0 | 1 | 9 | 98 | 3.51 | 1.7478 | 0 |  |  | 0 | 4857.9 | 5304.0337 | 446.1337 | 446.1337 |  |  | 8 | 472
2002 | 2 | 1 | 9 | 0 | 1 | 9 | 98 | 4.26 | 2.1213 | 0.84911 |  |  | 6.8778 | 4368.8833 | 4770.1073 | 401.224 | 394.3462 |  |  | 9 | 689
[20 empty] | 10 | 963
2002 | 2 | 5 | 6 | 0 | 1 | 9 | 98 | 17.62 | 8.774 | 639.9623 |  |  | 5183.6949 | 9879.2333 | 10786.5099 | 907.2765 | -4276.4184 |  |  | 11 | 1232
2002 | 2 | 5 | 7 | 0 | 1 | 9 | 98 | 16.71 | 8.3209 | 541.6306 |  |  | 4387.2076 | 10324.6 | 11272.7776 | 948.1776 | -3439.03 |  |  | 12 | 1406
2002 | 2 | 5 | 8 | 0 | 1 | 9 | 98 | 17.03 | 8.4802 | 576.2088 |  |  | 4667.291 | 20774.9333 | 22682.8354 | 1907.902 | -2759.389 |  |  | 13 | 1477
2002 | 2 | 5 | 9 | 0 | 1 | 9 | 98 | 14.9 | 7.4196 | 376.2297 |  |  | 3047.4609 | 33123.95 | 36165.9454 | 3041.9954 | -5.4655 |  |  | 14 | 1497
2002 | 2 | 5 | 10 | 0 | 1 | 9 | 98 | 13.08 | 6.5133 | 246.1613 |  |  | 1993.9068 | 30310.95 | 33094.6087 | 2783.6587 | 789.7519 |  |  | 15 | 1500
2002 | 2 | 5 | 11 | 0 | 1 | 9 | 98 | 9.55 | 4.7555 | 76.5744 |  |  | 620.2529 | 23985.2667 | 26187.9952 | 2202.7286 | 1582.4756 |  |  | 16 | 1500
2002 | 2 | 5 | 12 | 0 | 1 | 9 | 98 | 9.98 | 4.9696 | 89.2076 |  |  | 722.5818 | 22864.2667 | 24964.0463 | 2099.7796 | 1377.1978 |  |  | 17 | 1500
2002 | 2 | 5 | 13 | 0 | 1 | 9 | 98 | 7.62 | 3.7944 | 26.861 |  |  | 217.5741 | 16271.0167 | 17765.2937 | 1494.277 | 1276.7029 |  |  | 18 | 1500
2002 | 2 | 5 | 14 | 0 | 1 | 9 | 98 | 12.01 | 5.9805 | 180.2233 |  |  | 1459.8086 | 15664.6833 | 17103.2767 | 1438.5934 | -21.2152 |  |  | 19 | 1500
2002 | 2 | 5 | 15 | 0 | 1 | 9 | 98 | 15.8 | 7.8677 | 450.1765 |  |  | 3646.4297 | 21581.6833 | 23563.6747 | 1981.9913 | -1664.4384 |  |  | 20 | 1500
2002 | 2 | 5 | 16 | 0 | 1 | 9 | 98 | 17.94 | 8.9334 | 674.5405 |  |  | 5463.7783 | 26353.4833 | 28773.7012 | 2420.2179 | -3043.5605 |  |  | 21 | 1500
2002 | 2 | 5 | 17 | 0 | 1 | 9 | 98 | 19.49 | 9.7052 | 882.2252 |  |  | 7146.024 | 23070.7167 | 25189.456 | 2118.7393 | -5027.2847 |  |  | 22 | 1500
2002 | 2 | 5 | 18 | 0 | 1 | 9 | 98 | 22.81 | 11.3584 | 1294.3654 |  |  | 10484.3599 | 24633.55 | 26895.8148 | 2262.2648 | -8222.0951 |  |  | 23 | 1500
[20 empty] | 24 | 1500
2002 | 2 | 5 | 17 | 30 | 1 | 21 | 86 | 19.49 | 9.7052 | 882.2252 |  |  | 16674.0561 | 23133.5333 | 28782.4194 | 5648.886 | -11025.17 |  |  | 25 | 1500
2002 | 2 | 5 | 18 | 30 | 1 | 21 | 86 | 22.81 | 11.3584 | 1294.3654 |  |  | 24463.5065 | 25354.9167 | 31546.2335 | 6191.3169 | -18272.1897 |  |  | 26 | 0
2002 | 2 | 5 | 19 | 30 | 1 | 21 | 86 | 23.77 | 11.8365 | 1377.5443 |  |  | 26035.5878 | 19074.3167 | 23731.9986 | 4657.682 | -21377.9058 |  |  | 27 | 0
2002 | 2 | 5 | 20 | 30 | 1 | 21 | 86 | 22.49 | 11.1991 | 1266.6391 |  |  | 23939.4794 | 23931.7667 | 29775.5702 | 5843.8035 | -18095.6759 |  |  | 28 | 0
2002 | 2 | 5 | 21 | 30 | 0.5 | 21 | 86 | 24.25 | 12.0755 | 1411.3592 |  |  | 13337.3443 | 12379.3833 | 15402.256 | 3022.8727 | -10314.4716 |  |  | 29 | 0
[20 empty] | 30 | 0
2002 | 2 | 5 | 19 | 0 | 1 | 24 | 83 | 23.77 | 11.8365 | 1377.5443 |  |  | 29754.9575 | 22179.95 | 28593.4295 | 6413.4795 | -23341.478 |  |  | 31 | 0
2002 | 2 | 5 | 20 | 0 | 1 | 24 | 83 | 22.49 | 11.1991 | 1266.6391 |  |  | 27359.4051 | 21276.8 | 27429.1277 | 6152.3277 | -21207.0773 |  |  | 32 | 0
2002 | 2 | 5 | 21 | 0 | 1 | 24 | 83 | 24.25 | 12.0755 | 1411.3592 |  |  | 30485.3584 | 24757.55 | 31916.3596 | 7158.8096 | -23326.5488 |  |  | 33 | 0
[20 empty] | 34 | 0
2002 | 2 | 9 | 23 | 0 | 1 | 75 | 32 | 21.79 | 10.8505 | 1191.7858 |  |  | 80445.5413 | 48205.6833 | 161187.7536 | 112982.0703 | 32536.529 |  |  | 35 | 0
2002 | 2 | 10 | 0 | 0 | 1 | 75 | 32 | 21.26 | 10.5866 | 1120.7919 |  |  | 75653.4549 | 41694.7667 | 139416.876 | 97722.1094 | 22068.6545 |  |  | 36 | 0
2002 | 2 | 10 | 1 | 0 | 1 | 75 | 32 | 25.38 | 12.6382 | 1451.3104 |  |  | 97963.4491 | 40293.3167 | 134730.7776 | 94437.4609 | -3525.9881 |  |  | 37 | 0
2002 | 2 | 10 | 2 | 0 | 1 | 75 | 32 | 24.52 | 12.2099 | 1420.905 |  |  | 95911.0903 | 29606.5333 | 98996.8458 | 69390.3125 | -26520.7778 |  |  | 38 | 0
2002 | 2 | 10 | 3 | 0 | 1 | 75 | 32 | 23.99 | 11.946 | 1396.6062 |  |  | 94270.9159 | 32983.4167 | 110288.2995 | 77304.8828 | -16966.0331 |  |  | 39 | 0
2002 | 2 | 10 | 4 | 0 | 1 | 75 | 32 | 23.4 | 11.6522 | 1345.4858 |  |  | 90820.291 | 46890.3 | 156789.4406 | 109899.1406 | 19078.8496 |  |  | 40 | 0
2002 | 2 | 10 | 5 | 0 | 1 | 75 | 32 | 26.5 | 13.1959 | 1480.9177 |  |  | 99961.9475 | 40935.4667 | 136877.9667 | 95942.5 | -4019.4475 |  |  | 41 | 0
2002 | 2 | 10 | 6 | 0 | 1 | 75 | 32 | 25.38 | 12.6382 | 1451.3104 |  |  | 97963.4491 | 26911.4833 | 89985.2724 | 63073.7891 | -34889.66 |  |  | 42 | 0
2002 | 2 | 10 | 7 | 0 | 1 | 75 | 32 | 22.33 | 11.1194 | 1252.776 |  |  | 84562.3781 | 23010.4833 | 76941.3036 | 53930.8203 | -30631.5578 |  |  | 43 | 0
2002 | 2 | 10 | 8 | 0 | 0.5 | 75 | 32 | 22.38 | 11.1443 | 1257.1082 |  |  | 42427.402 | 10980.8333 | 36717.1615 | 25736.3281 | -16691.0739 |  |  | 44 | 0
[20 empty] | 45 | 0
2002 | 2 | 10 | 10 | 40 | 1 | 8 | 99 | 24.36 | 12.1303 | 1415.2482 |  |  | 10189.7873 | 41359.2 | 44701.3576 | 3342.1576 | -6847.6297 |  |  | 46 | 0
2002 | 2 | 10 | 11 | 40 | 0.75 | 8 | 99 | 25 | 12.449 | 1437.8755 |  |  | 7764.5274 | 28571.0167 | 30879.7857 | 2308.769 | -5455.7584 |  |  | 47 | 0
[20 empty] | 48 | 0
2002 | 2 | 14 | 7 | 0 | 1 | 61 | 46 | 16.18 | 8.057 | 484.3604 |  |  | 26591.3868 | 25539.8833 | 59407.9895 | 33868.1062 | 7276.7193 |  |  | 49 | 0
2002 | 2 | 14 | 8 | 0 | 1 | 61 | 46 | 18.32 | 9.1226 | 722.5898 |  |  | 39670.1808 | 22344.9167 | 51976.2192 | 29631.3025 | -10038.8782 |  |  | 50 | 0
2002 | 2 | 14 | 9 | 0 | 1 | 61 | 46 | 20.94 | 10.4272 | 1077.9277 |  |  | 59178.2307 | 24482.55 | 56948.5402 | 32465.9902 | -26712.2405 |  |  | 51 | 0
2002 | 2 | 14 | 10 | 0 | 1 | 61 | 46 | 25.91 | 12.9021 | 1470.0485 |  |  | 80705.6635 | 33092.0833 | 76975.0634 | 43882.9801 | -36822.6835 |  |  | 52 | 0
2002 | 2 | 14 | 11 | 0 | 1 | 61 | 46 | 29.01 | 14.4458 | 1498.3373 |  |  | 82258.7169 | 44532.6167 | 103586.7388 | 59054.1221 | -23204.5948 |  |  | 53 | 0
2002 | 2 | 14 | 12 | 0 | 1 | 61 | 46 | 27.46 | 13.6739 | 1490.4785 |  |  | 81827.2715 | 59455.7667 | 138299.2833 | 78843.5167 | -2983.7548 |  |  | 54 | 0
2002 | 2 | 14 | 13 | 0 | 1 | 61 | 46 | 29.65 | 14.7645 | 1499.2934 |  |  | 82311.2057 | 58323.4667 | 135665.4551 | 77341.9884 | -4969.2173 |  |  | 55 | 0
2002 | 2 | 14 | 14 | 0 | 1 | 61 | 46 | 29.55 | 14.7147 | 1499.144 |  |  | 82303.0043 | 44825 | 104266.8478 | 59441.8478 | -22861.1565 |  |  | 56 | 0
2002 | 2 | 14 | 15 | 0 | 1 | 61 | 46 | 30.19 | 15.0334 | 1500 |  |  | 82350 | 42844.8667 | 99660.8855 | 56816.0188 | -25533.9812 |  |  | 57 | 0
2002 | 2 | 14 | 16 | 0 | 1 | 61 | 46 | 28.64 | 14.2615 | 1497.7846 |  |  | 82228.3719 | 43613.5167 | 101448.8322 | 57835.3156 | -24393.0563 |  |  | 58 | 0
2002 | 2 | 14 | 17 | 0 | 1 | 61 | 46 | 28.37 | 14.1271 | 1497.3812 |  |  | 82206.2282 | 44172.7833 | 102749.7351 | 58576.9518 | -23629.2764 |  |  | 59 | 0
2002 | 2 | 14 | 18 | 0 | 1 | 61 | 46 | 29.23 | 14.5553 | 1498.6659 |  |  | 82276.7599 | 61335.2167 | 142671.0475 | 81335.8308 | -940.9291 |  |  | 60 | 0
2002 | 2 | 14 | 19 | 0 | 1 | 61 | 46 | 23.56 | 11.7319 | 1359.3489 |  |  | 74628.257 | 62350.2333 | 145032.0645 | 82681.8312 | 8053.5742 |  |  | 61 | 0
2002 | 2 | 14 | 20 | 0 | 1 | 61 | 46 | 21.95 | 10.9302 | 1213.2179 |  |  | 66605.6632 | 55878.9833 | 129979.3743 | 74100.3909 | 7494.7277 |  |  | 62 | 0
2002 | 2 | 14 | 21 | 0 | 1 | 61 | 46 | 18.1 | 9.013 | 692.5729 |  |  | 38022.2525 | 51431.3667 | 119633.8312 | 68202.4645 | 30180.212 |  |  | 63 | 0
2002 | 2 | 14 | 22 | 0 | 1 | 61 | 46 | 21.58 | 10.7459 | 1163.6561 |  |  | 63884.7226 | 49528.9833 | 115208.7221 | 65679.7388 | 1795.0162 |  |  | 64 | 0
2002 | 2 | 14 | 23 | 0 | 1 | 61 | 46 | 22.49 | 11.1991 | 1266.6391 |  |  | 69538.4879 | 50197.5333 | 116763.8275 | 66566.2942 | -2972.1937 |  |  | 65 | 0
[20 empty] | 66 | 0
2002 | 2 | 15 | 0 | 0 | 1 | 61 | 46 | 20.67 | 10.2928 | 1041.761 |  |  | 57192.6795 | 62460.8 | 145289.2522 | 82828.4522 | 25635.7727 |  |  | 67 | 0
2002 | 2 | 15 | 1 | 0 | 1 | 61 | 46 | 18.21 | 9.0678 | 707.5814 |  |  | 38846.2166 | 74624.8 | 173583.7739 | 98958.9739 | 60112.7573 |  |  | 68 | 0
2002 | 2 | 15 | 2 | 0 | 1 | 61 | 46 | 18.32 | 9.1226 | 722.5898 |  |  | 39670.1808 | 68736.45 | 159886.9598 | 91150.5098 | 51480.329 |  |  | 69 | 0
2002 | 2 | 15 | 3 | 0 | 1 | 61 | 46 | 15.54 | 7.7383 | 428.8141 |  |  | 23541.8945 | 61789.45 | 143727.6337 | 81938.1837 | 58396.2892 |  |  | 70 | 0
2002 | 2 | 15 | 4 | 0 | 1 | 61 | 46 | 12.49 | 6.2195 | 209.4369 |  |  | 11498.0873 | 53923.1833 | 125430.0134 | 71506.8301 | 60008.7428 |  |  | 71 | 0
2002 | 2 | 15 | 5 | 0 | 1 | 61 | 46 | 11.95 | 5.9506 | 177.5044 |  |  | 9744.993 | 39288.15 | 91387.6533 | 52099.5033 | 42354.5102 |  |  | 72 | 0
[20 empty] | 73 | 0
2002 | 2 | 15 | 6 | 0 | 1 | 13 | 94 | 22.92 | 11.4132 | 1303.8963 |  |  | 15255.5872 | 54607.9667 | 62160.1323 | 7552.1656 | -7703.4216 |  |  | 74 | 0
2002 | 2 | 15 | 7 | 0 | 1 | 13 | 94 | 29.92 | 14.8989 | 1499.6967 |  |  | 17546.4515 | 55915.3167 | 63648.286 | 7732.9693 | -9813.4822 |  |  | 75 | 0
[20 empty] | 76 | 0
2002 | 2 | 16 | 21 | 10 | 1 | 75 | 32 | 13.4 | 6.6726 | 266.0797 |  |  | 17960.3764 | 23347.95 | 78069.7078 | 54721.7578 | 36761.3814 |  |  | 77 | 0
2002 | 2 | 16 | 22 | 10 | 1 | 75 | 32 | 14.41 | 7.1756 | 335.9698 |  |  | 22677.9641 | 22832.5167 | 76346.2276 | 53513.7109 | 30835.7468 |  |  | 78 | 0
2002 | 2 | 16 | 23 | 10 | 0.5 | 75 | 32 | 16.23 | 8.0819 | 489.7633 |  |  | 16529.51 | 13150 | 43970.3125 | 30820.3125 | 14290.8025 |  |  | 79 | 0
[20 empty] | 80 | 0
2002 | 2 | 18 | 19 | 50 | 1 | 33 | 74 | 27.67 | 13.7785 | 1492.57 |  |  | 44329.3277 | 72468.0333 | 104784.859 | 32316.8257 | -12012.5021 |  |  | 81 | 0
2002 | 2 | 18 | 20 | 50 | 1 | 33 | 74 | 27.41 | 13.649 | 1489.9806 |  |  | 44252.4231 | 71902.6333 | 103967.3212 | 32064.6878 | -12187.7353 |  |  | 82 | 0
2002 | 2 | 18 | 21 | 50 | 1 | 33 | 74 | 25.96 | 12.927 | 1471.8163 |  |  | 43712.9431 | 66437.9667 | 96065.7086 | 29627.7419 | -14085.2012 |  |  | 83 | 0
2002 | 2 | 18 | 22 | 50 | 0.17 | 33 | 74 | 14.09 | 7.0162 | 309.6777 |  |  | 1563.5625 | 56306.5 | 81416.1554 | 25109.6554 | 23546.0929 |  |  | 84 | 0
[20 empty] | 85 | 0
2002 | 2 | 18 | 23 | 0 | 1 | 11 | 96 | 10.83 | 5.3929 | 126.7525 |  |  | 1254.8502 | 65712.0333 | 73241.5372 | 7529.5038 | 6274.6536 |  |  | 86 | 0
[20 empty] | 87 | 0
2002 | 2 | 19 | 2 | 0 | 1 | 46 | 61 | 19.87 | 9.8944 | 934.0726 |  |  | 38670.6046 | 62532.3333 | 109687.8634 | 47155.5301 | 8484.9254 |  |  | 88 | 0
2002 | 2 | 19 | 3 | 0 | 1 | 46 | 61 | 24.15 | 12.0257 | 1407.8237 |  |  | 58283.9005 | 41499.45 | 72794.1172 | 31294.6672 | -26989.2333 |  |  | 89 | 0
2002 | 2 | 19 | 4 | 0 | 0.5 | 46 | 61 | 34.41 | 17.1347 | 1500 |  |  | 31050 | 20226.2667 | 35478.8612 | 15252.5945 | -15797.4055 |  |  | 90 | 0
2002 | 2 | 19 | 4 | 30 | 1 | 52 | 55 | 34.41 | 17.1347 | 1500 |  |  | 70200 | 40986.4667 | 79737.3079 | 38750.8412 | -31449.1588
2002 | 2 | 19 | 5 | 30 | 1 | 52 | 55 | 33.29 | 16.577 | 1500 |  |  | 70200 | 33740.5333 | 65640.6739 | 31900.1406 | -38299.8594
2002 | 2 | 19 | 6 | 30 | 1 | 52 | 55 | 30.29 | 15.0831 | 1500 |  |  | 70200 | 28815.6833 | 56059.6021 | 27243.9188 | -42956.0812
2002 | 2 | 19 | 7 | 30 | 1 | 52 | 55 | 25.86 | 12.8772 | 1468.2808 |  |  | 68715.5398 | 44989.2833 | 87524.6058 | 42535.3224 | -26180.2174
2002 | 2 | 19 | 8 | 30 | 1 | 65 | 42 | 29.23 | 14.5553 | 1498.6659 |  |  | 87671.9573 | 61518.7 | 156726.2119 | 95207.5119 | 7535.5546
2002 | 2 | 19 | 9 | 30 | 0.75 | 65 | 42 | 30.88 | 15.3769 | 1500 |  |  | 65812.5 | 55225.6333 | 140693.8754 | 85468.2421 | 19655.7421
2002 | 2 | 19 | 10 | 10 | 1 | 68 | 39 | 33.5 | 16.6816 | 1500 |  |  | 91800 | 68873.9 | 188961.7256 | 120087.8256 | 28287.8256
2002 | 2 | 19 | 11 | 10 | 1 | 68 | 39 | 35.48 | 17.6675 | 1500 |  |  | 91800 | 70444.55 | 193270.9449 | 122826.3949 | 31026.3949
2002 | 2 | 19 | 12 | 10 | 1 | 68 | 39 | 35.05 | 17.4534 | 1500 |  |  | 91800 | 63690.1333 | 174739.5966 | 111049.4632 | 19249.4632
2002 | 2 | 19 | 13 | 10 | 1 | 68 | 39 | 31.63 | 15.7504 | 1500 |  |  | 91800 | 58200.35 | 159677.8833 | 101477.5333 | 9677.5333
2002 | 2 | 19 | 14 | 10 | 1 | 61 | 46 | 29.06 | 14.4707 | 1498.412 |  |  | 82262.8176 | 53537.0833 | 124531.9112 | 70994.8279 | -11267.9897
2002 | 2 | 19 | 15 | 20 | 0.75 | 61 | 46 | 34.04 | 16.9505 | 1500 |  |  | 61762.5 | 37808.9167 | 87946.8279 | 50137.9112 | -11624.5888
2002 | 2 | 19 | 16 | 0 | 1 | 70 | 37 | 33.4 | 16.6318 | 1500 |  |  | 94500 | 51425.25 | 148716.2635 | 97291.0135 | 2791.0135
2002 | 2 | 19 | 17 | 0 | 1 | 70 | 37 | 30.62 | 15.2475 | 1500 |  |  | 94500 | 51960.6333 | 150264.5342 | 98303.9009 | 3803.9009
2002 | 2 | 19 | 18 | 0 | 1 | 70 | 37 | 25.54 | 12.7178 | 1456.9672 |  |  | 91788.9311 | 50212.8 | 145209.9892 | 94997.1892 | 3208.2581
2002 | 2 | 19 | 19 | 0 | 1 | 70 | 37 | 19.07 | 9.4961 | 824.9202 |  |  | 51969.9715 | 47510.9833 | 137396.6275 | 89885.6441 | 37915.6727
2002 | 2 | 19 | 20 | 0 | 1 | 70 | 37 | 17.57 | 8.7491 | 634.5595 |  |  | 39977.2477 | 48673.4833 | 140758.4518 | 92084.9685 | 52107.7208
2002 | 2 | 19 | 21 | 0 | 1 | 70 | 37 | 19.71 | 9.8148 | 912.2421 |  |  | 57471.2521 | 60232.0333 | 174184.5288 | 113952.4955 | 56481.2434
2002 | 2 | 19 | 22 | 0 | 0.5 | 70 | 37 | 17.84 | 8.8836 | 663.7348 |  |  | 20907.6477 | 29222.1 | 84507.1541 | 55285.0541 | 34377.4064
2002 | 2 | 21 | 0 | 0 | 1 | 9 | 98 | 7.94 | 3.9538 | 30.8447 |  |  | 249.8418 | 7674.1333 | 8378.9007 | 704.7673 | 454.9256
2002 | 2 | 21 | 1 | 0 | 1 | 9 | 98 | 11.85 | 5.9008 | 172.973 |  |  | 1401.0814 | 12328.7833 | 13461.0185 | 1132.2352 | -268.8462
2002 | 2 | 21 | 2 | 0 | 1 | 26 | 81 | 19.33 | 9.6255 | 860.3947 |  |  | 20133.2362 | 19635.9833 | 25938.8916 | 6302.9082 | -13830.328
2002 | 2 | 21 | 3 | 0 | 1 | 26 | 81 | 17.78 | 8.8537 | 657.2514 |  |  | 15379.6835 | 24101.6833 | 31838.0261 | 7736.3428 | -7643.3407
2002 | 2 | 21 | 4 | 0 | 1 | 26 | 81 | 18.8 | 9.3616 | 788.0812 |  |  | 18441.1012 | 31086.0333 | 41064.2663 | 9978.2329 | -8462.8683
2002 | 2 | 21 | 5 | 0 | 1 | 26 | 81 | 20.03 | 9.9741 | 955.9031 |  |  | 22368.1315 | 47664.95 | 62964.8105 | 15299.8605 | -7068.271
2002 | 2 | 21 | 6 | 0 | 0.5 | 39 | 68 | 18.59 | 9.257 | 759.4287 |  |  | 13327.9745 | 24222.6833 | 38115.1047 | 13892.4213 | 564.4468
2002 | 2 | 21 | 6 | 30 | 1 | 31 | 76 | 18.59 | 9.257 | 759.4287 |  |  | 21188.062 | 44185.3333 | 62208.2982 | 18022.9649 | -3165.0971
2002 | 2 | 21 | 7 | 30 | 1 | 31 | 76 | 19.17 | 9.5459 | 838.5642 |  |  | 23395.9421 | 57067.85 | 80345.5257 | 23277.6757 | -118.2664
2002 | 2 | 21 | 9 | 40 | 1 | 11 | 96 | 22.43 | 11.1692 | 1261.4404 |  |  | 12488.2604 | 38318.4667 | 42709.1243 | 4390.6576 | -8097.6027
2002 | 2 | 21 | 10 | 40 | 1 | 27 | 80 | 24.79 | 12.3444 | 1430.4509 |  |  | 34759.9568 | 51933.1167 | 69460.5435 | 17527.4269 | -17232.5299
2002 | 2 | 21 | 11 | 40 | 0.25 | 27 | 80 | 25.91 | 12.9021 | 1470.0485 |  |  | 8930.5447
2002 | 2 | 21 | 12 | 0 | 1 | 53 | 54 | 28.37 | 14.1271 | 1497.3812 |  |  | 71425.0835 | 34898.4 | 69150.5333 | 34252.1333 | -37172.9502
2002 | 2 | 21 | 13 | 0 | 1 | 53 | 54 | 33.08 | 16.4725 | 1500 |  |  | 71550 | 37703.3 | 74708.3907 | 37005.0907 | -34544.9093
2002 | 2 | 21 | 14 | 0 | 1 | 53 | 54 | 32.33 | 16.099 | 1500 |  |  | 71550 | 43896.7333 | 86980.5642 | 43083.8309 | -28466.1691
2002 | 2 | 21 | 15 | 0 | 1 | 53 | 54 | 29.65 | 14.7645 | 1499.2934 |  |  | 71516.2935 | 69069.8167 | 136860.5627 | 67790.746 | -3725.5475
2002 | 2 | 21 | 16 | 0 | 0.25 | 53 | 54 | 22.92 | 11.4132 | 1303.8963 |  |  | 15548.9639
2002 | 2 | 21 | 16 | 10 | 1 | 27 | 80 | 22.92 | 11.4132 | 1303.8963 |  |  | 31684.6811 | 63523.3833 | 84962.5252 | 21439.1419 | -10245.5392
2002 | 2 | 21 | 17 | 10 | 0.75 | 27 | 80 | 21.74 | 10.8256 | 1185.0883 |  |  | 21598.2336 | 39934.75 | 53412.7281 | 13477.9781 | -8120.2554
2002 | 2 | 23 | 20 | 10 | 1 | 58 | 49 | 26.82 | 13.3552 | 1484.1047 |  |  | 77470.2638 | 12001.2667 | 26206.8476 | 14205.581 | -63264.6829
2002 | 2 | 23 | 21 | 10 | 1 | 58 | 49 | 21.95 | 10.9302 | 1213.2179 |  |  | 63329.9748 | 16463.0833 | 35949.9983 | 19486.915 | -43843.0599
2002 | 2 | 23 | 22 | 10 | 1 | 58 | 49 | 24.36 | 12.1303 | 1415.2482 |  |  | 73875.958 | 28079.6833 | 61316.8595 | 33237.1762 | -40638.7819
2002 | 2 | 23 | 23 | 10 | 0.75 | 58 | 49 | 26.87 | 13.3801 | 1484.6026 |  |  | 58122.1929 | 35730.8167 | 78024.4364 | 42293.6197 | -15828.5732
Note: "Enron" said following period started at midnight, ended at 1830, but only had 6.5 hrs, rather than 18.5
2002 | 2 | 24 | 0 | 0 | 1 | 58 | 49 | 27.67 | 13.7785 | 1492.57 |  |  | 77912.1518 | 86798.4667 | 189539.5088 | 102741.0422 | 24828.8904
2002 | 2 | 24 | 1 | 0 | 1 | 58 | 49 | 27.09 | 13.4897 | 1486.7936 |  |  | 77610.6282 | 115393.05 | 251980.7418 | 136587.6918 | 58977.0636
2002 | 2 | 24 | 2 | 0 | 1 | 58 | 49 | 27.14 | 13.5146 | 1487.2916 |  |  | 77636.6216 | 108015.4333 | 235870.4361 | 127855.0027 | 50218.3811
2002 | 2 | 24 | 3 | 0 | 1 | 58 | 49 | 25.8 | 12.8473 | 1466.1595 |  |  | 76533.524 | 85495.8333 | 186694.983 | 101199.1497 | 24665.6256
2002 | 2 | 24 | 4 | 0 | 1 | 58 | 49 | 27.03 | 13.4598 | 1486.1961 |  |  | 77579.4361 | 85862.25 | 187495.1173 | 101632.8673 | 24053.4312
2002 | 2 | 24 | 5 | 0 | 1 | 58 | 49 | 24.04 | 11.9709 | 1400.9384 |  |  | 73128.9843 | 88347.15 | 192921.3276 | 104574.1776 | 31445.1933
2002 | 2 | 24 | 6 | 0 | 1 | 58 | 49 | 25 | 12.449 | 1437.8755 |  |  | 75057.0985 | 88729.9667 | 193757.2741 | 105027.3075 | 29970.209
2002 | 2 | 24 | 7 | 0 | 1 | 58 | 49 | 20.56 | 10.238 | 1027.0264 |  |  | 53610.7798 | 90878 | 198447.8776 | 107569.8776 | 53959.0977
2002 | 2 | 24 | 8 | 0 | 1 | 58 | 49 | 17.36 | 8.6446 | 611.8675 |  |  | 31939.4856 | 90886.9333 | 198467.385 | 107580.4517 | 75640.9661
2002 | 2 | 24 | 9 | 0 | 1 | 58 | 49 | 19.71 | 9.8148 | 912.2421 |  |  | 47619.0375 | 91395.9333 | 199578.8748 | 108182.9415 | 60563.904
2002 | 2 | 24 | 10 | 0 | 1 | 58 | 49 | 17.57 | 8.7491 | 634.5595 |  |  | 33124.0052 | 89982.0667 | 196491.4517 | 106509.385 | 73385.3798
2002 | 2 | 24 | 11 | 0 | 1 | 58 | 49 | 17.68 | 8.8039 | 646.4457 |  |  | 33744.4679 | 88146.3667 | 192482.8823 | 104336.5156 | 70592.0478
2002 | 2 | 24 | 12 | 0 | 1 | 58 | 49 | 15.91 | 7.9225 | 459.2144 |  |  | 23970.994 | 81947.3167 | 178946.1813 | 96998.8646 | 73027.8707
2002 | 2 | 24 | 13 | 0 | 1 | 58 | 49 | 16.18 | 8.057 | 484.3604 |  |  | 25283.6137 | 49657.9667 | 108436.7844 | 58778.8177 | 33495.204
2002 | 2 | 24 | 14 | 0 | 1 | 58 | 49 | 17.41 | 8.6694 | 617.2704 |  |  | 32221.5141 | 47026.5667 | 102690.666 | 55664.0993 | 23442.5852
2002 | 2 | 24 | 15 | 0 | 1 | 58 | 49 | 17.57 | 8.7491 | 634.5595 |  |  | 33124.0052 | 46512.7667 | 101568.6946 | 55055.9279 | 21931.9227
2002 | 2 | 24 | 16 | 0 | 1 | 58 | 49 | 16.18 | 8.057 | 484.3604 |  |  | 25283.6137 | 44175.8333 | 96465.5952 | 52289.7619 | 27006.1482
2002 | 2 | 24 | 17 | 0 | 1 | 58 | 49 | 15.91 | 7.9225 | 459.2144 |  |  | 23970.994 | 34559.7667 | 75467.2456 | 40907.4789 | 16936.485
2002 | 2 | 24 | 18 | 0 | 0.5 | 58 | 49 | 15.64 | 7.7881 | 437.0304 |  |  | 11406.4938 | 11889.8667 | 25963.5864 | 14073.7197 | 2667.2259
2002 | 2 | 25 | 4 | 30 | 1 | 30 | 77 | 20.78 | 10.3476 | 1056.4956 |  |  | 28525.3809 | 65038.3667 | 90377.99 | 25339.6234 | -3185.7575
2002 | 2 | 25 | 5 | 30 | 1 | 30 | 77 | 15.32 | 7.6287 | 410.7382 |  |  | 11089.9323 | 53699.3167 | 74621.1284 | 20921.8117 | 9831.8794
2002 | 2 | 25 | 6 | 30 | 1 | 30 | 77 | 17.84 | 8.8836 | 663.7348 |  |  | 17920.8408 | 62317.0667 | 86596.4433 | 24279.3766 | 6358.5358
2002 | 2 | 25 | 7 | 30 | 1 | 30 | 77 | 17.52 | 8.7242 | 629.1566 |  |  | 16987.2294 | 53245.5833 | 73990.6158 | 20745.0325 | 3757.8031
2002 | 2 | 25 | 21 | 40 | 1 | 91 | 16 | 24.25 | 12.0755 | 1411.3592 |  |  | 115590.3174 | 2114.2667 | 14139.1583 | 12024.8917 | -103565.4257
2002 | 2 | 25 | 22 | 40 | 0.25 | 91 | 16 | 30.46 | 15.1678 | 1500 |  |  | 30712.5
2002 | 2 | 25 | 23 | 0 | 1 | 74 | 33 | 32.43 | 16.1488 | 1500 |  |  | 99900 | 1479.9333 | 4798.5717 | 3318.6384 | -96581.3616
2002 | 2 | 26 | 0 | 0 | 1 | 62 | 45 | 31.42 | 15.6458 | 1500 |  |  | 83700 | 6330.2167 | 15051.8485 | 8721.6319 | -74978.3681
2002 | 2 | 26 | 1 | 0 | 1 | 62 | 45 | 31.04 | 15.4566 | 1500 |  |  | 83700 | 23503.2833 | 55885.5848 | 32382.3015 | -51317.6985
2002 | 2 | 26 | 2 | 0 | 0.25 | 62 | 45 | 24.89 | 12.3942 | 1433.9864 |  |  | 20004.1103
2002 | 2 | 26 | 2 | 20 | 1 | 20 | 87 | 24.89 | 12.3942 | 1433.9864 |  |  | 25811.7552 | 39561.8167 | 48656.4872 | 9094.6705 | -16717.0847
2002 | 2 | 26 | 3 | 20 | 1 | 20 | 87 | 20.83 | 10.3725 | 1063.1931 |  |  | 19137.4762 | 68966.95 | 84821.4213 | 15854.4713 | -3283.0049
2002 | 2 | 26 | 4 | 20 | 0.75 | 20 | 87 | 18.59 | 9.257 | 759.4287 |  |  | 10252.2881 | 12943.4333 | 15918.9352 | 2975.5019 | -7276.7862
2002 | 2 | 26 | 5 | 0 | 1 | 20 | 87 | 17.09 | 8.5101 | 582.6922 |  |  | 10488.4593 | 30947.5333 | 38061.9088 | 7114.3755 | -3374.0838
2002 | 2 | 26 | 6 | 0 | 0.5 | 20 | 87 | 20.51 | 10.2131 | 1020.3289 |  |  | 9182.9601 | 21405.0667 | 26325.7716 | 4920.705 | -4262.2551
2002 | 2 | 26 | 6 | 30 | 1 | 38 | 69 | 20.51 | 10.2131 | 1020.3289 |  |  | 34895.2483 | 50825.9167 | 78817.0012 | 27991.0845 | -6904.1638
2002 | 2 | 26 | 7 | 30 | 1 | 38 | 69 | 21.74 | 10.8256 | 1185.0883 |  |  | 40530.0185 | 44329.2167 | 68742.4085 | 24413.1918 | -16116.8268
2002 | 2 | 26 | 8 | 30 | 0.5 | 38 | 69 | 21.31 | 10.6115 | 1127.4895 |  |  | 19280.0698 | 18241.5667 | 28287.6469 | 10046.0802 | -9233.9896
[13 empty] | 6653019.5541 |  |  | 6683511.2068 | 30491.6526
-103565.4257
75640.9661