## Sheet1
DATA SHEET
| LOST CREEK GATHERING COMPANY, L.L.C. | [32 empty] | Number
[34 empty] | Sheet |  |  | 1 |  | of | 2
| LOST CREEK COMPRESSOR STATION | [24 empty] | Date |  |  | By |  |  |  |  | Rev. |  |  |  | Date
[21 empty] | Approved | [12 empty] | P.O. Number
| SUBSTATION | [19 empty] | Approved | [12 empty] | P.O. Item No.
Spec. No.
GENERAL INFORMATION
|  | Applicable To: |  |  |  |  | X | Proposal |  |  |  | Purchase |  |  | As Built |  |  | X | Contractor shall complete Data Sheet with information not otherwise provided by Company.
|  | For |  | LOST CREEK COMPRESSOR STATION | [17 empty] | Unit Tag Number
|  | Site |  | SWEETWATER COUNTY, WYOMING | [17 empty] | No. Required
|  | Service |  |  |  | MOTOR DRIVEN RECIPROCATING COMPRESSOR | [15 empty] | Serial No.
|  | Vendor | [19 empty] | Mfr. / Model No.
INSTALLATION CONDITIONS
|  | Geographical Location | [7 empty] | SWEETWATER COUNTY, WYOMING | [11 empty] | Snow Load (PSF):
|  | Elevation (FT MSL) | [6 empty] | Sea level |  |  | 7000' | [9 empty] | Unusual Conditions:
|  | Ambient Temperature, °F: | [8 empty] | Max. |  | 100 |  | Min. |  | -50 | [6 empty] | Seismic Zone per Uniform Building Code:
|  | Relative Humidity (%): | [8 empty] | Max. |  | 80 |  | Min. |  | 25 | [6 empty] | Other:
Rainfall Intensity (Inch/Hr):
|  | Electrical Area Classification: | [9 empty] | X | Unclassified
|  |  | Class | [6 empty] | Division | [5 empty] | Group
SUBSTATION DATA
|  | Design Voltage: | [5 empty] | 34,500/4,160 |  |  |  | Operating Voltage: |  |  |  |  | 34,500/4,160 | [5 empty] | Substation Layout and Relay Protection Scheme:
|  | Design Pulloff Tension: | [24 empty] | See Attached One-Line Diagram
[5 empty] | Per Phase Conductor | [14 empty] | pounds | [6 empty] | Turnkey Vendor to Recommend
[5 empty] | Per static | [14 empty] | pounds |  |  | Substation Lighting | [6 empty] | Vendor Supplied | [6 empty] | Purchaser Supplied
|  | Angle of Incoming Lines | [13 empty] | degrees Maximum | [6 empty] | Substation Fencing
|  | Wind and Ice Loading: | [24 empty] | X | As specified
|  |  |  | 3 |  | NESC District Loading | [21 empty] | As indicated on attached Drawing
|  |  |  | x |  | Wind Loading of | [7 empty] | Ice Loading of | [13 empty] | Other
TRANSFORMER DATA
|  | Transformer: | [20 empty] | Oil Containment:
|  |  |  | X |  | See attached specification for Station Transformer | [16 empty] | X |  | Full Transformer Oil Containment Required
[6 empty] | Specification Number | [18 empty] | Incidental Oil Spill and Containment Required
Not Required
UTILITY METERING DATA
|  | Utility Meters: | [20 empty] | Meter Wiring Provided by: | [7 empty] | X | Utility Company
|  |  |  | X | Provided By Utility Company | [26 empty] | Turnkey Substation Vendor
[5 empty] | Provided By Turnkey Substation Vendor | [17 empty] | CT's: |  |  | X | Provided By Utility | [5 empty] | PT's: |  | X | Provided By Utility
[5 empty] | Specified by Purchaser: | [6 empty] | Manufacturer | [14 empty] | Provided By Vendor | [8 empty] | Provided By Vendor
[12 empty] | Model No. | [14 empty] | Specified by Purchaser | [8 empty] | Specified by Purchaser
[5 empty] | Mounted in Switchgear | [20 empty] | Manufacturer | [8 empty] | Manufacturer
[5 empty] | Rack Mounted (NEMA 3R) | [20 empty] | Model No. | [8 empty] | Model No.
|  | Enclosure Provided by: | [8 empty] | Utility Company
Turnkey Substation Vendor

## Sheet2
DATA SHEET
Number
|  | LOST CREEK GATHERING COMPANY, L.L.C. | [24 empty] | Sheet |  | 2 |  |  |  |  | of | 2
[23 empty] | Date |  | By |  | Rev. |  |  |  | Date
| LOST CREEK COMPRESSOR STATION | [17 empty] | Approved | [7 empty] | P.O. Number
[19 empty] | Approved | [7 empty] | P.O. Item No.
[12 empty] | SUBSTATION | [14 empty] | Spec. No.
SWITCHGEAR ENCLOSURE REQUIREMENTS
|  | X |  | Walk-in Elclosure as Specified | [15 empty] | Remarks:
NEMA 3R Switchgear
|  | Exterior Paint: | [7 empty] | X | ANSI 61, light gray |  |  |  |  | ANSI 70, sky gray
|  | Utility Company: | [6 empty] | TBA
|  | Contact: |  |  |  |  | TBA
|  | Telephone: | [5 empty] | TBA
CONSTRUCTION REQUIREMENTS
|  | Size Requirements: | [17 empty] | Foundations:
[6 empty] | Maximum Width | [15 empty] | X |  | Base Quotation on |  | 1500 | [7 empty] | PSI
[6 empty] | Maximum Length | [17 empty] | See Attached Soils Report
[6 empty] | See attached Drawing | [13 empty] | Grounding:
|  |  |  | X |  | As specified by Turnkey Vendor | [15 empty] | X |  | Assume Soils Resistivity of |  |  |  | TBA | [5 empty] | Ohm-cm
|  | Fencing Requirements: | [21 empty] | See Attached Soils Report
|  |  |  | X |  | Fencing As Specified | [13 empty] | Phase Conductor and Deadending Materials:
[6 empty] | Fencing As Indicated On Attached Drawings | [15 empty] | X |  | Provided by Turnkey Vendor
[6 empty] | Other: | [17 empty] | Provided by Local Utility
AUXILARY POWER REQUIREMENTS
|  | X |  | Vendor to Supply Batteries and Charger for Switchgear at | [12 empty] | 120 |  |  |  | Volts DC Nominal.
|  |  |  | Purchaser to Supply DC for Switchgear at | [16 empty] | Volts DC Nominal.
|  |  |  | Turnkey Vendor to Supply Transformer for All Substation | [16 empty] | Volts AC Requirements.
|  |  |  | Purchaser to Supply | [10 empty] | Volts AC to Turnkey Vendor Supplied AC Panelboard.
SUBSTATION CONDUIT REQUIREMENTS
|  |  | PVC Coated Rigid Below Grade | [16 empty] | X | Extend Conduits for Purchaser's Connection | [8 empty] | 10 |  |  | Ft beyond Fence
|  | X | PVC Schedule | [6 empty] | 40 |  |  | Acceptable Below Grade | [7 empty] | Turnkey Vendor shall Install | [6 empty] | Each |  |  |  | Conduits from
|  |  | All PVC Schedule | [9 empty] | Must be encased In Concrete | [7 empty] | Switchgear Building To Substation Boundary for Controls.
ADDITIONAL REQUIREMENTS
Provide Foundation, Grounding, Installation, and Connection of Purchaser Supplied Variable Speed Drive DC Link Reactors
Provide Foundation, Grounding, Installation, and Connection of Purchaser Supplied Variable Speed Drive Isolation Transformer.
|  | X | Provide Foundation, Grounding, Installation, and Connection of Purchaser Supplied Harmonic Filter / Power Factor Correction Equipment.
|  | X | Provide Foundation, Grounding, Installation, and Connection of | [14 empty] | 300 | KVA 480 V Auxilary Transformer and Secondary Breaker.
See Attached Specifications for Equipment
Purchaser To Supply Information at a Later Date. Turnkey Vendor to finalize after receipt of information.
COMMENTS/ADDITIONAL INFORMATION
UTIILITY COMPANY CONTACT: Bob Dahl
Pacific Power and Light (PacifiCorp)
(307) 352-5201