## TOP3
Routing; Sloat K, Johnson K, Anderson D, Boschee R, Garcia J, Lytle D, Chesworth J, Russell C, Wong M, McCurdy R, Steiner P
| Date Collected | PCB Result (ppm) | Lab
PGE TOP3 | 1998-07-20 | 39 | BC Labs
Pipeline liquid tank | 1998-07-29 | 0 | BC Labs
connected to top | 1998-08-27 | 0 | BC Labs
section of Peco | 1998-09-10 | 25 | Sherwood
Filter/Separator | 1998-10-28 | 0 | Sherwood
at Topock Compressor | 1998-12-09 | 30 | Sherwood
Station | 1999-01-08 | 45 | Sherwood
| 1999-01-29 | 64 | Sherwood
| 1999-02-05 | 90 | Sherwood
| 1999-02-12 | 92 | Sherwood
| 1999-02-19 | 78 | Sherwood
| 1999-02-26 | 71 | Sherwood
| 1999-03-04 | 75 | Sherwood
| 1999-03-11 | 93 | Sherwood
| 1999-03-18 | 90 | Sherwood
| 1999-03-25 | 86 | Sherwood
| 1999-04-01 | 82 | Sherwood
| 1999-04-09 | 111 | Sherwood
| 1999-04-15 | 92 | Sherwood
| 1999-04-22 | 91 | Sherwood
| 1999-04-23 | 82 | Sherwood
| 1999-04-24 | 117 | Sherwood
| 1999-04-25 | 116 | Sherwood
| 1999-04-26 | 130 | Sherwood
| 1999-04-27 | 131 | Sherwood
| 1999-04-28 | 124 | Sherwood
| 1999-04-29 | 158 | Sherwood
| 1999-04-29 | 156 | Sherwood
| 1999-04-30 | 154 | Sherwood
| 1999-05-01 | 159 | Sherwood
| 1999-05-02 | 169 | Sherwood
| 1999-05-03 | 169 | Sherwood
| 1999-05-04 | 190 | Sherwood
| 1999-05-05 | 111 | Sherwood
| 1999-05-06 | 141 | Sherwood
| 1999-05-07 | 170 | Sherwood
| 1999-05-07 | 144 | Sherwood
| 1999-05-08 | 278 | Sherwood
| 1999-05-09 | 177 | Sherwood
| 1999-05-10 | 194 | Sherwood
| 1999-05-11 | 106 | Sherwood
| 1999-05-12 | 184 | Sherwood
| 1999-05-13 | 208 | Sherwood
| 1999-05-14 | 203 | Sherwood
| 1999-05-15 | 205 | Sherwood
| 1999-05-16 | 204 | Sherwood
| 1999-05-17 | 204 | Sherwood
| 1999-05-20 | 212 | Sherwood
| 1999-05-21 | 204 | Sherwood
| 1999-05-28 | 203 | Sherwood
| 1999-06-03 | 217 | Sherwood
| 1999-06-08 | 213 | Sherwood
| 1999-06-10 | 213 | Sherwood
| 1999-06-17 | 192 | Sherwood
| 1999-07-05 | 79 | Sherwood
| 1999-07-08 | 273 | Sherwood
| 1999-07-15 | 162 | Sherwood
| 1999-07-22 | 105 | Sherwood
| 1999-07-29 | 62 | Sherwood
| 1999-08-05 | 96 | Sherwood
| 1999-08-12 | 104 | Sherwood
| 1999-08-19 | 61 | Sherwood
| 1999-08-26 | 87 | Sherwood
| 1999-08-31 | 79 | Sherwood
| 1999-09-02 | 118 | Sherwood
| 1999-09-06 | 90 | Sherwood
| 2000-06-21 | 16 | Sherwood

## TOP4
Sample location | Date collected | PCB result (ppm) | Laboratory
PGE-TOP-4 | 1999-04-15 | 65 | Sherwood
Bottom section of | 1999-04-21 | 83 | Sherwood
Peco Filter/Separator | 1999-05-07 | 223 | Sherwood
at Topock Compressor | 1999-05-08 | 295 | Sherwood
Station | 1999-05-09 | 303 | Sherwood
| 1999-05-10 | 388 | Sherwood
| 1999-05-11 | 275 | Sherwood
| 1999-05-12 | 337 | Sherwood
| 1999-05-13 | 333 | Sherwood
| 1999-05-14 | 340 | Sherwood
| 1999-05-15 | 328 | Sherwood
| 1999-05-16 | 328 | Sherwood
| 1999-05-17 | 321 | Sherwood
| 1999-05-20 | 329 | Sherwood
| 1999-05-28 | 227 | Sherwood
| 1999-06-03 | 328 | Sherwood
| 1999-06-08 | 339 | Sherwood
| 1999-06-17 | 314 | Sherwood
| 1999-07-03 | 219 | Sherwood
| 1999-07-04 | 95 | Sherwood
| 1999-07-05 | 115 | Sherwood
| 1999-07-06 | 116 | Sherwood
| 1999-07-08 | 73 | Sherwood
| 1999-07-15 | 38 | Sherwood
| 1999-07-22 | 55 | Sherwood
| 1999-08-05 | 164 | Sherwood
| 1999-08-12 | 55 | Sherwood
| 1999-08-19 | 37 | Sherwood
| 1999-08-26 | 28 | Sherwood
| 1999-08-31 | 34 | Sherwood
| 1999-09-02 | 51 | Sherwood
| 1999-09-06 | 62 | Sherwood
| 1999-09-14 | 35 | Sherwood
| 2000-05-30 | 505 | Sherwood
| 2000-06-14 | 567 | Sherwood
| 2000-07-05 | 220 | Sherwood
0 data values = ND or less than a detection limit of 1ppm

## TOP A6
Sample location | Date collected | PCB result (ppm) | Laboratory
PGE A6 | 1998-10-30 | None | Sherwood
Line 300 A Scrubber | 1999-01-08 | None | Sherwood
that Transwestern | 1999-05-27 | 27 | Sherwood
flows through | 1999-07-03 | 78 | Sherwood
| 1999-07-04 | 29 | Sherwood
| 1999-08-31 | 55 | Sherwood
| 1999-09-02 | 69 | Sherwood
| 1999-09-06 | 67 | Sherwood
| 1999-09-12 | 71 | Sherwood
0 data values = ND or less than a detection limit of 1ppm

## TOP B6
Sample location | Date collected | PCB result (ppm) | Laboratory
PGE B6 | 1998-12-09 | 5 | Sherwood
Line 300 B Scrubber | 1999-02-05 | 17 | Sherwood
that Transwestern | 1999-02-18 | 10 | Sherwood
flows through. | 1999-04-16 | 1 | Sherwood
| 1999-05-27 | 25 | Sherwood
| 1999-07-03 | 101 | Sherwood
| 1999-07-04 | 69 | Sherwood
| 1999-08-31 | 59 | Sherwood
| 1999-09-02 | 71 | Sherwood
| 1999-09-06 | 77 | Sherwood
0 data values = ND or less than a detection limit of 1ppm

## TW2
Sample location | Date collected | PCB result (ppm)
PGE-TW-2 | 1999-01-29 | 68 | Sherwood
| 1999-02-05 | 18 | Sherwood
Transwestern Filter/Separator | 1999-02-19 | 109 | Sherwood
at Transwestern Metering | 1999-02-26 | 77 | Sherwood
Station | 1999-03-04 | 126 | Sherwood
| 1999-03-11 | 138 | Sherwood
| 1999-03-18 | 144 | Sherwood
| 1999-03-25 | 216 | Sherwood
| 1999-04-01 | 232 | Sherwood
| 1999-04-09 | 293 | Sherwood
| 1999-04-15 | 216 | Sherwood
| 1999-04-22 | 280 | Sherwood
| 1999-04-29 | 307 | Sherwood
| 1999-05-07 | 152 | Sherwood
| 1999-05-13 | 264 | Sherwood
| 1999-05-20 | 280 | Sherwood
| 1999-05-28 | 207 | Sherwood
| 1999-06-03 | 278 | Sherwood
| 1999-06-10 | 321 | Sherwood
| 1999-06-17 | 368 | Sherwood
| 1999-07-08 | <1 | Sherwood
| 1999-07-15 | 9 | Sherwood
| 1999-07-22 | 26 | Sherwood
| 1999-07-29 | 20 | Sherwood
| 1999-08-05 | 36 | Sherwood
| 1999-08-12 | 27 | Sherwood
| 1999-08-19 | 11 | Sherwood
| 1999-08-26 | 11 | Sherwood
| 1999-09-02 | 18 | Sherwood

## TW4
Sample location | Date collected | PCB result (ppm)
PGE TW4 | 1999-09-04 | 29 | Sherwood
First siphon point downstream
of PGE/TW intertie. Siphon
point owned by Transwestern

## 0.55B
Sample location | Date collected | PCB result (ppm) | Lab
PGE Mile pt. | 1999-11-03 | 14 | Sherwood
0.55 B side | 1999-11-18 | 26 | Sherwood
| 1999-11-24 | 44 | Sherwood
| 1999-12-01 | 47 | Sherwood
| 1999-12-08 | 30 | Sherwood
| 1999-12-14 | 21 | Sherwood
| 1999-12-29 | 29 | Sherwood
| 2000-01-05 | 17 | Sherwood
| 2000-01-19 | 17 | Sherwood
| 2000-02-09 | 29 | Sherwood
| 2000-03-01 | 23 | Sherwood
| 2000-03-22 | 10 | Sherwood
| 2000-04-05 | 20 | Sherwood
| 2000-04-19 | 17 | Sherwood
| 2000-05-03 | 17 | Sherwood
| 2000-05-17 | 11 | Sherwood
| 2000-05-31 | 17 | Sherwood
| 2000-06-14 | 15 | Sherwood
| 2000-06-21 | 18 | Sherwood
| 2000-06-27 | 19 | Sherwood
| 2000-07-05 | 17 | Sherwood
| 2000-08-09 | 13 | Sherwood
| 2000-09-20 | 8 | Sherwood
| 2000-10-04 | 5 | Sherwood
| 2000-10-18 | 5 | Sherwood
| 2000-12-13 | 4 | Sherwood
| 2001-02-14 | 3 | Sherwood
0 data values = ND or less than a detection limit of 1ppm

## 10.84A
Sample location | Date collected | PCB result (ppm)
PGE Mile pt. | 1998-10-30 | 0 | Sherwood
10.84 A side | 1999-01-08 | 2 | Sherwood
| 1999-01-29 | 2 | Sherwood
| 1999-02-05 | 2 | Sherwood
| 1999-02-12 | 1 | Sherwood
| 1999-02-19 | 2 | Sherwood
| 1999-02-26 | 2 | Sherwood
| 1999-03-04 | 2 | Sherwood
| 1999-03-11 | 2 | Sherwood
| 1999-03-18 | 2 | Sherwood
| 1999-03-25 | 2 | Sherwood
| 1999-04-01 | 3 | Sherwood
| 1999-04-09 | 5 | Sherwood
| 1999-04-15 | 4 | Sherwood
| 1999-04-22 | 3 | Sherwood
| 1999-04-29 | 2 | Sherwood
| 1999-05-07 | 4 | Sherwood
| 1999-05-13 | 2 | Sherwood
| 1999-05-20 | 7 | Sherwood
| 1999-05-28 | 7 | Sherwood
| 1999-06-03 | 6 | Sherwood
| 1999-06-08 | 8 | Sherwood
| 1999-06-10 | 8 | Sherwood
| 1999-06-17 | 6 | Sherwood
| 1999-07-04 | 2 | Sherwood
| 1999-07-08 | 1 | Sherwood
| 1999-07-15 | 4 | Sherwood
| 1999-07-22 | 4 | Sherwood
| 1999-07-29 | 6 | Sherwood
| 1999-08-05 | 6 | Sherwood
| 1999-08-12 | 3 | Sherwood
| 1999-08-19 | 4 | Sherwood
| 1999-08-26 | 7 | Sherwood
| 1999-09-02 | 2 | Sherwood
| 1999-09-16 | 4 | Sherwood
| 1999-09-23 | 5 | Sherwood
| 1999-09-30 | 4 | Sherwood
| 1999-10-06 | 9 | Sherwood
| 1999-10-27 | 19 | Sherwood
| 1999-11-03 | 16 | Sherwood
| 1999-11-18 | 22 | Sherwood
| 1999-11-24 | 13 | Sherwood
| 1999-12-01 | 11 | Sherwood
| 1999-12-08 | 13 | Sherwood
| 1999-12-14 | 9 | Sherwood
| 1999-12-29 | 16 | Sherwood
| 2000-01-05 | 9 | Sherwood
| 2000-01-19 | 8 | Sherwood
| 2000-03-01 | 21 | Sherwood
| 2000-03-22 | 13 | Sherwood
| 2000-05-03 | 21 | Sherwood
| 2000-05-17 | 16 | Sherwood
| 2000-05-31 | 23 | Sherwood
| 2000-06-21 | 24 | Sherwood
| 2000-07-05 | 21 | Sherwood
| 2000-07-26 | 20 | Sherwood
| 2000-08-09 | 18 | Sherwood
| 2000-10-04 | 18 | Sherwood
| 2000-10-18 | 16 | Sherwood
| 2000-11-08 | 15 | Sherwood
| 2000-12-13 | 11 | Sherwood
| 2001-01-10 | 8 | Sherwood
| 2001-02-14 | 8 | Sherwood
| 2001-03-14 | 7 | Sherwood

## 10.47B
Sample location | Date collected | PCB result (ppm)
PGE Mile pt. | 1998-08-27 | 0 | BCLabs
10.47 B side | 1999-02-05 | 1 | Sherwood
| 1999-02-12 | 0 | Sherwood
| 1999-02-19 | 0.5 | Sherwood
| 1999-03-04 | 0 | Sherwood
| 1999-03-11 | 0.5 | Sherwood
| 1999-03-18 | 0 | Sherwood
| 1999-03-25 | 0 | Sherwood
| 1999-04-01 | 0 | Sherwood
| 1999-04-09 | 0 | Sherwood
| 1999-04-15 | 0 | Sherwood
| 1999-04-22 | 0 | Sherwood
| 1999-04-29 | 0 | Sherwood
| 1999-05-07 | 0 | Sherwood
| 1999-05-13 | 1 | Sherwood
| 1999-05-20 | 0.5 | Sherwood
| 1999-05-28 | 1 | Sherwood
| 1999-06-03 | 0.5 | Sherwood
| 1999-06-10 | 1 | Sherwood
| 1999-06-17 | 2 | Sherwood
| 1999-07-06 | 0 | Sherwood
| 1999-07-08 | <1 | Sherwood
| 1999-07-15 | <1 | Sherwood
| 1999-07-22 | <1 | Sherwood
| 1999-07-29 | 1 | Sherwood
| 1999-08-05 | <1 | Sherwood
| 1999-08-12 | <1 | Sherwood
| 1999-08-19 | <1 | Sherwood
| 1999-09-16 | <1 | Sherwood
| 1999-09-23 | 1 | Sherwood
| 1999-09-30 | <1 | Sherwood
| 1999-10-14 | 2 | Sherwood
| 1999-11-03 | <1 | Sherwood
| 1999-12-01 | 3 | Sherwood
| 1999-12-29 | 2 | Sherwood
| 2000-01-19 | 1 | Sherwood
0 data values = ND
.5 data values = <1

## 15.33A
Sample location | Date collected | PCB result (ppm) | Lab
PGE Mile pt. | 1999-04-15 | 0.5 | Sherwood
15.33 A side | 1999-04-29 | 4 | Sherwood
| 1999-05-07 | 3 | Sherwood
| 1999-05-13 | 2 | Sherwood
| 1999-05-20 | 6 | Sherwood
| 1999-05-28 | 6 | Sherwood
| 1999-06-03 | 7 | Sherwood
| 1999-06-10 | 8 | Sherwood
| 1999-06-17 | 9 | Sherwood
| 1999-07-08 | 6 | Sherwood
| 1999-07-15 | 4 | Sherwood
| 1999-07-22 | 3 | Sherwood
| 1999-07-29 | 6 | Sherwood
| 1999-08-05 | 5 | Sherwood
| 1999-08-12 | 5 | Sherwood
| 1999-09-16 | 4 | Sherwood
| 1999-09-23 | 5 | Sherwood
| 1999-09-30 | 7 | Sherwood
| 1999-10-06 | 8 | Sherwood
| 1999-10-14 | 10 | Sherwood
| 1999-10-20 | 28 | Sherwood
| 1999-10-27 | 27 | Sherwood
| 1999-11-03 | 18 | Sherwood
| 1999-11-18 | 18 | Sherwood
| 1999-11-24 | 10 | Sherwood
| 1999-12-01 | 25 | Sherwood
| 1999-12-08 | 35 | Sherwood
| 1999-12-14 | 39 | Sherwood
| 1999-12-29 | 30 | Sherwood
| 2000-01-05 | 33 | Sherwood
| 2000-01-19 | 24 | Sherwood
| 2000-02-09 | 29 | Sherwood
| 2000-03-01 | 26 | Sherwood
| 2000-03-22 | 35 | Sherwood
| 2000-05-03 | 24 | Sherwood
| 2000-05-17 | 17 | Sherwood
| 2000-06-14 | 25 | Sherwood
| 2000-06-21 | 24 | Sherwood
| 2000-06-27 | 23 | Sherwood
| 2000-07-05 | 16 | Sherwood
| 2000-07-12 | 14 | Sherwood
| 2000-07-26 | 15 | Sherwood
| 2000-08-09 | 18 | Sherwood
| 2000-08-23 | 19 | Sherwood
| 2000-09-20 | 14 | Sherwood
| 2000-10-04 | 15 | Sherwood
| 2000-11-08 | 12 | Sherwood
| 2000-12-13 | 10 | Sherwood
| 2001-03-14 | 4 | Sherwood
0 data values = ND or less than a detection limit of 1ppm

## 63.26A
Sample location | Date collected | PCB result (ppm) | Lab
PGE Mile pt. | 2000-06-21 | 27 | Sherwood
63.26 A Side | 2000-06-27 | 24 | Sherwood
| 2000-07-05 | 20 | Sherwood
| 2000-07-26 | 18 | Sherwood
| 2000-08-23 | 16 | Sherwood
| 2000-09-06 | 14 | Sherwood
| 2000-10-04 | 15 | Sherwood
| 2000-10-18 | 14 | Sherwood
| 2000-11-08 | 18 | Sherwood
| 2001-02-14 | 14 | Sherwood
| 2001-03-14 | 10 | Sherwood
0 data values = ND or less than a detection limit of 1ppm

## 63.26B
Sample location | Date collected | PCB result (ppm) | Lab
PGE Mile pt. | 2000-03-22 | 27 | Sherwood
63.26 B Side | 2000-04-05 | 8 | Sherwood
| 2000-04-19 | 10 | Sherwood
| 2000-05-03 | 9 | Sherwood
| 2000-05-17 | 7 | Sherwood
| 2000-05-31 | 11 | Sherwood
| 2000-06-14 | 16 | Sherwood
| 2000-06-21 | 17 | Sherwood
| 2000-06-27 | 26 | Sherwood
| 2000-07-05 | 19 | Sherwood
| 2000-07-12 | 19 | Sherwood
| 2000-07-26 | 18 | Sherwood
| 2000-08-09 | 17 | Sherwood
| 2000-08-23 | 15 | Sherwood
| 2000-09-06 | 16 | Sherwood
| 2000-09-20 | 15 | Sherwood
| 2000-10-04 | 16 | Sherwood
| 2000-10-18 | 14 | Sherwood
| 2000-11-08 | 16 | Sherwood
| 2000-12-13 | 15 | Sherwood
| 2001-02-14 | 9 | Sherwood
| 2001-03-14 | 6 | Sherwood
0 data values = ND or less than a detection limit of 1ppm

## 84.10A
Sample location | Date collected | PCB result (ppm) | Lab
PGE Mile pt. | 2000-03-22 | 21 | Sherwood
84.10 A Side | 2000-07-05 | 21 | Sherwood
| 2000-08-09 | 16 | Sherwood
| 2000-08-23 | 16 | Sherwood
| 2000-09-06 | 17 | Sherwood
| 2000-10-04 | 17 | Sherwood
| 2000-10-18 | 14 | Sherwood
| 2001-01-10 | 13 | Sherwood
0 data values = ND or less than a detection limit of 1ppm