## Table of Contents
City of Austin 4 x LM6000 Power Project
Operations & Maintenance Cost Estimate
Table of Contents
Table of Contents |  | 1
Scope
| Project Scope Description | 2
| List of Assumptions | 3
| Map | 4
Summary - Operations & Maintenance Cost Estimate |  | 5
| Comparison vs. Other Plants | 6
O&M Staff Organization Chart |  | 7
O&M Pre-Mobilization / Mobilization Cost Estimate |  | 6
| O&M Staff Mobilization Schedule | 7
| O&M Staff Mobilization Plan | 8
| Training Program | 9
| Assumed Turnkey/Operator/Owner Scope Split | 10
| Pre-Mob / Mobilization Drawdown Schedule | 14
| Owners' Engineer | 16
| Pre-Mob / Mobilization Estimate Backup/Detail | 12
Commercial Operations O&M Estimate |  | 12
| Staffing Plans | 13
| Contract & Opns Support Staffing Plan | 24
| Commercial Office Cost Estimate & Staffing Plan | 25
| Foreign vs. Local Costs | 26
| Personnel Benefits | 19
| O&M Estimate Backup/Detail | 20
Major Maintenance Cost Estimate
| Initial Operating Spares | 35
| GT Scheduled Major Maint. Program (10 Year term) | 25

## Scope
City of Austin 4 x LM6000 Power Project
Project Scope Description
Scope of Work: | Full Operations and Maintenance services during the Pre-Operating and
Operating Period for one gas-fired LM6000 simple cycle peaking facility
Location: | Austin, TX
Location at approximately 10 miles from two existing operating plants
Located on sight of a water treatment plant
Ownership: | To be owned and operated by City of Austin
Capacity: | 180 | MW
Equipment: | (4) GE LM6000 PC SPRINT Gas Turbine packages with standard combustor (non-DLE)
SPRINT water injection assumed at a rate of 7.5 gpm
Water injection for NOX control assumed at a rate of 60 gpm
Water source:
Potable water for supply to reverse osmosis process
treated water from nearby water treatment plant for cooling tower makeup
Demin system: Reverse Osmosis and leased trailer back mounted mixed bed
(1) induced draft Cooling Tower with circ. water pumps
(8) Chillers with condenser and chilled water pumps
Distributed Control System at site
No remote monitoring or control from other nearby plant sites
(4) Selective Catalytic Reduction units
No gas compression assumed
No gas or electric distribution
Facilities: | Small Administrative office space, storage
Small onsite warehouse with some climate control space
Maintenance shop with bay
Central control room and small lab area
Sanitary facilities, to include lockers & showers
Fuel: | Primary: Pipeline Quality Natural Gas
Backup: None
Operations Mode: | Peaking duty, 1,300 fired hours per year
Year round availability requirement (excluding scheduled maintenance)
PPA: | Enron to contract for 50% of capacity for first 3 years
3 and 20 year term modeled
Schedule: | Commercial Operations Date: |  | 2001-05-01
Commercial Office: | Costs not included
Other Facilities: | Barge dock on river for fuel deliveries.
Owners Engineer: | Costs not included

## Assumptions
City of Austin 4 x LM6000 Power Project
List of O&M Assumptions
1) Base year for all costs and prices herein: current 2000 US $ (no escalation or inflation included).
2) O&M personnel salaries and benefits per Enron experience, with some slight increase in wages due to assumed union labor force.
3) Primary fuel to be Pipline Quality Natural Gas only at required operating pressures, with no backup fuel.
4) Water injection for Nox control at an assumed rate of 60 gpm; SPRINT at 7.5 gpm.
5) Plant to be considered available year round with the exception of scheduled maintenance outages.
6) Gas turbine run hours/year: 1,300 hours/year.
7) Gas turbine starts/year: assumed to be less than 200 per year with the above indicated dispatch schedule.
7A) Type of combustion system to be Standard, non-DLE combustor, with water injection.
8) Assume any major schedule maintenance will be performed during off-peak season.
9) Gas turbine major scheduled maintenance pricing per GE Pricing catalog (George Graham e-mail dated 3/00).
10) Major scheduled maintenance intervals per OEM (GE): Hot Gas Path - 24,000 hrs; Major - 50,000 hours.
11) Water Source: Municipal and treated water. TDS is assumed to be 750 ppm. Owner/Originator to provide sample analysis.
12) Water treatment chemicals costs per inhouse estimating model and performance dept tabulations (no Water Balance available).
13) Chemical costs and 10% of annual maintnenace are assumed variable with dispatch; all other costs are fixed.
14) Variable costs are based on 15% annual plant capacity factor.
15) EPC Contract to provide an allowance for GT familiarization and operations training to O&M staff.
16) Spare Parts estimate per GE recommended spares for stand alone domestic project, with some assumed adjustments.
17) Staffing plan assumes that all plant supervision and admin/commercial services to support operation will be from existing City of Austin staff.
18) Assumed Scope Split between Turnkey/Startup Contractor and Owner/Operator per enclosed.
19) Turnkey Contractor: Assumed to be EECC.
20) Owners Engineer: Owner's responsibility (estimate not included).
21) Sustaining capital expenses intended to cover only replacement of initial procurement items at end of their useful life.
22) Admin staff and support are provided by Operator from home office and other sites.
23) Owner to provide Commercial Office function.
Revenue and Property Book Accounting including customer and fuel supplier billing
Tax Accounting including preparing Local and US tax returns
Annual financial audits by outside auditors.
Maintaining Bank accounts and treasury functions
Commercial contracts and interface with Power Purchasers and Fuel Suppliers
Fuel purchasing & supply, logistics and scheduling
Government and Public Relations
Legal and contractual requirements
Project Human resources (compensation and benefits plans)
Interface with Lenders and Partners regarding funding and information requests
Budgeting, Operating and Capital planning (Operator to provide plans per contract)
24) This O&M Estimate does not include the cost of the following items:
Fuel or fuel testing
Water rights and water usage costs
Purchased (backfeed) power and other purchased utilities
Insurance
Buildings: Administration, Warehouse and Shop facilities
Operating or Environmental Permits
Communications facilities (internal & external)
Customs duties, Taxes or VAT
Changes in escalation, inflation or exchange rate
Emissions, discharge or waste hauling Fees
Security (At Owner's discretion)
Lease Engine Membership fees
25) SCR replacement not accrued for in the estimate.
26) Portion of chemical cost estimate assumes usage of leased trailers for mixed bed at a cost of $0.30/M gal.
27) Cooling Tower chemicals cost estimate assumes 3 cycles, 34,000 gpm flow rate and 20 deg F range.
28) Estimate assumes that adequate maintenance and calibration facilities, mobile equipment and lab services available at nearby COA facilities.
29) Esimate makes standard assumptions for labor practices. Union labor practices, if required, may differ.
30) GT Major Maintenance not accrued for in the estimate.

## Map
City of Austin 4 x LM6000 Power Project
Map of Austin

## Summary
City of Austin 4 x LM6000 Power Project
Summary - Operations & Maintenance Cost Estimate
(US $)
Expenses before Commercial Operation:
|  | US $ |  | $/kW
O&M Pre-Mobilization / Mobilization Expenses
| Pre-Mobilization Expenses | 0
| Mobilization Payroll and Burden | 117282.8861
| Mobilization Operating Expenses | 159887.7143
| Mobilization Procurement Expenses | 126394.75
| Total O&M Pre-Mobilization / Mobilization Expenses | 403565.3504 |  | 2.242
| Housing Colony Mobilization Expenses | NA
| Commercial Office Mobilization Expenses | NA
| Owners' Engineer Expenses | NA
| Initial Operating Spares | 1135750 |  | 6.3097
| O&M Mobilization Period Fee | 160000 |  | 0.88889
Operator Overhead Charge (G&A)
| TOTAL ($/Kw) | 1699315.3504 |  | 9.4406
Expenses during Commercial Operation:
|  |  |  | 3 YEAR | 20 YEAR | 3 YEAR |  | 20 YEAR
|  | Year 1 | Years 2+ | AVERAGE | AVERAGE | FOM ($/kW-yr) | VOM ($/mWh) | FOM ($/kW-yr) | VOM ($/mWh)
O&M Expenses
| Payroll and Burden | 508225.8397 | 508225.8397 | 508225.8397 | 508225.8397 | 2.8235 |  | 2.8235
| Administration & Operations Expenses | 188733.0878 | 173483.0878 | 178566.4211 | 174245.5878 | 0.99204 |  | 0.96803
| Chemicals | 127190.71 | 127190.71 | 127190.71 | 127190.71 |  | 0.54355 |  | 0.54355
| Maintenance Expenses (excl. GT Scheduled Maint. Program) | 376859.0777 | 646769.0075 | 556799.0309 | 633273.511 | 2.784 | 0.23795 | 3.1664 | 0.27063
| Sustaining Capital Expenses | 12639.475 | 12639.475 | 12639.475 | 12639.475 | 0.070219 |  | 0.070219
| Total O&M Expenses (ex GT Scheduled Maint.) | 1213648.1903 | 1468308.12 | 1383421.4768 | 1455575.1235 | 6.6697 | 0.7815 | 7.0281 | 0.81418
O&M Annual Operating Fee |  | 200000 | 200000 | 200000 | 200000 | 1.1111 |  | 1.1111
GT Scheduled Major Maintenance Accrual ($/fired hour) |  |  |  |  | 54.3462
SCR Catalyst Replacement Accrual ($/fired hour) |  |  |  |  | 25
GT Lease Program Annual Membership (1 unit) |  | 0 | 0 | 0 | 0
Housing Colony Operating Expenses |  | NA | NA
Commercial Office Expenses |  | NA | NA | NA | NA
Operator Overhead Charge (G&A) |  | #REF! | #REF! | #REF! | #REF!

## Mob_Estimate
City of Austin 4 x LM6000 Power Project
O&M Pre-Mobilization / Mobilization Cost Estimate
US $
O&M Pre-Mobilization Expenses |  | 0
Mobilization Payroll & Burden |  | 117282.8861
Mobilization Operating Expenses
| Employee Expenses | 3950
| Recruiting Expenses | 5000
| Relocation Expenses | 10000
| Outside Services | 9400
| Other Supplies & Expenses | 8635.7143
| Communications | 6300
| Temporary Offices/Facilities | 0
| Training | 72202
| Manuals & Procedures | 29150
| Permits | 0
| Insurance | 0
| Operations Support Personnel | 15250
| Total Mobilization Operating Expenses | 159887.7143
Mobilization Procurement Expenses
| Office Furnishings & Equipment | 44782.5
| Safety & Environmental Equipment | 21420
| Vehicles & Mobile Equipment | 3550
| Warehouse Furnishings & Equipment | 4725
| Laboratory Equipment | 4200
| Shop Tools & Equipment | 37217.25
| Chemicals, Lubricants, Hydraulic Fluids | 10500
| Total Mobilization Procurement Expenses | 126394.75
Total O&M Pre-Mobilization / Mobilization Expenses |  | 403565.3504
Housing Colony Mobilization Expenses |  | NA
Commercial Office Mobilization Expenses |  | NA
Owners' Engineer Expenses |  | NA
Initial Operating Spares |  | 1135750
O&M Mobilization Period Fee |  | 160000
Operator Overhead Charge (G&A) |  | 0

## Mob_Schedule
City of Austin 4 x LM6000 Power Project
Staff Mobilization Schedule
MOB. MONTHS | 6 | 5 | 4 | 3 | 2 | 1 | COD
SCHEDULE | Recruiting/Procedures/Setup------------------------------------------------------------------------------------------> |  |  | Training/Early Commissioning----------------------------------------------> |  | Commissioning/Startup--------->
PLANT MANAGER
CLERK
O&M SUPERVISOR
CONTROL ROOM TECHNICIAN
OUTSIDE TECHNICIAN
FACILITY NEEDS
ADMINISTRATION FACILITIES
OFFICE EQUIPMENT
WAREHOUSE/SHOP
VEHICLES
TRAINING FACILITIES
TOOLS AND O&M EQUIPMENT

## Mob_Staffing
City of Austin 4 x LM6000 Power Project
O&M Staff Mobilization Plan
|  | Staff | Number | Salary & | Total Salary
| No. | Area | of | Benefits | & Benefits
| Personnel | A,O or M | Months | US$/Month | US $
PLANT MANAGER | 0 | A | 6 | 0 | 0
MAINTENANCE MANAGER | 0 | M | 0 |  | 0
PURCHASING / WAREHOUSE | 0 | A | 0 |  | 0
CLERK | 0 | A | 5 | 0 | 0
PLANT SUPERVISOR | 0 | O,M | 5 | 0 | 0
CONTROL ROOM TECHNICIAN | 3 | O | 3 | 24577.1193 | 73731.358
OUTSIDE TECHNICIAN | 2 | O | 3 | 14517.176 | 43551.5281
Overtime @ 20% |  |  |  |  | 0
TOTALS | 5 |  |  |  | 117282.8861

## Training
City of Austin 4 x LM6000 Power Project
Training Program
Class
|  | Weeks | Weeks | $M
Basic Plant Training (All New Hires) (1session at site/existing plants)
| New Employee Orientation (1 day) * | 0.2 | 0.2 | 0
| Plant Safety/Environmental/Firefighting (3 days) * | 0.6 | 0.6 | 0
| Power Plant Basic O&M (2 days)* | 0.4 | 0.4 | 0
| Introduction to Plant & Systems (3 days)* | 0.6 | 0.6 | 0
|  | 1.8 | 1.8 | 0
Major Systems Training (All O&M Personnel) (1 session at site)
| GT&G Operation & Familiarization (equip vendor)3 | 0.6 | 0.6 | 15
| Boiler Familiarization & Operation (general vendor) | 0 | 0 | 0
| Balance of Plant (general vendor) | 0 | 0 | 0
|  | 0.6 | 0.6 | 15
Specialized Operator Training (All Operators) (1 session at existing plants)
| Water Systems & Chemistry (performed by AE in house)* | 0.4 | 0.4 | 0
|  | 0.4 | 0.4 | 0
Control Room Training (All Operators) (1 session at site/other plants)
| GTG controls MK VI (equip vendor) | 0.6 | 0.6 | 15
| Boiler controls (general vendor) | 0 | 0 | 0
| DCS Operation & Familiarization (equip. vendor)3 | 0.6 | 0.6 | 15
|  | 1.2 | 1.2 | 30
Basic Maintenance Training (2 x Mechanics) (At Cincinnati)
| Level 1 Maintenance (equip. vendor) | 1 | 1 | 3.848
| Level 2 Maintenance (equip. vendor) | 1.4 | 1.4 | 8.47
| Boroscope Maintenance (equip. vendor) | 0.6 | 0.6 | 3.534
|  | 3 | 3 | 15.852
Electrical/Controls Maintenance Training (3 x I/C/E Technicians) (at OEM sites)
| GTG controls MK VI (equip vendor) | 2 | 2 | 15
| Generator/Excitation Maintenance (equip. vendor) | 0.6 | 0.6 | 6
| Electrical System Maintenance (general vendor) | 0 | 0 | 0 | Familiarization | No Charge
| DCS Maint. (equip. vendor) | 0.4 | 0.4 | 8
|  | 3 | 3 | 29
Total Class Training Cost |  |  | 10 | 89.852
Travel, lodging, facilities, misc.
| Maint Techs' Per diem: # techs x # class weeks at OEM site x 5d/wk x $150/day |  |  | 14.25
| Instructor Per diem: # class weeks at site for OEM x 5d/wk x $150/day (1 instructor/class week) |  |  | 1.35
| Travel: maintenance techs 8 trips x $1M/trip |  |  | 8
| Travel: Instructors (3 Vendors) x $1M/trip ea |  |  | 3
| On site Training Coordinator/Instructor (4 wks x $2600/wk incl per diem + $1M travel) * |  |  | 0
12.35
Total Training Cost Estimate |  |  |  | 102.202
| Less Training provided by Turnkey/Startup Contractor |  |  | 30
Net Training Cost Estimate ($M) for Operator/Owner |  |  |  | 72.202
Notes:
1. Assumed cost of training (instructor, training materials, aids, manuals, etc.):
Equip. Vendor Training - $25M/wk
Basic Plant Training (developed in-house) - no added cost
General Vendor Training - $8M/wk
2. The asterisk (*) denotes training and expenses provided by Operator
3. LM6000 and DCS Familiarization training assumed provided for by Equipment Supplier (in Equipment PO).

## ScopeSplit
City of Austin 4 x LM6000 Power Project
Assumed Turnkey/O&M/Owner Scope Split
Turnkey/
| Startup | O&M | Owner | Remarks/Comments
OPERATING EXPENSES (pre-COD):
Payroll and Benefits
for Owner Personnel |  |  | x
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Employee Expenses/Recruiting/Relocation
for Owner Personnel |  |  | x
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Outside Services
Technical Direction of Installation (TD of I) | x
Vendor reps & startup services | x
Security before COD | x
Security after COD |  |  | x | At Owner's discretion
O&M related services |  | x
Reliability Availability Maintainability (RAM) Study |  |  | x | At Owner's discretion
Process Hazards Analysis (HAZOP) |  |  | x | At Owner's discretion
Other Supplies & Expenses
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Communications (phone bills, etc.)
for O&M Personnel |  | x
for Startup Personnel | x
Offices/Buildings/Facilities (temporary)
for O&M Personnel (admin, training, etc.) |  | x
for Startup/Commissioning Personnel | x
Training for O&M Personnel *
Vendor Familiarization Training (Maj. Equip & Controls) |  |  | x | Assumed in equipment supply
Add'l Major Equip. Vendor |  | x
OJT during startup/commissioning | x
Basic Power Plant Training (& all other training) |  | x
Permits/Insurance
Construction & Startup Contractor's name | x |  |  | need permit matrix
Operator's name |  | x |  | "
Owner's name |  |  | x | "
Manuals, Procedures and Plans
Startup/Commissioning Plans & Procedures | x
Job Data books | x
Engineering drawings (incl. "as builts") | x |  |  | AutoCad 14 (or apprvd substitute)
Systems Descriptions | x
Test procedures & report | x
O&M Procedures | x | x
Admin and all other Plant procedures |  | x
Punchlist resolution | x |  |  | with O&M walkdown
Purchase and transportation of fuel to plant (startup) | x
Schedule fuel deliveries from supplier |  | x
Purchase of turbine generator startup power (backfeed) |  |  | x
Purchase of construction power (from fence line) | x
Purchase and delivery of Process water (hydrotests, etc) | x
Steam Blows |  |  |  | na
Chemical Cleaning (including disposal) | x
Oil Flushes | x
* O&M has overall responsibility for training O&M personnel, but Major Equip. Vendor training (for CT, Chillers, Water
Treatment/Desal, and DCS) will be provided under the major equip. purchase orders (with O&M participation in scoping).
Turnkey/
| Startup | O&M | Owner | Remarks/Comments
Warranty Implementation | x |  |  | O&M/Owner participate
Pre-Mobilization expenses
O&M engineering review/comments |  | x
Operating plans/budgets/estimates |  | x
Other Owner directed O&M services |  | x
Fuel/water quality checking (pre-COD) | x
Procurement Expenses:
Office Furnishings & Equipment
Stationary items (built-ins) | x
PABX (internal) telephone system & wiring | x
LAN wiring
External communications (satellite dish) |  |  |  | na
Office/Building furniture |  | x
Office equipment (copiers, fax, etc.) |  | x
Computer hardware/software |  | x
CMMS computer system (incl training) |  | x
Safety & Environmental equipment
Permanent Fire protection | x
Portable fire extinguishers (for offices & buildings) | x
Portable fire extinguishers (exterior) | x
Safety showers/eye washes | x
Permanent Environmental testing equip. | x
Portable Environmental testing equip. |  | x
O&M Personnel Safety/First Aid equip. |  | x
Vehicles & Mobile Equipment
Construction/Startup Contractor requirements | x
O&M requirements |  | x
Warehouse/Shop Furnishings & Equipment
Stationary items incl hoists (built-ins) | x
Non-stationary items (bins, furniture, etc.) |  | x
Process Monitoring & Laboratory Equipment
Installed analyzers/instruments | x
Stationary lab items (vent hoods, lab benches, etc.) | x
Analytical equipment, glassware, etc. |  | x
Shop Tools and Equipment
Machine shop/Instrument shop tools |  | x
Maint. (incl I/C&E) test equipment |  | x
Work benches, storage bins |  | x
Hand tools for O&M personnel |  | x
Hand tools for Startup personnel | x
Special Tools
Startup, Std Vendor supply | x
Optional vendor supply |  | x | x | Incl with Vendor PO
Chemicals, Lubricants, Fluids
Initial equipment/vessel fill | x
Consumption (pre-COD) | x
Consumption (post-COD) |  | x
Warehouse stock |  | x
Spare parts*
Consumption (pre-COD) | x
Consumption (post-COD) |  | x
Capital (Overhaul) Spares for major equip. |  |  | x | In Owner's scope to accrue
Operating (Initial) Spares for major equip. |  | x
Warehouse stock & BOP spare parts |  | x
Installed Cranes |  |  |  | na
* Turbine spare parts will be purchased based on competitive bids as part of and prior to Turbine vendors selection;
actual parts purchased will be approved by Owner.

## Mob_Backup (hidden)
| EstimateSummary | Group Item | Budget Item | Line Item | Detail/Basis |  | Total (US $) | LOCAL | FOREIGN | Calculation and Note Area
City of Austin 4 x LM6000 Power Project
O&M Pre-Mobilization / Mobilization Estimate Backup/Detail
O&M Mobilization BudgetOperating ExpensesPublic Relations Title | O&M Mobilization Budget | Operating Expenses | Public Relations | Pre-Mobilization Expenses
O&M Mobilization BudgetOperating ExpensesPublic Relations | O&M Mobilization Budget | Operating Expenses | Public Relations | recruiting | Recruiting PM |  |  | 0 | 0
|  |  |  | payroll | Plant Manager - 1 month pay/benefits |  |  | 0 | 0
|  |  |  | Travel Expenses in to/fro Houston | 2 trips x $1000/trip+ $150/day x 30 days |  |  | 0 | 0
|  |  |  | miscellaneous |  |  |  | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
O&M Mobilization BudgetOperating ExpensesPublic Relations Total | O&M Mobilization Budget | Operating Expenses | Public Relations | (Assumes Mob period begins COD less 6 months) |  | Sub-Total | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesPayroll with burden Title | O&M Mobilization Budget | Operating Expenses | Payroll with burden | Payroll with burden
|  |  |  | Total Company Payroll with benefits and 20% overtime on Opns/Maint. |  |  | 117282.8861 | 117282.8861 | 0
|  |  |  | (See detailed PltMobStaff schedule) |  |  |  | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
O&M Mobilization BudgetOperating ExpensesPayroll with burden Total | O&M Mobilization Budget | Operating Expenses | Payroll with burden |  |  | Sub-Total | 117282.8861 | 117282.8861 | 0
O&M Mobilization BudgetOperating ExpensesEmployee Expenses Title | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Employee Expenses
O&M Mobilization BudgetOperating ExpensesEmployee Expenses | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Travel related to Plant Mobilization | Local travel |  | 1000 | 1000
|  |  |  | Misc. (OT meals, Conferences,etc.) | $200/month x 6 months |  | 1200 | 1200
|  |  |  | Dues, Misc |  |  | 1000 | 1000
|  |  |  | Employee Expenses | $250/month x 3 months |  | 750
O&M Mobilization BudgetOperating ExpensesEmployee Expenses Total | O&M Mobilization Budget | Operating Expenses | Employee Expenses |  |  | Sub-Total | 3950 | 3200 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses Title | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Recruiting Expenses
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | HR/Home office support | existing support |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Advertisements | Local |  | 3000 | 3000 | 0
|  |  |  | Screening Tests | $200/employee |  | 1000 | 1000 | 0
|  |  |  | Misc expenses | reproduction, postage, etc |  | 1000 | 1000 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses Total | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses |  |  | Sub-Total | 5000 | 5000 | 0
O&M Mobilization BudgetOperating ExpensesRelocation Expenses Title | O&M Mobilization Budget | Operating Expenses | Relocation Expenses | Relocation Expenses
|  |  |  | Plant Mgr |  |  | 0 | 0 | 0
|  |  |  | Technician III (assume 1 needed) | cover HHG shipment |  | 5000 | 5000 | 0
|  |  |  | Technician II (assume 1 needed) | cover HHG shipment |  | 5000 | 5000 | 0
Rest of staff assumed obtained locally
O&M Mobilization BudgetOperating ExpensesRelocation Expenses Total | O&M Mobilization Budget | Operating Expenses | Relocation Expenses |  |  | Sub-Total | 10000 | 10000 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services Title | O&M Mobilization Budget | Operating Expenses | Outside Services | Outside Services
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Guards | Turnkey responsibility |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Groundskeepers | Turnkey responsibility |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Janitors | contract |  | 3200 | 3200 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Legal | existing support |  | 0 | 0 | 0
|  |  |  | Tax | existing support |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Accounting | existing support |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Safety | existing support |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Environmental | existing support |  |  | 0 | 0
|  |  |  | Management | existing support
|  |  |  | Technical/Professional | existing support
|  |  |  | Trash/Waste Disposal | Turnkey responsibility |  |  | 0 | 0
|  |  |  | Electrical Testing/Calibration | Turnkey responsibility |  |  | 0 | 0
|  |  |  | Buyer support from other projects | existing support |  |  | 0 | 0
|  |  |  | Uniform services |  |  | 3000
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Office Equipment Maintenance |  |  |  | 0 | 0
|  |  |  | Warehouse temporaries | $20/hr x 160 hrs |  | 3200
O&M Mobilization BudgetOperating ExpensesOutside Services Total | O&M Mobilization Budget | Operating Expenses | Outside Services |  |  | Sub-Total | 9400 | 3200 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses Title | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Other Supplies & Expenses
|  |  |  | Postage & Freight | $100/month x 6 months |  | 600 | 600
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Office & Misc. Supplies (usage) | $500/month x 5 months |  | 2500 | 2500
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Vehicle fuel and maint | 1 vehicles x 5 months x 1000miles/month x $1.5/14 miles + $500 |  | 1035.7143 | 1035.7143
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Janitorial Supplies (usage) |  |  | 2000 | 2000
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Bldg. Utilities (water, power, gas) | 5 months x $500/month |  | 2500 | 2500
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses Total | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses |  |  | Sub-Total | 8635.7143 | 8635.7143 | 0
O&M Mobilization BudgetOperating ExpensesCommunications Title | O&M Mobilization Budget | Operating Expenses | Communications | Communications
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Phone Service | 5 months x $500/month (excludes cellular service) |  | 2500 | 2500
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Cellular Phones | 2ea. x 6 months x $300/month |  | 3600 | 3600
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications |  | cellular activation fee: 2 ea. $100 |  | 200 | 200
O&M Mobilization BudgetOperating ExpensesCommunications Total | O&M Mobilization Budget | Operating Expenses | Communications |  |  | Sub-Total | 6300 | 6300 | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses Title | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Temporary Offices/Facilities
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Office Bldgs. | Use existing plant buildings/offices when necessary |  |  | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Trailers (admin only, ex training) |  |  |  | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Sanitary facilities |  |  |  | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Misc. Furnishings |  |  |  | 0
|  |  |  | Temporary Living Quarters |  |  |  | 0
Assume admin facilties complete COD minus 5 months
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses Total | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses |  |  | Sub-Total | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining Title | O&M Mobilization Budget | Operating Expenses | Training | Training
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Basic Plant Training | See Training sheet |  | 72202 | 72202 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Major Systems Training |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Plant Chemistry |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Control Room Training |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Basic Maintenance |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Electrical/Controls Maintenance |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Additional Vendor Training |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Per diem for instructors |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Facilities (trailer rental, hall) |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Travel |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Training Coordinator |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Additional Manuals/Documents |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Miscellaneous |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Translation |  |  |  | 0 | 0
[8 empty] | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining Total | O&M Mobilization Budget | Operating Expenses | Training |  |  | Sub-Total | 72202 | 72202 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures Title | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Manuals/Operating Procedures
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Administration | Should have already |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Operations check lists | 5P&IDsx 2 mandays each x $400/day |  | 4000 | 4000 | 0
|  |  |  | Maintenance | 1/2 of Operating procedures |  | 2000 | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Maintenance/CMMS (excluding data) | Should have already |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Warehouse/Inventory | Should have already |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Emergency Plans | 40 mandays @$400/manday |  | 16000 | 16000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Safety and Health | Should have already |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Environmental Compliance | Should have already |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Utility dispatch | Should have already |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Government Reporting | Should have already |  | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Owner Reports | Should have already |  | 0 | 0 | 0
|  |  |  | Accounting | Should have already |  | 0 | 0 | 0
|  |  |  | Training Program | 10 mandays @$400/manday |  | 4000 | 4000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures |  |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Reproduction/Printing |  |  | 3000 | 3000 | 0
|  |  |  | Freight | 5% of Reproduction cost |  | 150 | 150 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures Total | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures |  |  | Sub-Total | 29150 | 29150 | 0
O&M Mobilization BudgetOperating ExpensesPermits Title | O&M Mobilization Budget | Operating Expenses | Permits | Permits
O&M Mobilization BudgetOperating ExpensesPermits | O&M Mobilization Budget | Operating Expenses | Permits | Owner's Scope of Supply |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesPermits Total | O&M Mobilization Budget | Operating Expenses | Permits |  |  | Sub-Total | 0 | 0 | 0
O&M Mobilization BudgetOperating ExpensesInsurance Title | O&M Mobilization Budget | Operating Expenses | Insurance | Operator's Insurance
O&M Mobilization BudgetOperating ExpensesInsurance | O&M Mobilization Budget | Operating Expenses | Insurance |  |  |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesInsurance | O&M Mobilization Budget | Operating Expenses | Insurance
O&M Mobilization BudgetOperating ExpensesInsurance Total | O&M Mobilization Budget | Operating Expenses | Insurance |  |  | Sub-Total | 0 | 0 | 0
Operations Support Personnel
|  |  |  | Operations Support Personnel | 1ea.x$350/dayx30days (includes benefits) |  | 10500 | 10500 | 0
|  |  |  | Per diem | 1ea.x$125/dayx30days |  | 3750 | 3750 | 0
|  |  |  | Home leave, travel | 1ea.x$1000 tripx1trips (coach class) |  | 1000 | 1000 | 0
[8 empty] | 0 | 0
|  |  |  | Basis: 1 Operating Engineer as operations support 1 months prior to COD |  | Sub-Total | 15250 | 15250 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies Title | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Office Furnishings, Equipment, Supplies
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Offices (desk, chair, table, misc) | 4ea @ $800/set |  | 1600 | 1600 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Chairs - misc. | 10ea @ $150 |  | 600 | 600 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Bookshelves | 10ea @ $75 |  | 750 | 750 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | File Cabinets | 4ea @ $200 |  | 800 | 800 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Storage Shelves/Cabinets | 10ea @ $50 |  | 500 | 500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Conference Room (table & chairs) | 1ea @ $150 + $1500 |  | 1000 | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Tables | 1ea @ $150 |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Chairs | 6ea @ $75 |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Microwave | 1 ea @ $300 |  | 150 | 150 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Coffee Pot | 1 ea. @ $150 |  | 150 | 150 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Refrig. | 1 ea @ $750 |  | 750 | 750 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Misc |  |  | 500 | 500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Computer Tables | 5ea @ $200 |  | 1000 | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Computers w printers | 5ea @ $3000 |  | 8000 | 8000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Systems Software | 5ea @ $500 |  | 1000 | 1000 | 0
|  |  |  | CMMS software/installation | $10M License + $10M installation/training |  | 20000 | 20000 | 0
|  |  |  | CMMS hardware, equipment | 1 PC's ($2500), printer |  | 0 | 0 | 0
|  |  |  | SAP Acctg System | Software & License |  | 0 | 0 | 0
|  |  |  | SAP Acctg System | Training & Implementation |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Copiers | 1ea @ $8000 |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Typewriters | 1ea @ $250 |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Local Area Network | LAN $2M + Installation $1,000 |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Calculators | 5ea @ $20 |  | 100 | 100 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Projectors (overhead) | 1ea @ $400 |  | 0 | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | TV/VCR/Camcorders | 1ea @ $750/$500/$750 |  | 1000 | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies |  |  |  |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | White Boards | 5ea @ $80 |  | 400 | 400 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | FAX machine | 2ea @ $400 |  | 400 | 400 | 0
|  |  |  | Misc Supplies | pens, paper, staplers, envelopes, etc. |  | 500 | 500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Phones | 6ea @ $200 |  | 1200 | 1200 | 0
|  |  |  | Office Misc, pictures, plants, rugs, boards |  |  | 2000 | 2000 | 0
|  |  |  | Janitorial supplies |  |  | 250 | 250 | 0
|  |  |  | Freight | 5% of cost |  | 2132.5 | 2132.5 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies Total | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies |  |  | Sub-Total | 44782.5 | 44782.5 | 0
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies Title | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Safety & Environmental Equipment & Supplies
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Personnel Safety equipment | Safety glasses, Hard hats, goggles, face shields, gloves, |  |  | 0 | 0
[5 empty] | locks, acid suits, SCBA respirators, safety shoes, etc. |  | 3000 | 3000 | 0
|  |  |  | Portable Fire Extinguishers | 10ea. @ $120 |  | 1200 | 1200 | 0
|  |  |  | Firehose Cabinet Accessories |  |  | 7700 | 7700 | 0
|  |  |  | First Aid equipment | First Aid kit, stretcher, water jell blanket |  | 6000 | 6000 | 0
|  |  |  | Safety test Equipment | Biosystem unit, LEL & O2 meter |  | 2500 | 2500 | 0
|  |  |  | Environmental Test Equipment | Noise level meter |  |  | 0 | 0
|  |  |  | 6" and 12" containment booms |  | 44700 |  | 0 | 0
|  |  |  | 30 ton/hr skimmer |  | 21000 |  | 0 | 0
|  |  |  | Misc. anchors, tow bridles, buoys, etc. |  | 17600 |  | 0 | 0
|  |  |  | Freight | 5% of cost |  | 1020 | 1020 | 0
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies Total | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies |  |  | Sub-Total | 21420 | 21420 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment Title | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Vehicles & Mobile Equipment
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Cars 4 WD w AC |  | $26M |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 1/2 ton Pickup Trucks | 1ea leased $2000 down & lease | 700/mnth | 0 | 0 | 0
|  |  |  | 2 1/2 ton flat bed truck w winch |  | $32M |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 6 ton Forklift (outside) |  | $38M |  | 0 | 0
|  |  |  | 3 ton Forklift (warehouse) | 1ea leased $1000 down & lease | 500/mnth | 0 | 0 | 0
|  |  |  | 12 passenger Van w/o AC |  | $24M |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 18 passenger Van w/o AC |  | $30M | 0 | 0 | 0
|  |  |  | Firefighting equipment | 1ea. extinguisher cart | $1M per | 1000 | 1000 | 0
|  |  |  | Backhoe/heavy equipment |  |  | 0 | 0 | 0
|  |  |  | Compressor water wash cart |  | $10M |  | 0 | 0
|  |  |  | 250 cfm Air Compressor (trailer mtd) |  | $16M |  | 0 | 0
|  |  |  | 400 amp welder(diesel drvr, trailer) |  | $11M |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 8 ton Crane |  | $30M (used) |  | 0 | 0
|  |  |  | Crew Boats |  | $60M (used) | 0 | 0 | 0
|  |  |  | Switch engine |  | $300M | 0 | 0 | 0
|  |  |  | Maintenance cart |  |  | 2500
|  |  |  | Freight | 5% of cost |  | 50 | 50 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment Total | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Basis: Purchasing Dept. |  | Sub-Total | 3550 | 1050 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment Title | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Warehouse Furnishings & Equipment
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Bins/Racks/shelves | includes Lumber, nails, materials (to construct) |  | 3000 | 3000 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Equipment/Tools | dollies, scales, carpenter tools, banding & labeling machines |  | 1000 | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Furniture | tables, desks, chairs, file cabinets |  |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Miscellaneous Supplies |  |  | 500 | 500 | 0
|  |  |  | Freight | 5% of cost |  | 225 | 225 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment Total | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment |  |  | Sub-Total | 4725 | 4725 | 0
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment Title | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Laboratory Equipment
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Laboratory Analyzers (pH, conductivity, spectrophotometer) |  |  | 3000 | 3000 | 0
|  |  |  | Glassware/Misc. Equipment (centrifuge, vacuum pump, PC,scale,oven) |  |  | 0 | 0 | 0
|  |  |  | Furniture, cabinets, benches, tables, refrigerator |  |  | 1000 | 1000 | 0
|  |  |  | Fuel Testing equipment | Gas Chromatogragh/Atomic Absorption |  |  | 0 | 0
|  |  |  | Freight | 5% of cost |  | 200 | 200 | 0
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment Total | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Basis: Rino Manzano ccMail dtd 8/8/96 |  | Sub-Total | 4200 | 4200 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment Title | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Shop Tools & Equipment
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Mechanic Hand Tools | tool boxes | $1200 each | 1200 | 1200 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | I/E Tech Hand Tools | tool boxes | $1500 each | 1500 | 1500 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Consumables (Cleaning, Mech. supplies, compounds, I&E supplies, hoses) |  | 8000 | 8000 | 8000 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Radios (Basis: Houston 2-way Radio - Motorola HC1000, 2 channels) |  | $1000 each | 4000 | 4000 | 0
|  |  |  | Radio Base |  | $1000 each | 1000 | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Mechanical Shop Tools & Equip. | High Pressure Hand Pump | $1200 each |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Nordstrom Hyper Grease Gun 5 gal. | $3015 each |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Rockwell Hand Held High Pressure Grease Gun | $960 each | 960 | 960 | 0
[5 empty] | Hydraulic Torque Wrench | $4000 each |  | 0 | 0
[5 empty] | Centrifugal Pump | $2500 each | 0 | 0 | 0
[5 empty] | Pneumatic diaphram pump | $1000 each | 0 | 0 | 0
[5 empty] | Bead Blaster | $1800 each |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Sand Blaster | $900 each | 900 | 900 | 0
[5 empty] | Portable Air Compressor | $600 each | 600 | 600 | 0
[5 empty] | Hydraulic Press - 25 ton | $1400 each | 1400 | 1400 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment Total | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Post Hole Digger | $1200 each |  | 0 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids Title | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Steel Work Bench | $160 each | 160 | 160 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Employee Lockers | $250 each | 2000 | 2000 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Storage Cabinets | $300 each | 600 | 600 | 0
[5 empty] | Parts Washer | $1000 each | 1000 | 1000 | 0
[5 empty] | Bench Grinder | $400 each | 400 | 400 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids Total | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Drill Press | $2375 each | 2375 | 2375 | 0
O&M Mobilization BudgetO&M Mobilization Fee Title | O&M Mobilization Budget | O&M Mobilization Fee |  |  | AC/DC Welder Generator | $3100 each | 3100 | 3100 | 0
O&M Mobilization BudgetO&M Mobilization Fee | O&M Mobilization Budget | O&M Mobilization Fee |  |  | Assortment Hammer Wrenches | $5000 each |  | 0 | 0
[5 empty] | Flange Spreader | $250 each | 250 | 250 | 0
[5 empty] | Hoists /Come-a-longs | $1000 each | 1000 | 1000 | 0
[5 empty] | Miscellaneous small hand tools | $5000 set | 5000 | 5000 | 0
O&M Mobilization BudgetO&M Mobilization Fee Total | O&M Mobilization Budget | O&M Mobilization Fee |  | I/E Shop Tools & Test Equipment | Gas Detector Calibration Kit | $500 each | 0 | 0 | 0
O&M Mobilization BudgetOwner Optional Items Title | O&M Mobilization Budget | Owner Optional Items |  |  | Flow, Press, & Temp Transmitter Communicators | $5000 set | 0 | 0 | 0
O&M Mobilization BudgetOwner Optional Items | O&M Mobilization Budget | Owner Optional Items |  |  | Digital Thickness Gauge | $1800 each | 0 | 0 | 0
[5 empty] | UV IR Portable Test Kit | $4000 each |  | 0 | 0
[5 empty] | IRD Vibration Meter | $8000 each |  | 0 | 0
[5 empty] | Fluke Digital Multimeter | $350 each | 0 | 0 | 0
O&M Mobilization BudgetOwner Optional Items Total | O&M Mobilization Budget | Owner Optional Items |  |  | Thermocoupler Calibrator | $950 each | 0 | 0 | 0
[5 empty] | Precision Pressure Calibrator | $5700 each | 0 | 0 | 0
[5 empty] | Simpson Multimeter | $300 each |  | 0 | 0
[5 empty] | RTD Calibrator | $700 each | 0 | 0 | 0
[5 empty] | Test Gauges 0 -1500 psig. | $1000 set | 0 | 0 | 0
[5 empty] | Gravitometer | $5850 each |  | 0 | 0
[5 empty] | PK Tester | $4065 each | 0 | 0 | 0
[5 empty] | Pipeline Locator | $3900 each |  | 0 | 0
|  |  |  | Test/Troubleshooting Equipment | Beta Engine Analyzer | $60,000 each |  | 0 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) Title | O&M Mobilization Budget | Capital, Operating and BOP Spares (1996$) |  |  | Oscilloscope | $3000 each |  | 0 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) | O&M Mobilization Budget | Capital, Operating and BOP Spares (1998$) |  |  | Bore Scope (probe, light source and photo) | $15,000 each |  | 0 | 0
[5 empty] | Combustible Gas Detector | $1795 each | 0 | 0 | 0
[8 empty] | 0 | 0
|  |  |  | Freight | 5% |  | 1772.25 | 1772.25 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) Total | O&M Mobilization Budget | Capital, Operating and BOP Spares (1998$)
[6 empty] | Sub-Total | 37217.25 | 37217.25
Chemicals, Lubricants, Hydraulic Fluids
|  |  |  | Warehouse Stock | 1month's worth x chemicals |  | 10000 | 10000 | 0
[8 empty] | 0 | 0
|  |  |  | Freight | 5% of cost (included above) |  | 500 | 500 | 0
[6 empty] | Sub-Total | 10500 | 10500 | 0
O&M Mobilization Fee
|  |  |  | Fixed Fee |  |  | 160000 | 160000 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[6 empty] | Sub-Total | 160000 | 160000 | 0
Operator Overhead Charge (G&A)
|  |  |  | Included in the "Benefits" calculations |  |  |  | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[6 empty] | Sub-Total |  | 0 | 0
Commercial Office Mobilization
|  |  |  | Within the Owner's scope |  |  | 0 | 0 | 0
[6 empty] | Sub-Total | 0 | 0 | 0
Owners' Engineer
|  |  |  | Within the Owner's scope |  |  | NA | NA | #VALUE!
[6 empty] | Sub-Total | NA | 0 | #VALUE!
Capital, Operating and BOP Spares
|  |  |  | LM6000PC package spares |  |  | 1000000 | 1000000 | 0
|  |  |  | BOP |  |  | 100000 | 100000 | 0
|  |  |  | Freight & Insurance |  |  | 35750 | 35750 | 0
[8 empty] | 0 | 0
[6 empty] | Sub-Total | 1135750 | 1135750 | 0

## O&M_Estimate
City of Austin 4 x LM6000 Power Project
Commercial Operations O&M Estimate
US $
|  |  |  | 3 YEAR | 20 YEAR
|  | Year 1 | Years 2+ | AVERAGE | AVERAGE
Payroll & Burden |  | 508225.8397 | 508225.8397 | 508225.8397 | 508225.8397 | Fixed
Administration and Operations Expenses
| Employee Expenses | 23700 | 23700 | 23700 | 23700
| Permanent Contract Labor | 18000 | 18000 | 18000 | 18000
| Environmental Expense | 57000 | 57000 | 57000 | 57000
| Safety Expense | 10000 | 10000 | 10000 | 10000
| Buildings & Grounds | 13893.0878 | 13893.0878 | 13893.0878 | 13893.0878
| Other Supplies & Expenses | 33200 | 33200 | 33200 | 33200
| Communications | 13200 | 13200 | 13200 | 13200
| Operating Insurance | 0 | 0 | 0 | 0
| Control Room/Laboratory Expenses | 4490 | 4490 | 4490 | 4490
| Operations Support (Year 1 Only) | 15250 | 0 | 5083.3333 | 762.5
| Total Administration & Operations Expenses | 188733.0878 | 173483.0878 | 178566.4211 | 174245.5878 | Fixed
Chemicals |  | 127190.71 | 127190.71 | 127190.71 | 127190.71 | Variable
Maintenance Expenses
| Painting | 10616.9885 | 42467.954 | 31850.9655 | 40875.4057
| Instruments & Controls | 7003.125 | 14006.25 | 11671.875 | 13656.0938
| Water Treatment System | 4246.5881 | 8493.1762 | 7077.6469 | 8280.8468
| Cooling System & Chillers | 42250.8745 | 84501.749 | 70418.1242 | 82389.2053
| Electrical/Substation/Interconnects | 31252.1266 | 62504.2532 | 52086.8777 | 60941.6469
| Gas Turbines (excluding overhaul maint.) | 102297.5 | 204595 | 170495.8333 | 199480.125
| Selective Catalytic Reduction & Ammonia System | 48000 | 96000 | 80000 | 93600
| Steam Turbine (including Scheduled Maint.) | 0 | 0 | 0 | 0
| Potable Water System | 639.7917 | 1919.375 | 1492.8472 | 1855.3958
| Fuel Handling System | 864.5833 | 2593.75 | 2017.3611 | 2507.2917
| Miscellaneous Maintenance Expense | 129687.5 | 129687.5 | 129687.5 | 129687.5
| Total Maintenance | 376859.0777 | 646769.0075 | 556799.0309 | 633273.511 | 90% Fixed / 10% Variable
Sustaining Capital Expenses |  | 12639.475 | 12639.475 | 12639.475 | 12639.475 | Fixed
Total O&M Expenses (excl GT Scheduled Maint. Program) |  | 1213648.1903 | 1468308.12 | 1383421.4768 | 1455575.1235
GT Scheduled Major Maintenance Accrual ($/fired hour) |  | 54.3462 |  |  |  | Variable
SCR Catalyst Replacement Accrual ($/fired hour) |  | 25 |  |  |  | Variable
GT Lease Program Annual Membership (1 unit) | [5 empty] | Fixed
Housing Colony Operating Expenses |  | NA | NA
Commercial Office Expenses |  | NA | NA | NA | NA
O&M Annual Operating Fee |  | 200000 | 200000 | 200000 | 200000 | Fixed

## Plt_Staff
City of Austin 4 x LM6000 Power Project
Commercial Operations Staffing Plan
(US$)
|  | INDIVIDUAL |  | ANNUAL | TOTAL ANNUAL | TOTAL ANNUAL
| STAFFING | SALARY | HOURLY RATE | HOURS | SALARY & WAGES | BENEFITS | TOTAL
PLANT MANAGER | 0
CLERK | 0
O&M SUPERVISOR | 0
CONTROL ROOM TECHNICIAN | 3
Straight Time |  |  | 25 | 2080 | 156000 | 96348.6696 | 252348.6696
Over time |  |  | 37.5 | 416 | 46800 | 20353.8816 | 67153.8816
OUTSIDE TECHNICIAN | 2
Straight Time |  |  | 22 | 2080 | 91520 | 57806.3446 | 149326.3446
Over time |  |  | 33 | 416 | 27456 | 11940.9439 | 39396.9439
OVERTIME @ 10%
TOTAL | 5 |  |  |  | 321776 | 186449.8397 | 508225.8397

## Pay & Benefits Calculations (hidden)
City of Austin 4 x LM6000 Power Project
Pay & Benefits Calculations
POSITIONS | ANNUAL* | Annual
| SALARY | Hours
| IN US $ | 2080
PLANT MANAGER | 134532.4946
MAINTENANCE MANAGER | 124133.7592
PURCHASING / WAREHOUSE | 82556.2232
CLERK | 43940.757
PLANT SUPERVISOR | 103810.0792
TECHNICIAN III | 84116.2232
TECHNICIAN II | 74663.1723
Straight Time Domestic Rates
Employee Cost Breakdown
[12 empty] | Mobilization Period |  |  | Operating Period
[5 empty] | Monthly | [6 empty] | Quantity | Hours | Total | Quantity | Hours | Total
| Base | Payroll | Workers |  | Group | General
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | ESOP | 401(k) | Burdened | Base
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  |  |  | Total | Annual
|  | 14.34% | 7.78% | 15% | 440.66 | 1% | 5% | 5% | 3% |  | Salary
Administration
Plant Manager | 41 | 5.8794 | 3.1898 | 6.15 | 2.5423 | 0.58761 | 2.05 | 2.05 | 1.23 | 64.6791 | 85280 | 0 | 1120 | 0 | 0 | 2080 | 0
Maintenance Manager | 38.4615 | 5.5154 | 2.9923 | 5.7692 | 2.5423 | 0.55281 | 1.9231 | 1.9231 |  | 59.6797 | 80000 |  | 1120 | 0 |  |  | 0
Purchasing / Warehouse | 25 | 3.585 | 1.945 | 3.75 | 2.5423 | 0.36822 | 1.25 | 1.25 |  | 39.6905 | 52000 |  | 1120 | 0 |  |  | 0
Clerk | 12.25 | 1.7567 | 0.95305 | 1.8375 | 2.5423 | 0.19339 | 0.6125 | 0.6125 | 0.3675 | 21.1254 | 25480 | 0 | 1120 | 0 | 0 | 2080 | 0
Operations & Maint.
Supervisor | 31.25 | 4.4813 | 2.4312 | 4.6875 | 2.5423 | 0.45392 | 1.5625 | 1.5625 | 0.9375 | 49.9087 | 65000 |  |  | 0 |  |  | 0
CONTROL ROOM TECHNICIAN | 25 | 3.585 | 1.945 | 3.75 | 2.5423 | 0.36822 | 1.25 | 1.25 | 0.75 | 40.4405 | 52000 | 3 | 480 | 58234.3084 | 3 | 2080 | 252348.6696
OUTSIDE TECHNICIAN | 22 | 3.1548 | 1.7116 | 3.3 | 2.5423 | 0.32709 | 1.1 | 1.1 | 0.66 | 35.8958 | 45760 | 2 | 480 | 34459.9257 | 2 | 2080 | 149326.3446
Over Time Domestic Rates
Employee Cost Breakdown
| Base | Payroll | Workers |  | Group | General
Position or | Hourly | Tax | Comp. | O/H | Ins. | Liability | Pension | ESOP | 401(k) | Burdened
Employee Name | Rate | Burdens | Ins. | Alloc. | Prem. | Ins. |  |  |  | Total
|  | 14.34% | 7.78% | 15% | 0 | 1% | 5% | 0% | 0%
Administration
Plant Manager | 61.5 | 8.8191 | 4.7847 | 9.225 | 0 | 0.84329 | 3.075 |  |  | 88.2471 |  | 0 | 0 | 0 | 0 | 0 | 0
Maintenance Manager | 57.6923 | 8.2731 | 4.4885 | 8.6538 | 0 | 0.79108 | 2.8846 |  |  | 82.7834 |  |  |  | 0 |  |  | 0
Purchasing / Warehouse | 37.5 | 5.3775 | 2.9175 | 5.625 | 0 | 0.5142 | 1.875 |  |  | 53.8092 |  |  |  | 0 |  |  | 0
Clerk | 18.375 | 2.635 | 1.4296 | 2.7563 | 0 | 0.25196 | 0.91875 |  |  | 26.3665 |  | 0 | 0 | 0 | 0 | 0 | 0
Operations & Maint.
Supervisor | 46.875 | 6.7219 | 3.6469 | 7.0312 | 0 | 0.64275 | 2.3438 |  |  | 67.2615 |  |  |  | 0 |  |  | 0
CONTROL ROOM TECHNICIAN | 37.5 | 5.3775 | 2.9175 | 5.625 | 0 | 0.5142 | 1.875 |  |  | 53.8092 |  | 3 | 96 | 15497.0496 | 3 | 416 | 67153.8816
OUTSIDE TECHNICIAN | 33 | 4.7322 | 2.5674 | 4.95 | 0 | 0.4525 | 1.65 |  |  | 47.3521 |  | 2 | 96 | 9091.6024 | 2 | 416 | 39396.9439
[13 empty] | Totals | 117282.8861 |  |  | 508225.8397
Note on O28: EI: 7 months
Note on O31: EI: 7 months
Note on O34: EI: 3.5 months
Note on O35: EI: 3.5 months
Note on O52: EI: 20% overtime
Note on R52: EI: 20% overtime assumed
Note on O53: EI: 20% overtime
Note on R53: EI: 20% overtime assumed

## O&M_Backup (hidden)
Line Item | Detail/Basis |  | Total (US $) | Calculation and Note Area
City of Austin 4 x LM6000 Power Project
O&M Estimate Backup/Detail
Payroll & Burden (Total over project life)
| See detailed sheet |  | 508225.8397
0
0
0
Basis: HR data |  | Sub-Total | 508225.8397
Employee Expenses
Travel Expenses/Overtime Meals | 4 x $1,000/trip + 20 days x $150/day + $50/day x 15days |  | 7750
Conferences/Training | 7 x $1500 each |  | 10500
Fees & Dues |  |  | 500
Employees Expense | $250/month |  | 3000
Entertainment Expense | $150/employee |  | 750
Recruiting |  |  | 1200
Basis: OEC experience |  | Sub-Total | 23700
Permanent Contract Labor
0
Janitorial | $800/month x 12 months |  | 9600
Groundskeeping/Landscaping | $400/month x 12 months |  | 4800
Uniform Services | $300/month x 12 months |  | 3600
Lab Services | costs shown in Lab Expenses category
Basis: |  | Sub-Total | 18000
Environmental Expense
Training/Awards |  |  | 2500
Permits | RATA testing |  | 25000
Materials & Supplies | Calibration/test gases |  | 20000
Technical/Professional Services | 2 trip x $1M/trip + 4 days perdiem x $125/day |  | 2500
Technical/Professional Services | 80 manhrs x $75/hr (audit) | covered in O/H | 0
Other Outside Services |  |  | 0
Non-Hazardous Waste Handling |  |  | 5000
Other |  |  | 2000
Basis: OEC experience |  | Sub-Total | 57000
Safety Expense
Training/Awards |  |  | 2500
Permits
Company Membership & Dues |  |  | 1000
Routine Safety Supplies |  |  | 4000
Technical/Professional Services | 2 x $1M/trip + 4 days perdiem x $125/day |  | 2500
Technical/Professional Services | Labor covered in O/H
Safety Equipment Rentals
Basis: OEC experience |  | Sub-Total | 10000
Buildings & Grounds
HVAC | Scaled on MW |  | 13893.0878
Building repairs & painting | $22,900 x (180MW/414MW)^.6
Road repairs
Technical/Professional Services
Outside services Contract labor | Vineland annual expense avg= 3500
Equipment Rentals | (5 years of data -- new plant)
Other Rents
Supplies
Basis: Tx City/Clear Lake experience |  | Sub-Total | 13893.0878
Other Supplies & Expenses
Office Supplies & Expenses | $200/month x 12 months |  | 2400
Postage & Express Mail | $100/month x 12 months |  | 1200
Outside Services Contract Labor | 80 hrs x $12/hr |  | 960
Technical/Professional Services | Misc consulting at 40 hrs x $100/hr |  | 4000
Legal | Home office support covered in overheads |  | 0
Accounting | Home office support covered in overheads |  | 0
Office Equipment Maint. |  |  | 500
Tax | Home office support covered in overheads |  | 0
Regional Mgmt Support | Misc expenses |  | 0
Uniform services
Regulatory | Owner's scope |  | 500
Janitorial
Other Outside Services | Garbage & Trash |  | 3000
Office Equipment Rental |  |  | 1200
Other Rents |  |  | 2000
Radio parts/repair | 50% of Subic |  | 1800
PC Hardware (purchase) | Same as Subic for items < $1000, otherwise in Sus. Capital |  | 1000
PC Software | 1 CMMS licenses @ $750 ea.+ upgrades |  | 1500
PC Hardware Rental/Lease
PC Maintenance |  |  | 2000
Misc Freight Expenses |  |  | 5000
Utilities (office water, power, gas) | Assumed in Plant's House Load |  | 0
Public relations/Contributions |  |  | 2500
Boat maintenance/repair |  |  | 0
Vehicle & mobile equipment Lease | existing vehicles |  | 0
Vehicle maintenance/repair | $500/vehicle/year |  | 500
Vehicle fuel | see detail below |  | 3140
Boat fuel | na |  | 0
|  | Sub-Total | 33200
Communications
Phone service (international calls) | 12x$500/month |  | 6000
Cellular phone service | 2 phones x $300/month |  | 7200
VSAT | none assumed for this project
|  | Sub-Total | 13200
Operating Insurance
Operating Insurance |  |  | 0
Basis: Vineland, NJ experience |  | Sub-Total | 0
Control Room/Laboratory Expenses
Technical/Professional Services | Lab analysis monthly, annual, etc |  | 2400
Reagents & Supplies |  |  | 1000
Rental Equipment
Analyzer Repairs |  |  | 1000
Contract Labor/Temporaries
Other Outside Services
Freight | 5% of 75% of total |  | 90
Basis: OEC/Vineland Experience |  | Sub-Total | 4490
Operations Support (Year 1 Only)
Operations Support Personnel | 1ea.x$350/dayx30days (includes benefits) |  | 10500
Per diem | 1ea.x$125/dayx30days |  | 3750
Home leave, travel | 1ea.x$1000 trip x 1trips (coach class) |  | 1000
Tax Protection (over 6 months) | n/a |  | 0
Ops engineer for 1 month to aid in Initial Operating Period |  | Sub-Total | 15250
Chemicals & Water Treatment
Technical/Professional Services |  |  | 0
Demin Acid/Caustic |  |  | 2244
Trailer Leasing Mixed Beds | $0.30/Mgal x 4GTs x 67 gal/min/gt x 60min/hr x 1300 hrs/yr |  | 6271.2
Resin Replacement
CT Chemicals | assume at 3 cycles, surface water makeup |  | 23160
Boiler Chemicals
Desal RO Chemicals & Membrane replacement |  |  | 30095
Potable Water Chemicals | n/a
SCR Ammonia usage | 46 lbs/hr x 1300 hrs/year x $0.2/lb |  | 47840
Hydrogen (generators) | Assume air cooled
Waste Water Treatment |  |  | 2000
GT Water Wash Detergent | 4 drums / year |  | 10000
freight | 5% of total |  | 5580.51
Basis: source is 750 ppm TDS surface water; CT flow 8500 gpm; range 10deg F |  | Sub-Total | 127190.71
Painting
Paint & Materials | $70,000 x (180/414)^.6 |  | 42467.954
Technical/Professional Services | Scaled on MW
Outside Contract Services
Equipment rental
Miscellaneous
Basis: 13 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 42467.954
Instruments & Controls
Repair Parts | $3,375/yr x 4 | fixed | 13500
Outside Repair Services
Technical/Professional Services
Outside Contract Services
Equipment rental
Miscellaneous
Freight | 5% of 75% of total |  | 506.25
Basis: Vineland, NJ experience (1 x LM6000) |  | Sub-Total | 14006.25
Water Treatment System
Repair Parts | $9,816 x (133 kpph/180 kpph)^.6 x 2,500hrs/2,500hrs |  | 8186.194 | 133464
Outside Repair Services | scaled on throughput and hrs of operation
Technical/Professional Services
Outside Contract Labor | The mixed beds are leased
Equipment rental
Miscellaneous
Freight | 5% of 75% of total |  | 306.9823
Basis: Vineland, NJ experience (1 x LM6000) |  | Sub-Total | 8493.1762
Cooling System & Chillers
Repair Parts | Scaled on plant size |  | 81447.4689
Outside Repair Services | $179,000 x (180MW/414MW)^.6 x 75%
Technical/Professional Services | multiplied by factor of 75% due to no STG at this plant
Outside Contract Labor
Equipment rental
Miscellaneous
Freight | 5% of 75% of total |  | 3054.2801
Basis: 13 years of Actuals from Tx City/Clear Lake Plants |  | Sub-Total | 84501.749
Electrical/Substation/Interconnects
Repair Parts | Scaled on genrator MW and # generators |  | 62162.3602
Electric Meter Calibration & Testing | Scaled cost = Labor Cost + Materials Cost
Outside Repair Services | Labor cost (25% of total) = 25% x $94,000
Technical/Professional Services | Material Cost (75% of total) = 75% x $94,000 x (1gens/4.5gens)
Outside Contract Labor | x (46.5MW/104MW)^0.6
Equipment rental
Miscellaneous
Freight | 5% of 11% of total |  | 341.893
Basis: Vineland, NJ experience (1 x LM6000) |  | Sub-Total | 62504.2532
Gas Turbines (excluding overhaul maint.)
Repair Parts | 35000 x 4 | fixed | 140000
Outside Repair Services | $22,000/gt x 1300hrs/2000 hrs x 4 gts | variable | 57200
Technical/Professional Services | preventive and corrective maintenance, to include
Outside Contract Labor | semi-annual boroscope, calibration & inspection by S&S
Equipment rental | assumed to cover a few routine TIL installations each year |  |  | .
Miscellaneous | Does not include a membership into the Lease Engine Program
Freight | 5% of 75% of total |  | 7395
Basis: Vineland, NJ experience (1 x LM6000 avg annual maint = $57,000 @ 2000 hrs) |  | Sub-Total | 204595
Selective Catalytic Reduction & Ammonia System
HRSG |  |  | 0 | 69750.5052
Chemical Feed system | $3500/yr x 8700hrs/2500 hrs |  | 0
Condensate system |  |  | 0
feedwater system |  |  | 0
Steam distribution system |  |  | 0
Auxiliary boiler | Assuming minimal usage each year |  | 0
SCR + Ammonia system | 2% of cost $1,200,000/unit x 4 units |  | 96000
Freight |  |  | 0
Basis: OEC Vineland Experience |  | Sub-Total | 96000
Steam Turbine (including Scheduled Maint.)
Non-scheduled maint. parts/repairs |  |  | 0
Outside Repair Services
Technical/Professional Services
Scheduled Maint.
Equipment rental
Miscellaneous | NOT IN SCOPE OF WORK
Auxiliary Parts
Freight |  |  | 0
|  | Sub-Total | 0
Potable Water System
Repair Parts |  |  | 1850
Outside Repair Services
Technical/Professional Services
Outside Contract Labor
Equipment rental
Miscellaneous
Freight |  |  | 69.375
Basis: OEC Vineland Experience |  | Sub-Total | 1919.375
Fuel Handling System
Repair Parts |  |  | 2500
Outside Repair Services |  |  | 0
Technical/Professional Services
Outside Contract Labor
Equipment rental
Miscellaneous
Freight |  |  | 93.75
Basis: Vineland, NJ experience (scaled down to remove compressor costs) |  | Sub-Total | 2593.75
Miscellaneous Maintenance Expense
Warehouse Supplies |  |  | 5000
Vehicle Fuel/Gasoline
Vehicle Repairs & Maintenance
Vehicle Lease
Equipment/tools rental |  |  | 6000
Lubricants/Turbine Oil/Grease/Compounds |  |  | 24000
Tools & Tool Repair |  |  | 10500
Maint. Materials & Supplies |  |  | 50000
CEMS maint |  |  | 20000
Fire Protection System |  |  | 4000
Wastewater System |  |  | 5000
Instrument Air system |  |  | 500
Radio Parts and repairs
BOP Repairs
Hydrogen
Freight | 5% of 75% of total |  | 4687.5
Basis: OEC Vineland Experience |  | Sub-Total | 129687.5 | 558895.3575
O&M Annual Fee
Fixed Fee |  |  | 200000
|  | Sub-Total | 200000
Operator Overhead Charge (G&A)
This is included in benefits loading under payroll
0%
|  | Sub-Total | 0%
Major Equipment Maintenance Program (20 year total)
|  | Sub-Total | 0
Commercial Office Expenses
Administrative/Technical |  |  | 0
NOT IN SCOPE OF WORK
Basis: |  | Sub-Total | 0
Sustaining Project Expenses
| 10% of procurement items |  | 12639.475
Basis: Eval team concensus |  | Sub-Total | 12639.475
Vehicular Fuel Usage
1 Trucks:
1 x gal/15 miles x $1.3/gal x 30,000 miles/yr |  |  | 2600
0 Van & 1 Flat-bed Truck:
2 x gal/ 10 miles x $1.5/gal x 20 miles/day x 365 days/year |  |  | 0
1 Forklifts:
1 x 2 gal/hr x $1.5/gal x 1 hr/day x 180 days/yr |  |  | 540
0 Crane:
5 gal/hr x $1.5/gal x 40 days/yr x 8 hours/day |  |  | 0
0 Crew Boats:
20 gal/hr x 1hr/30 miles x 30 miles x 2rd trips/d x365 days/yr x $1.5/gal x 2.0 (idle factor) |  |  | 0
THESE COSTS ARE ALREADY INCLUDED ABOVE IN "OFFICE SUPPLIES/EXPENSES"
Basis: |  | Sub-Total | 3140
Note:
1/ Fixed Maintenance costs are assumed to be 50% parts, 25% labor, 25% consumables.
0..

## LM6000PC_MMR_Gas (hidden)
City of Austin 4 x LM6000 Power Project
GE LM6000 - Major Maintenance Reserve
Gas Fired Operation |  |  |  |  | Project Life |  | 20 | Years
Lease Club Membership Fees Not Included | [6 empty] | 5652000 | total cost
[7 empty] | 1413000 | cost per engine
Total Number of Installed Units |  |  | 4 |  |  |  | 70650 | cost per year per engine
[7 empty] | 54.3462 | cost per FIRED hour per engine
Inputs
Annual Lease Club Fees |  |  | 0 | per engine |  |  | $201,368 for LM6000 DLE (PD) & 20% increase for liquid fuel operation
Lease Engine Usage Fee |  |  | 83650 | per week (1-26 weeks) |  |  | 50,000 hour engine refurbishment assumes 16 week usage of lease engine
Preventative Maintenance |  |  | 0 | per year |  |  | Semi-Annual Preventative Maintenance included in annual O&M
Hot Section Refurbishment / 24,000 hrs |  |  | 1403000 | per GT |  |  | Rotable exchange for the hot section
Engine Refurbishment / 50,000 hrs |  |  | 3000000 | per GT |  |  | Depot level repair
Labor & Engineering / Hot Section |  |  | 10000 |  |  |  | Misc rentals, Freight, Travel & diem for GE personnel
Labor & Engineering / Major |  |  | 25000 |  |  |  | Misc rentals, Freight, Travel & diem for GE personnel
Dispatch |  | 1300 | Fired hrs/yr
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Hours (EOY) |  | 1300 | 2600 | 3900 | 5200 | 6500 | 7800 | 9100 | 10400 | 11700 | 13000 | 14300 | 15600 | 16900 | 18200 | 19500 | 20800 | 22100 | 23400 | 24700 | 26000
Maint Inspection (C, H or M) | [19 empty] | h
Comb., Hot Sec & Major Maint. Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5612000 | 0
Preventative Miantenance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Labor & Engineering | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 0
Lease Program |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Engine Usage Fee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yearly Totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5652000 | 0 | 5652000
Assumptions:
1. Hot Gas Path inspection conducted at 25,000 fired hour intervals and Major at 50,000 hour intervals.
2. Pricing in 2000 USD. Does not include escalation beyond that.
3. Assumes that Owner will not enter the Lease Engine Membership program.
4. Maintenance and lease costs from George Graham/GE Mar 2000 e-mail.
BASE LOAD CASE
Gas Fired Operation |  |  |  |  | Project Life |  | 20 | Years
Lease Club Membership Fees Included | [6 empty] | 56877600 | total cost
[7 empty] | 14219400 | cost per engine
Total Number of Installed Units |  |  | 1 |  |  |  | 710970 | cost per year
[7 empty] | 88.8713 | cost per FIRED hour
Inputs
Annual Lease Club Fees |  |  | 0 | per engine |  |  | $201,368 for LM6000 DLE (PD) & 20% increase for liquid fuel operation
Lease Engine Usage Fee |  |  | 23900 | per week (1-26 weeks) |  |  | 48,000 hour engine refurbishment assumes assumes 12 week usage of lease engine
Preventative Maintenance |  |  | 0 | per year |  |  | Semi-Annual Preventative Maintenance
Hot Section Refurbishment / 24,000 hrs |  |  | 1403000 | per GT | (rotable exchnage) |  | excludes DLE adder
Engine Refurbishment / 48,000 hrs |  |  | 3000000 | per GT |  |  | excluding 20% adder for DLN
Labor & Engineering / Hot Section |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Labor & Engineering / Major |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Dispatch |  | 8000 | Fired hrs/yr
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Hours (EOY) |  | 8000 | 16000 | 24000 | 32000 | 40000 | 48000 | 56000 | 64000 | 72000 | 80000 | 88000 | 96000 | 104000 | 112000 | 120000 | 128000 | 136000 | 144000 | 152000 | 160000
Maint Inspection (H or M) |  |  |  | H |  |  | M |  |  |  | H |  | M |  |  | H |  |  | M
Hot Sec & Major Maint. | 0 | 0 | 0 | 5612000 | 0 | 0 | 12000000 | 0 | 0 | 0 | 5612000 | 0 | 12000000 | 0 | 0 | 5612000 | 0 | 0 | 12000000 | 0 | 0
Preventative Miantenance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Labor & Engineering | 0 | 0 | 0 | 100000 | 0 | 0 | 100000 | 0 | 0 | 0 | 100000 | 0 | 100000 | 0 | 0 | 100000 | 0 | 0 | 100000 | 0 | 0
Lease Program |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Engine Usage Fee | 0 | 0 | 0 | 0 | 0 | 0 | 1147200 | 0 | 0 | 0 | 0 | 0 | 1147200 | 0 | 0 | 0 | 0 | 0 | 1147200 | 0 | 0
| 0 | 0 | 0 | 5712000 | 0 | 0 | 13247200 | 0 | 0 | 0 | 5712000 | 0 | 13247200 | 0 | 0 | 5712000 | 0 | 0 | 13247200 | 0 | 0
|  | 0 | 0 | 5712000 | 5712000 | 5712000 | 18959200 | 18959200 | 18959200 | 18959200 | 24671200 | 24671200 | 37918400 | 37918400 | 37918400 | 43630400 | 43630400 | 43630400 | 56877600 | 56877600 | 56877600
Assumptions:
1. Hot Gas Path inspection conducted at 25,000 fired hour intervals.
2. Major inspection conducted at 50,000 fired hour intervals.
3. Maintenance and lease costs from George Graham/Stewart & Stevenson 12/10/99 e-mail.