## Sheet1
|  | outdoor | indoor | LM6000 | LM6000 | LM6000 | LM6000 | LM6000
|  | example | example | optimum | ElectriCities | Fairley | optimum | optimum
ambient air temp | F | 90 | 75 | 50 | 91 | 95 | 95 | 50
ambient RH | % | 54% | 50% | 95% | 46% | 60% | 90% | 95%
ambient water | lbH20/lbdair | 0.0162 | 0.0093 | 0.00725 | 0.0143 | 0.0215 | 0.0322 | 0.00725
Latent heat | Btu/lb water | 1061 | 1061 | 1061 | 1061 | 1061 | 1061 | 1061
| Btu/lb air | 17.1882 | 9.8673 | 7.6923 | 15.1723 | 22.8115 | 34.1642 | 7.6923
Sensible heat, vapor | Btu/lb air | 0.64735 | 0.30969 | 0.16095 | 0.57778 | 0.90687 | 1.3582 | 0.16095
Sensible heat, air | Btu/lb air | 21.69 | 18.075 | 12.05 | 21.931 | 22.895 | 22.895 | 12.05
Total Heat | Btu/lb air | 39.5256 | 28.252 | 19.9032 | 37.6811 | 46.6134 | 58.4174 | 19.9032
exhaust flow | lb/hr |  |  |  | 1058729 | 1058729 | 1058729
fuel flow | lb/hr |  |  |  | -21793 | -21793 | -21793
nozzle water | lb/hr |  |  |  | -22257 | -22257 | -22257
Sprint water | lb/hr |  |  |  | -2194 | -2194 | -2194
compressor flow | lb/hr |  |  |  | 1012485 | 1012485 | 1012485
chilling required | Btu/hr |  |  |  | 17999833.9968 | 27043646.4725 | 38995045.7371
| ton/hr |  |  |  | 1499.9862 | 2253.6372 | 3249.5871
adjustment |  |  |  |  | 1.038 | 1.038 | 1.038
real chilling | ton/hr |  |  |  | 1556.9856 | 2339.2754 | 3373.0715

## waterwell
Ft Devens MA
for UAE Lowell
|  | LM6000 | LM6000
optimum
ambient air temp | F | 50 | 80
ambient RH | % | 95% | 40%
cooling to 50/95%
ambient water | lbH20/lbdair | 0.00725 | 0.0088 | look up in pyscho table
Latent heat | Btu/lb water | 1061 | 1061
| Btu/lb air | 7.6923 | 9.3368 | 32.27%
Sensible heat, vapor | Btu/lb air | 0.16095 | 0.31258 | 1.08%
Sensible heat, air | Btu/lb air | 12.05 | 19.28 | 66.65%
Total Heat | Btu/lb air | 19.9032 | 28.9294
exhaust flow | lb/hr |  | 1058729
fuel flow | lb/hr |  | -21793
nozzle water | lb/hr |  | -22257
Sprint water | lb/hr |  | -2194
compressor flow | lb/hr |  | 1012485
chilling required | Btu/hr |  | 9138867.8074
| ton/hr |  | 761.5723
adjustment |  |  | 1.038
real chilling | ton/hr |  | 790.5121