## Table of Contents
AES Corp, Dallas, TX (640 MW)
Operations & Maintenance Cost Estimate
Table of Contents
Table of Contents |  |  | 1
Scope
| Project Scope Description |  | 2
| List of Assumptions |  | 3
| Map |  | 4
Summary - Operations & Maintenance Cost Estimate |  |  | 4
| Comparison vs. Other Plants |  | 6
O&M Staff Organization Chart |  |  | 7
O&M Pre-Mobilization / Mobilization Cost Estimate |  |  | 5
Commercial Operations O&M Estimate |  |  | 6
Major Maintenance Cost Estimate
| Initial Operating Spares |  | 7
GT Scheduled Major Maint. Program (year by year)
|  | 2xGE-Frame 7FA GT Scheduled Maintenance Cost | 7
Summary - Housing Colony Operating Cost Estimate |  | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 8
| Mobilization Cost Estimate | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 9
| Mobilization Staffing Plan | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 10
| Commercial Operations Operating Cost Estimate | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 11
| Staffing Plan | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 12
| Mobilization Cost Estimate Backup/Detail | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 13
| Operating Cost Estimate Backup/ Detail | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 14
|  | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 15
|  | =IF('O&M Backup_Detail'!O7=1,'GT sched cost (LM6000)'!A1,if('O&M Backup_Detail'!O7=2,'GT schd cost(7EA)'!A2,if('O&M Backup_Detail'!O7=3,'GT schd cost(7FA)'!A2,if('O&M Backup_Detail'!O7=4,'GT schd cost(W501D5)'!A2,if('O&M Backup_Detail'!O7=6,'GT schd cost(6B)'!A2,""))))) | 16

## Scope
AES Corp, Dallas, TX (640 MW)
Project Scope Description
Project Name: | Name |  | AES Corp
Location: | Nearest City |  | Dallas, TX
| Country |  | USA
Capacity: | Nominal baseload capacity (MW) |  | 640
Equipment: | Gas turbine model | 2 | GE 7FA
| Each gross gas turbine output (MW) |  | 170
| Cycle (Simple, Combined) |  | combined
| Gas turbine model | 0 | None
| Each gross gas turbine output (MW) |  | 0
Cycle (Simple, Combined)
| Gas turbine model | 0 | None
| Each gross gas turbine output (MW) |  | 0
Cycle (Simple, Combined)
| Steam Turbine | 2 | Condensing
| Each gross steam turbine output (MW) |  | 150
| Steam Turbine | 0 | Condensing
| Each gross steam turbine output (MW) |  | 0
| Other fired vessels | 0
Capacity (KPPH)
| Cooling Tower |  | Induced draft/Wet
Gas Compressors
Chillers
| Demin System |  | Cation/Anion
Fuel: | Primary: |  | Pipeline Quality Natural Gas
| Secondary: |  | None
Operations Mode: | Plant load factor (%) |  | 95%
| MWh generated per year |  | 5326080
| Number of operational hours per year |  | 8322
| Number of starts per year |  | <100
| Load Profile (Base/Peaker/Intermediate) |  | Base
PPA: | PPA to be signed with |  | TBD
Tentative schedule: | Notice to Proceed (EPC) |  | TBD
| Comercial Operations Date |  | 2003-01-01
Housing Colony: | Employees live in Mumbai. No housing colony on site.
Commercial Office: | Location |  | Mumbai
Other Facilities: | Barge dock on river for fuel deliveries.
Owners Engineer: | Provided by |  | Enron
O&M Estimate: | Date |  | 2000-05-19 12:48
| Provided by: |  | Rich Bickings / Asset Ops.

## Assumptions
AES Corp, Dallas, TX (640 MW)
List of Assumptions
Base year for all costs and prices herein: current 2000 US $ (no escalation or inflation included).
Prime Mover
| 1 | 2xGE 7FA with DLN combustor.
| 2 | 2xCondensing Steam Turbine
Operations
| 1 | Plant is Base loaded with a PLF of 95%
| 2 | Plant is assumed to start <100 times per year
Fuel
| 1 | Pipeline Quality Natural Gas
| 2 | None
Water Treatment
| 1 | Raw water make-up provided by Muni
| 2 | Pre-treatment to be Anion/Cation Demineralizer
Inlet Air Cooling
| 1 | Each GE LM6000 to be equipment with 2000 tons inlet cooling
Plant Staff
| 1 | Plant is assumed to be staffed year round.
| 2 | Labor cost is based regional OEC salary & benefit accuals.
Contracters
| 1 | EPC Contracter unknown.
| 2 | Owner's Engineer is unknown
| 3 | Scope split between turnkey/startup contractor owwner/operator per enclosed schedule.
Cost Assumptions
| 1 | GT parts discount of 10%. No LTSA signed.
| 2 | All costs are based in US Dollars.
Project Commercial Office
| 1 | Commercial office: Houston Corporate Office.
| 2 | Functions of commercial include: | Revenue and Property Book Accounting including customer and fuel supplier billing
|  | a) | Tax Accounting including preparing Local and US tax returns
|  | b) | Annual financial audits by outside auditors.
|  | c) | Maintaining Bank accounts and treasury functions
|  | d) | Commercial contracts and interface with Power Purchasers and Fuel Suppliers
|  | e) | Fuel purchasing & supply, logistics and scheduling
|  | f) | Government and Public Relations
|  | g) | Legal and contractual requirements
|  | h) | Project Human resources (compensation and benefits plans)
|  | i) | Interface with Lenders and Partners regarding funding and information requests
|  | j) | Budgeting, Operating and Capital planning
|  | k) | Dealing with Customs authorities with regard to imported goods and services.
l)
This O&M Estimate does not include the cost of the following items:
| 1 | Fuel
| 2 | Raw Water makeup
| 3 | Purchased (backfeed) power and other purchased utilities
| 4 | Owner's Insurance (Operator to be named as additional insured)
| 5 | Buildings: Administration, Warehouse and Shop facilities
| 6 | Operating or Environmental Permits (Operator to assist Owner in obtaining)
| 7 | Communications facilities (internal & external)
| 8 | Customs duties, Taxes or VAT
| 9 | Changes in escalation, inflation or exchange rate

## Summary
AES Corp, Dallas, TX (640 MW)
Summary - Operations & Maintenance Cost Estimate
Expenses before Commercial Operation:
US $
O&M Pre-Mobilization / Mobilization Expenses
| Pre-Mobilization Expenses |  | 33679
| Mobilization Payroll and Burden |  | 517680.9145
| Mobilization Operating Expenses |  | 341215.7143
| Mobilization Procurement Expenses |  | 260555.2229
| Total O&M Pre-Mobilization / Mobilization Expenses |  | 1153130.8517
| Housing Colony Mobilization Expenses |  | #REF!
| Commercial Office Mobilization Expenses |  | #REF!
| Owners' Engineer Expenses |  | #REF!
| Initial Operating Spares |  | 9657148.05
| OM&A Mobilization Fee (incl. Comm. Office) |  | 120000
| Operator Overhead Charge (G&A) |  | 0
Expenses during Commercial Operation:
[7 empty] | Annual | 20 YEAR
|  |  | Year 1 | Year 2 | Year 3 | Years 4+ | Avg. (20 yrs) | FOM ($/kW-yr) | VOM ($/mWh)
O&M Expenses
| Payroll and Burden |  | 1451918.666 | 1451918.666 | 1451918.666 | 1451918.666 | 1451918.666 | 2.2686
| Administration & Operations Expenses |  | 348852.285 | 348852.285 | 348852.285 | 348852.285 | 348852.285 | 0.54508
| Chemicals at PLF |  | 604319.675 | 604319.675 | 604319.675 | 604319.675 | 604319.675 |  | 0.11346
| Maintenance Expenses (excl. GT Scheduled Maint. Program) |  | 1239658.4712 | 1254171.6308 | 1254171.6308 | 2309119.5677 | 2150151.7192 | 2.5197 | 0.10093
| Sustaining Capital Expenses |  | 26055.5223 | 26055.5223 | 26055.5223 | 26055.5223 | 26055.5223 | 0.040712
| Total O&M Expenses (excl. GT Scheduled Maint.) |  | 3670804.6195 | 3685317.7791 | 3685317.7791 | 4740265.716 | 4581297.8675
[8 empty] | 5.3741 | 0.21439
GT Scheduled Major Maintenance Program |  | 20 yr total | 141072289.1304 |  |  | Annual Avg. | 7053614.4565
Total Plant O&M Expenses (incl. GT Scheduled Maint.) | [5 empty] | Annual Avg. | 11634912.324
Housing Colony Operating Expenses |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
Commercial Office Expenses |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
Average Annual Operating Expenses (excluding Fee) | [6 empty] | #REF!
OM&A Annual Fee (incl. Commercial Office) |  |  | 1160000 | 1160000 | 1160000 | 1160000 | 1160000
Operator Overhead Charge (G&A) |  |  | 0 | 0 | 0 | 0 | 0
* - variable with power generated

## Mob_Estimate
AES Corp, Dallas, TX (640 MW)
O&M Pre-Mobilization / Mobilization Cost Estimate
US $
O&M Pre-Mobilization Expenses |  | 33679
Mobilization Payroll & Burden |  | 517680.9145
Mobilization Operating Expenses
| Employee Expenses | 6000
| Recruiting Expenses | 10500
| Relocation Expenses | 21750
| Outside Services | 47250
| Other Supplies & Expenses | 8635.7143
| Communications | 6300
| Temporary Offices/Facilities | 2800
| Training | 156580
| Manuals & Procedures | 61150
| Permits | 0
| Insurance | 5000
| Operations Support Personnel | 15250
| Total Mobilization Operating Expenses | 341215.7143
Mobilization Procurement Expenses
| Office Furnishings & Equipment | 89092.5
| Safety & Environmental Equipment | 21420
| Vehicles & Mobile Equipment (excluding switch engine) | 13210
| Warehouse Furnishings & Equipment | 12075
| Laboratory Equipment | 6300
| Shop Tools & Equipment | 68097.75
| Chemicals, Lubricants, Hydraulic Fluids | 50359.9729
| Total Mobilization Procurement Expenses | 260555.2229
Total O&M Pre-Mobilization / Mobilization Expenses |  | 1153130.8517
Initial Operating Spares |  | 9657148.05
OM&A Mobilization Fee (incl. Commercial Office) |  | 120000
Operator Overhead Charge (G&A) |  | 0

## Mob_Schedule (hidden)
AES Corp, Dallas, TX (640 MW)
Staff Mobilization Schedule
Months Prior to COD | No. of Employees | Month on Site Prior to COD | No. of Months on Site | -19 | -18 | -17 | -16 | -15 | -14 | -13 | -12 | -11 | -10 | -9 | -8 | -7 | -6 | -5 | -4 | -3 | -2 | -1 | COD
Employees | 3 | [9 empty] | Recruiting/Procedures ----> |  |  |  | Training/Early Commissioning-------> |  |  |  | Commissioning/Startup -------->
Controller
Plant Manager | 1 | -12 | 12 | [7 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Assistant Plant Manager | 0 | 0 | 0
Plant Engineer | 0 | 0 | 0
Administration Manager | 0 | 0 | 0
Controller | 0 | 0 | 0
Accountant | 0 | 0 | 0
Administrative Assistant | 1 | 7 | -7
Warehouse Supervisor | 0 | 0 | 0
Other | 0 | 0 | 0
Other | 0 | 0 | 0
Other | 0 | 0 | 0
Operations Staff
Operations Manager | 1 | -9 | 9 | [10 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Operations Shift Supervisors | 0 | 0 | 0
Control Room Operators | 0 | 0 | 0
Turbine Operators | 0 | 0 | 0
Water System Opertors | 0 | 0 | 0
Fuel Storage/Handling Operators | 0 | 0 | 0
Utility Operators | 0 | 0 | 0
Chemist | 0 | 0 | 0
Tech III | 4 | -6 | 6 | [13 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Tech II | 4 | -6 | 6 | [13 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Other | 0 | 0 | 0
Maintenance Staff
Maintenance Manager | 1 | -9 | 9 | [10 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Mechanical Engineer | 0 | 0 | 0
Maintenance Planner | 0 | 0 | 0
Mechanic | 1 | -6 | 6 | [13 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
I&C Engineer | 0 | 0 | 0
I&C Technician | 1 | -6 | 6 | [13 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Electrical Technician | 1 | -6 | 6 | [13 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Other | 0 | 0 | 0
Other | 0 | 0 | 0
Other | 0 | 0 | 0
Other | 0 | 0 | 0
FACILITY NEEDS
Administration Facilities |  | -8 | 8 | [11 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Office Equipment |  | -6 | 6 | [13 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Warehouse Equipment/Shop |  | -3 | 3 | [16 empty] | XXXXX | XXXXX | XXXXX
Vehicles |  | -8 | 8 | [11 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Training Facilities |  | -6 | 6 | [13 empty] | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX | XXXXX
Tools & Equipment |  | -3 | 3 | [16 empty] | XXXXX | XXXXX | XXXXX

## Mob_Staffing (hidden)
AES Corp, Dallas, TX (640 MW)
O&M Staff Mobilization Plan
[6 empty] | of | Salary | Salary | at 15% | Benefits
|  | No. of Expats | No. of Locals | Total No. of Employees | Month on Site Prior to COD | No. of months on site | Individual Base Salary USD/Month | Overtime USD/Month | Benefits USD/Month | Total Mobilization Salary
(negative No.)
Administration Staff
| Plant Manager | 0 | 1 | 1 | -12 | 12 | 7250 | 0 | 5089.5 | 148074
| Assistant Plant Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Plant Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Administration Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Controller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accountant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Administrative Assistant | 0 | 1 | 1 | 7 | -7 | 2250 | 337.5 | 1758.7125 | -30423.4875
| Warehouse Supervisor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operations Staff
| Operations Manager | 0 | 1 | 1 | -9 | 9 | 5833.3333 | 0 | 4095 | 89355
| Operations Shift Supervisors | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Control Room Operators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Turbine Operators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water System Opertors | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel Storage/Handling Operators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Utility Operators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chemist | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tech III | 0 | 4 | 4 | -6 | 6 | 4333.3333 | 650 | 3387.15 | 50222.9
| Tech II | 0 | 4 | 4 | -6 | 6 | 3813.3333 | 572 | 2980.692 | 44196.152
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maintenance Staff
| Maintenance Manager | 0 | 1 | 1 | -9 | 9 | 5416.6667 | 0 | 3802.5 | 82972.5
| Mechanical Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Maintenance Planner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mechanic | 0 | 1 | 1 | -6 | 6 | 3166.6667 | 475 | 2475.225 | 36701.35
| I&C Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I&C Technician | 0 | 1 | 1 | -6 | 6 | 4583.3333 | 687.5 | 3582.5625 | 53120.375
| Electrical Technician | 0 | 1 | 1 | -6 | 6 | 3750 | 562.5 | 2931.1875 | 43462.125
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL |  | 0 | 15 | 15 | [5 empty] | 517680.9145

## Training (hidden)
AES Corp, Dallas, TX (640 MW)
Training Program
Class
|  | Weeks | Weeks | $M
Basic Plant Training (All O&M Personnel) (1sessions)
| New Employee Orientation (1 day) * | 0.2 | 0.2 | 1.2
| Plant Safety/Environmental/Firefighting (3 days) * | 0.6 | 0.6 | 3.6
| Power Plant Basic O&M (2 days) | 0.4 | 0.4 | 2.4
| Introduction to Plant Systems (3 days) | 0.6 | 0.6 | 3.6
|  | 1.8 | 1.8 | 10.8
Major Systems Training (All O&M Personnel) (1 sessions)
| GT&G Operation & Familiarization (equip vendor)3 | 1 | 1 | 20
| Boiler Familiarization & Operation (general vendor) | 1 | 1 | 8
| Balance of Plant (general vendor) | 0.6 | 0.6 | 4.8
|  | 2.6 | 2.6 | 32.8
Specialized Operator Training (All Operators & Chemist) (1 session)
| Boiler & Cooling Water Chemistry (general vendor) | 0.4 | 0.4 | 3.2
|  | 0.4 | 0.4 | 3.2
Control Room Training (Ctrl Rm Ops, Shft Supvrs, Utl Ops) (1 session)
| GTG controls (equip vendor) | 0.6 | 0.6 | 12
| Boiler controls (general vendor) | 0.4 | 0.4 | 3.2
| DCS (equip. vendor) | 0.6 | 0.6 | 12
|  | 1.6 | 1.6 | 27.2
Basic Maintenance Training (All Mechanics) (1 session)
| GT-G Maintenance (equip. vendor) | 1 | 1 | 20
| Boiler Maintenance (general vendor) | 0.6 | 0.6 | 4.8
|  | 1.6 | 1.6 | 24.8
Electrical/Controls Maintenance Training (I/C/E Technicians) (1 session)
| Excitation Maintenance (equip. vendor) | 0.6 | 0.6 | 12
| Electrical System Maintenance (general vendor) | 0.4 | 0.4 | 3.2
| DCS Maint. (equip. vendor) | 0.6 | 0.6 | 12
| Mark VI | 2 | 2 | 20
|  | 3.6 | 3.6 | 47.2
Total Class Training Cost |  |  | 11.6 | 146
Travel, lodging, facilities, misc.
| Instructor Per diem: # class weeks x 7d/wk x $150/day (1 instructor/class week) |  |  | 12.18
| Travel: 7 (3 Basic, 4 Vendor) instructors x $1M/trip |  |  | 7
| On site Training Coordinator/Instructor (4 wks x $2600/wk incl per diem + $1M travel) * |  |  | 11.4
30.58
Total Training Cost Estimate |  |  |  | 176.58
| Less Training provided by Turnkey/Startup Contractor |  |  | 20
Net Training Cost Estimate ($M) for Operator/Owner |  |  |  | 156.58
Notes:
1. Assumed cost of training (instructor, training materials, aids, manuals, etc.):
Equip. Vendor Training - $20M/wk
Basic Plant Training (developed in-house) - $6M/wk
General Vendor Training - $8M/wk
2. The asterisk (*) denotes training and expenses provided by Operator

## ScopeSplit (hidden)
AES Corp, Dallas, TX (640 MW)
Turnkey/O&M/Owner Scope Split
Turnkey/
| Startup | O&M | Owner | Remarks/Comments
OPERATING EXPENSES (pre-COD):
Payroll and Benefits
for Owner Personnel |  |  | x
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Employee Expenses/Recruiting/Relocation
for Owner Personnel |  |  | x
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Outside Services
Technical Direction of Installation (TD&I) | x
Vendor reps & startup services | x
Security before COD | x
Security after COD |  | x
O&M related services |  | x
Reliability Availability Maintainability (RAM) Study |  | x |  | EPC to assist & participate
Process Hazards Analysis (HAZOP) | x |  |  | O&M to assist & participate
Other Supplies & Expenses
for O&M Personnel |  | x
for Turnkey/Startup Personnel | x
Communications (phone bills, etc.)
for O&M Personnel |  | x
for Startup Personnel | x
Offices/Buildings/Facilities (temporary)
for O&M Personnel (admin, training, etc.) |  | x
for Startup/Commissioning Personnel | x
Training for O&M Personnel *
Vendor Familiarization Training (CT, ST, HRSG, WT/Desal) | x |  |  | Defined scope req'd
Add'l Major Equip. Vendor (CT,ST,HRSG, WT/Desal,DCS) | x |  |  | Defined scope req'd
OJT during startup/commissioning | x |  |  | Defined scope req'd
Basic Power Plant Training (& all other training) | x |  |  | Defined scope req'd
Permits/Insurance
Construction & Startup Contractor's name | x |  |  | need permit matrix
Operator's name |  | x |  | "
Owner's name |  |  | x | "
Manuals, Procedures and Plans
Startup/Commissioning Plans & Procedures | x
Job Data books | x
Engineering drawings (incl. "as builts") | x |  |  | AutoCad 14 (or apprvd substitute)
Systems Descriptions | x
Test procedures & report | x
O&M Procedures |  | x
Admin and all other Plant procedures |  | x
Punchlist resolution | x |  |  | with O&M walkdown
Purchase and transportation of fuel to plant (startup) | x |  |  | Allowance in LSTK price
Schedule fuel deliveries from supplier |  | x
Purchase of turbine generator startup power (backfeed) |  |  | x
Purchase of construction power (from fence line) | x
Purchase and delivery of Process water (hydrotests, etc) | x
Steam Blows | x |  |  | Given power, fuel and water
Chemical Cleaning (including disposal) | x
Oil Flushes | x
* O&M has overall responsibility for training O&M personnel, but Major Equip. Vendor training (for CTs, STs, HRSGs, Water
Treatment/Desal, and DCS) will be provided under the major equip. purchase orders (with O&M participation in scoping).
Turnkey/
| Startup | O&M | Owner | Remarks/Comments
Warranty Implementation | x |  |  | O&M/Owner participate
Pre-Mobilization expenses
O&M engineering review/comments |  | x
Operating plans/budgets/estimates |  | x
Other Owner directed O&M services |  | x
Fuel/water quality checking (pre-COD) | x
Procurement Expenses:
Office Furnishings & Equipment
Stationary items (built-ins) | x
PABX (internal) telephone system & wiring | x
LAN wiring | x
External communications (satellite dish) |  |  | x
Office/Building furniture |  | x
Office equipment (copiers, fax, etc.) |  | x
Computer hardware/software |  | x
CMMS computer system (incl training) |  | x |  | with Owner approval
Safety & Environmental equipment
Permanent Fire protection | x
Portable fire extinguishers (for offices & buildings) | x
Portable fire extinguishers (exterior) | x
Safety showers/eye washes | x
Permanent Environmental testing equip. | x |  |  | if required
Portable Environmental testing equip. |  | x
O&M Personnel Safety/First Aid equip. |  | x
Vehicles & Mobile Equipment
Construction/Startup Contractor requirements | x
O&M requirements (@ post Comm. Opns level) |  | x
Warehouse/Shop Furnishings & Equipment
Stationary items incl hoists (built-ins) | x
Non-stationary items (bins, furniture, etc.) |  | x
Process Monitoring & Laboratory Equipment
Installed analyzers/instruments | x
Stationary lab items (vent hoods, lab benches, etc.) | x
Analytical equipment, glassware, etc. |  | x
Shop Tools and Equipment
Machine shop/Instrument shop tools |  | x
Maint. (incl I/C&E) test equipment |  | x
Work benches, storage bins |  | x
Hand tools for O&M personnel |  | x
Hand tools for Startup personnel | x
Special Tools
Startup, Std Vendor supply | x
Optional vendor supply |  | x |  | Incl with Vendor PO
Chemicals, Lubricants, Fluids
Initial equipment/vessel fill | x
Consumption (pre-COD) | x
Consumption (post-COD) |  | x
Warehouse stock |  | x
Spare parts*
Consumption (pre-COD) | x
Consumption (post-COD) |  | x
Capital (Overhaul) Spares for major equip. |  | x |  | Incl. with Vendor PO
Operating (Initial) Spares for major equip. |  | x |  | Incl. with Vendor PO
Warehouse stock & BOP spare parts |  | x
Installed Cranes | x
* Turbine spare parts will be purchased based on competitive bids as part of and prior to Turbine vendors selection;
actual parts purchased will be approved by Owner.

## Mob_Backup (hidden)
AES Corp, Dallas, TX (640 MW)
O&M Pre-Mobilization / Mobilization Estimate Backup/Detail
| EstimateSummary | Group Item | Budget Item | Line Item | Detail/Basis |  | Total Cost (USD) | Local Cost % | LOCAL | FOREIGN | Calculation and Note Area
O&M Mobilization BudgetOperating ExpensesPublic Relations Title | O&M Mobilization Budget | Operating Expenses | Public Relations | Pre-Mobilization Expenses
O&M Mobilization BudgetOperating ExpensesPublic Relations | O&M Mobilization Budget | Operating Expenses | Public Relations | Payroll and Benefits (US) |  |  | 0 | 100% | 0 | 0
[5 empty] | Plant Manager - 2 months prior to site mob |  | 24679 | 100% | 24679 | 0
|  |  |  | Travel Expenses in Region | $150/dayperdiem x 60 days |  | 9000 | 100% | 9000 | 0
|  |  |  | Travel for Expat To/From Home (UK) | 1 trip/quarter x 3 quarters x $6M/trip |  | 0 | 100% | 0 | 0
|  |  |  | Temporary Living (Expat) in Houston | $3000/month x 9 months |  |  | 100% | 0 | 0
|  |  |  | Tech Services/Studies | 15 mandaysx$75/hrx8hrs/d |  |  | 100% | 0 | 0
|  |  |  | Miscellaneous (comms, etc.) | $1000/month x 12 months |  |  | 100% | 0 | 0
[5 empty] | HAZOP Study (3rd party consultant) |  |  | 100% | 0 | 0
[5 empty] | RAM Study (3rd party consultant) |  |  | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesPublic Relations Total | O&M Mobilization Budget | Operating Expenses | Public Relations |  |  | Sub-Total | 33679 |  | 33679 | 0
O&M Mobilization BudgetOperating ExpensesPayroll with burden Title | O&M Mobilization Budget | Operating Expenses | Payroll with burden | Payroll with burden
|  |  |  | Total Company Payroll with benefits and 15% overtime on Opns/Maint. (w/o expats) personnel |  |  | 517680.9145 | 100% | 517680.9145 | 0
(See detailed PltMobStaff schedule)
O&M Mobilization BudgetOperating ExpensesPayroll with burden Total | O&M Mobilization Budget | Operating Expenses | Payroll with burden | Basis: Project Schedule |  | Sub-Total | 517680.9145 |  | 517680.9145 | 0
O&M Mobilization BudgetOperating ExpensesEmployee Expenses Title | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Employee Expenses
O&M Mobilization BudgetOperating ExpensesEmployee Expenses | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Trips to US | 5 trips to US x $6M + $150/dayperdiem x 50 days |  | 0 | 100% | 0 | 0
|  |  |  | Misc. (OT meals, Conferences,etc.) | Travel Exp./O.T. Meals (33% of Travel) |  | 0 | 100% | 0 | 0
|  |  |  | Meal Allowance | $2/day/employee x 200 days x # staff |  | 6000 | 100% | 6000 | 0
O&M Mobilization BudgetOperating ExpensesEmployee Expenses Total | O&M Mobilization Budget | Operating Expenses | Employee Expenses | Basis: HR recommends 1 meal/day subsidized by the company |  | Sub-Total | 6000 |  | 6000 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses Title | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Recruiting Expenses
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | HR/Home office support | 2 trips x $1M/trip + $150/day x 10days |  | 3500 | 100% | 3500 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses | Advertisements | Local |  | 3000 | 0% | 0 | 3000
|  |  |  | Screening Tests | $200/employee |  | 3000 | 100% | 3000 | 0
|  |  |  | Misc expenses | reproduction, postage, etc |  | 1000 | 100% | 1000 | 0
O&M Mobilization BudgetOperating ExpensesRecruiting Expenses Total | O&M Mobilization Budget | Operating Expenses | Recruiting Expenses |  |  | Sub-Total | 10500 |  | 7500 | 3000
O&M Mobilization BudgetOperating ExpensesRelocation Expenses Title | O&M Mobilization Budget | Operating Expenses | Relocation Expenses | Relocation Expenses
O&M Mobilization BudgetOperating ExpensesRelocation Expenses | O&M Mobilization Budget | Operating Expenses | Relocation Expenses | Plant Mgr | Assumed 25% of base pay to cover goods, house hunt, lump sum |  | 21750 | 0 | 21750
|  |  |  | Technician III (assume 1 needed) | cover HHG shipment |  |  | 100% | 0 | 0
|  |  |  | Technician II (assume 1 needed) | cover HHG shipment |  |  | 0% | 0 | 0
|  |  |  | Rest of staff assumed obtained locally |  |  |  | 100% | 0 | 0
|  |  |  | Locals | 25% of Base Salaries + $200/person for examination |  |  | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesRelocation Expenses Total | O&M Mobilization Budget | Operating Expenses | Relocation Expenses |  |  | Sub-Total | 21750 |  | 21750 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services Title | O&M Mobilization Budget | Operating Expenses | Outside Services | Outside Services
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Guards | Turnkey responsibility |  |  | 100% | 0 | 0
|  |  |  | Groundskeepers | Turnkey responsibility |  |  | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Janitors | contract |  | 4000 | 100% | 4000 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Legal | Covered in Fee |  | 0 | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Tax | Covered in Fee |  | 0 | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Accounting | Covered in Fee |  | 0 | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Safety | 2 trips x $1M/trip + 8 days perdiem x $150/day |  | 3200 | 100% | 3200 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Environmental | 2 trips x $1M/trip + 8 days perdiem x $150/day |  | 3200 | 100% | 3200 | 0
|  |  |  | Management | 2 trips x $1M/trip + 8 days perdiem x $150/day |  | 3200 | 100% | 3200 | 0
|  |  |  | Technical/Professional | 15 days x $60/hr x 8hrs/day |  | 7200 | 100% | 7200 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Trash/Waste Disposal | Turnkey responsibility |  |  | 100% | 0 | 0
|  |  |  | Electrical Testing/Calibration | Turnkey responsibility |  |  | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Buyer support from other OEC projects | $40/hr x 500 manhrs |  | 20000 | 100% | 20000 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Uniform services |  |  | 3250 | 100% | 3250 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services | Office Equipment Maintenance |  |  |  | 100% | 0 | 0
[7 empty] | 3200 | 100% | 3200 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services |  |  |  |  | 100% | 0 | 0
[8 empty] | 100% | 0 | 0
[8 empty] | 100% | 0 | 0
[8 empty] | 100% | 0 | 0
[8 empty] | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services | O&M Mobilization Budget | Operating Expenses | Outside Services |  |  |  |  | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesOutside Services Total | O&M Mobilization Budget | Operating Expenses | Outside Services | Basis: HR Salary & Benefits Survey |  | Sub-Total | 47250 |  | 47250 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses Title | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Other Supplies & Expenses
|  |  |  | Postage & Freight | $100/month x 6 months |  | 600 | 100% | 600 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Office & Misc. Supplies (usage) | $500/month x 5 months |  | 2500 | 100% | 2500 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Vehicle fuel and maint | 1 vehicles x 5 months x 1000miles/month x $1.5/14 miles + $500 |  | 1035.7143 | 100% | 1035.7143 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Janitorial Supplies (usage) |  |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses | Bldg. Utilities (water, power, gas) | 5 months x $500/month |  | 2500 | 100% | 2500 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses |  |  |  |  | 100% | 0 | 0
[8 empty] | 100% | 0 | 0
[8 empty] | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesOther Supplies & Expenses Total | O&M Mobilization Budget | Operating Expenses | Other Supplies & Expenses |  |  | Sub-Total | 8635.7143 |  | 8635.7143 | 0
O&M Mobilization BudgetOperating ExpensesCommunications Title | O&M Mobilization Budget | Operating Expenses | Communications | Communications
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Phone Service | 5 months x $500/month (excludes cellular service) |  | 2500 | 100% | 2500 | 0
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications | Cellular Phones | 2ea. x 6 months x $300/month |  | 3600 | 100% | 3600 | 0
O&M Mobilization BudgetOperating ExpensesCommunications | O&M Mobilization Budget | Operating Expenses | Communications |  | cellular activation fee: 2 ea. $100 |  | 200 | 100% | 200 | 0
O&M Mobilization BudgetOperating ExpensesCommunications Total | O&M Mobilization Budget | Operating Expenses | Communications |  |  | Sub-Total | 6300 |  | 6300 | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses Title | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Temporary Offices/Facilities
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Office Bldgs. |  |  |  | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Trailers (admin only, ex training) | 1x2monthsx$1000/month (if available) |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Sanitary facilities | 2x2monthsx$200/month |  | 800 | 100% | 800 | 0
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses | Misc. Furnishings |  |  |  | 100% | 0 | 0
|  |  |  | Temporary Living Quarters |  |  |  | 100% | 0 | 0
Assume admin facilties complete COD minus 5 months
O&M Mobilization BudgetOperating ExpensesMiscellaneous Office Expenses Total | O&M Mobilization Budget | Operating Expenses | Miscellaneous Office Expenses |  |  | Sub-Total | 2800 |  | 2800 | 0
O&M Mobilization BudgetOperating ExpensesTraining Title | O&M Mobilization Budget | Operating Expenses | Training | Training
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Basic Plant Training | See Training sheet |  | 156580 | 100% | 156580 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Major Systems Training |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Plant Chemistry |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Control Room Training |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Basic Maintenance |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Electrical/Controls Maintenance |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Additional Vendor Training |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Per diem for instructors |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Facilities (trailer rental, hall) |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Travel |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Training Coordinator |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Additional Manuals/Documents |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Miscellaneous |  |  |  | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining | O&M Mobilization Budget | Operating Expenses | Training | Translation |  |  |  | 0% | 0 | 0
[8 empty] | 0% | 0 | 0
O&M Mobilization BudgetOperating ExpensesTraining Total | O&M Mobilization Budget | Operating Expenses | Training |  |  | Sub-Total | 156580 |  | 156580 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures Title | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Manuals/Operating Procedures
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Administration | 5 mandays x $400/day |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Operations check lists | 5P&IDsx 2 mandays each x $400/day |  | 4000 | 100% | 4000 | 0
|  |  |  | Maintenance | 1/2 of Operating procedures |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Maintenance/CMMS (excluding data) | 5 mandays @$400/manday |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Warehouse/Inventory | 5 mandays @$400/manday |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Emergency Plans | 40 mandays @$400/manday |  | 16000 | 100% | 16000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Safety and Health | 5 mandays @$400/manday |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Environmental Compliance | 20 mandays @$400/manday |  | 8000 | 100% | 8000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Utility dispatch | 10 mandays @$400/manday |  | 4000 | 100% | 4000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Government Reporting | 10 mandays @$400/manday |  | 4000 | 100% | 4000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Owner Reports | 5 mandays @$400/manday |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Houston Reports | 5 mandays @$400/manday |  | 2000 | 100% | 2000 | 0
|  |  |  | Accounting | 10 mandays @$400/manday |  | 4000 | 100% | 4000 | 0
|  |  |  | Training Program | 10 mandays @$400/manday |  | 4000 | 100% | 4000 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures |  |  |  |  | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures | Reproduction/Printing |  |  | 3000 | 100% | 3000 | 0
|  |  |  | Freight | 5% of Reproduction cost |  | 150 | 100% | 150 | 0
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures
O&M Mobilization BudgetOperating ExpensesManuals/Operating Procedures Total | O&M Mobilization Budget | Operating Expenses | Manuals/Operating Procedures |  |  | Sub-Total | 61150 |  | 61150 | 0
O&M Mobilization BudgetOperating ExpensesPermits Title | O&M Mobilization Budget | Operating Expenses | Permits | Permits
O&M Mobilization BudgetOperating ExpensesPermits | O&M Mobilization Budget | Operating Expenses | Permits | Owner's Scope of Supply |  |  | 0 | 100% | 0 | 0
O&M Mobilization BudgetOperating ExpensesPermits Total | O&M Mobilization Budget | Operating Expenses | Permits |  |  | Sub-Total | 0 |  | 0 | 0
O&M Mobilization BudgetOperating ExpensesInsurance Title | O&M Mobilization Budget | Operating Expenses | Insurance | Operator's Insurance
O&M Mobilization BudgetOperating ExpensesInsurance | O&M Mobilization Budget | Operating Expenses | Insurance |  |  |  | 5000 | 100% | 5000 | 0
O&M Mobilization BudgetOperating ExpensesInsurance | O&M Mobilization Budget | Operating Expenses | Insurance
O&M Mobilization BudgetOperating ExpensesInsurance Total | O&M Mobilization Budget | Operating Expenses | Insurance |  |  | Sub-Total | 5000 |  | 5000 | 0
Operations Support Personnel
|  |  |  | Operations Support Personnel | 1ea.x$350/dayx30days (includes benefits) |  | 10500 | 100% | 10500 | 0
|  |  |  | Per diem | 1ea.x$125/dayx30days |  | 3750 | 100% | 3750 | 0
|  |  |  | Home leave, travel | 1ea.x$1000 tripx1trips (coach class) |  | 1000 | 100% | 1000 | 0
[8 empty] | 100% | 0 | 0
[6 empty] | Sub-Total | 15250 |  | 15250 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies Title | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Office Furnishings, Equipment, Supplies
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Offices (desk, chair, table, misc) | 4ea @ $800/set |  | 3200 | 100% | 3200 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Chairs - misc. | 10ea @ $150 |  | 1500 | 100% | 1500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Bookshelves | 10ea @ $75 |  | 750 | 100% | 750 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | File Cabinets | 4ea @ $200 |  | 800 | 100% | 800 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Storage Shelves/Cabinets | 10ea @ $50 |  | 500 | 100% | 500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Conference Room (table & chairs) | 1ea @ $150 + $1500 |  | 1650 | 100% | 1650 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Tables | 1ea @ $150 |  | 150 | 100% | 150 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Chairs | 6ea @ $75 |  | 450 | 100% | 450 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Microwave | 1 ea @ $300 |  | 300 | 100% | 300 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Coffee Pot | 1 ea. @ $150 |  | 150 | 100% | 150 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Refrig. | 1 ea @ $750 |  | 750 | 100% | 750 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Lunch Room - Misc |  |  | 500 | 100% | 500 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Computer Tables | 5ea @ $200 |  | 1000 | 100% | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Computers w printers | 5ea @ $3000 |  | 15000 | 100% | 15000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Systems Software | 5ea @ $500 |  | 2500 | 100% | 2500 | 0
|  |  |  | CMMS software/installation | $10M License + $10M installation/training |  | 20000 | 100% | 20000 | 0
|  |  |  | CMMS hardware, equipment | 1 PC's ($2500), printer |  | 2500 | 100% | 2500 | 0
|  |  |  | SAP Acctg System | Software & License |  | 0 | 100% | 0 | 0
|  |  |  | SAP Acctg System | Training & Implementation |  | 10000 | 100% | 10000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Copiers | 1ea @ $8000 |  | 8000 | 100% | 8000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Typewriters | 1ea @ $250 |  | 250 | 100% | 250 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Local Area Network | LAN $2M + Installation $1,000 |  | 3000 | 100% | 3000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Calculators | 5ea @ $20 |  | 100 | 100% | 100 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Projectors (overhead) | 1ea @ $400 |  | 400 | 100% | 400 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | TV/VCR/Camcorders | 1ea @ $750/$500/$750 |  | 2000 | 100% | 2000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies |  |  |  |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | White Boards | 5ea @ $80 |  | 400 | 100% | 400 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | FAX machine | 2ea @ $400 |  | 800 | 100% | 800 | 0
|  |  |  | Misc Supplies | pens, paper, staplers, envelopes, etc. |  | 1000 | 100% | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies | Phones | 6ea @ $200 |  | 1200 | 100% | 1200 | 0
|  |  |  | Office Misc, pictures, plants, rugs, boards |  |  | 5000 | 100% | 5000 | 0
|  |  |  | Janitorial supplies |  |  | 1000 | 100% | 1000 | 0
|  |  |  | Freight | 5% of cost |  | 4242.5 | 100% | 4242.5 | 0
O&M Mobilization BudgetProcurement ExpensesOffice Furnishings, Equipment, Supplies Total | O&M Mobilization Budget | Procurement Expenses | Office Furnishings, Equipment, Supplies |  |  | Sub-Total | 89092.5 |  | 89092.5 | 0
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies Title | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Safety & Environmental Equipment & Supplies
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies | Personnel Safety equipment | Safety glasses, Hard hats, goggles, face shields, gloves,
[5 empty] | locks, acid suits, SCBA respirators, safety shoes, etc. |  | 3000 | 100% | 3000 | 0
|  |  |  | Portable Fire Extinguishers | 10ea. @ $120 |  | 1200 | 100% | 1200 | 0
|  |  |  | Firehose Cabinet Accessories |  |  | 7700 | 100% | 7700 | 0
|  |  |  | First Aid equipment | First Aid kit, stretcher, water jell blanket |  | 6000 | 100% | 6000 | 0
|  |  |  | Safety test Equipment | Biosystem unit, LEL & O2 meter |  | 2500 | 100% | 2500 | 0
|  |  |  | Environmental Test Equipment | Noise level meter |  |  | 100% | 0 | 0
|  |  |  | 6" and 12" containment booms |  | 44700
|  |  |  | 30 ton/hr skimmer |  | 21000
|  |  |  | Misc. anchors, tow bridles, buoys, etc. |  | 17600
|  |  |  | Freight | 5% of cost |  | 1020 | 100% | 1020 | 0
O&M Mobilization BudgetProcurement ExpensesSafety Equipment & Supplies Total | O&M Mobilization Budget | Procurement Expenses | Safety Equipment & Supplies |  |  | Sub-Total | 21420 |  | 21420 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment Title | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Vehicles & Mobile Equipment
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Cars 4 WD w AC |  | $26M |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 1/2 ton Pickup Trucks | 1ea leased $2000 down & lease | 700/mnth | 6200 | 100% | 6200 | 0
|  |  |  | 2 1/2 ton flat bed truck w winch |  | $32M |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 6 ton Forklift (outside) |  | $38M |  | 100% | 0 | 0
|  |  |  | 3 ton Forklift (warehouse) | 1ea leased $1000 down & lease | 500/mnth | 3000 | 100% | 3000 | 0
|  |  |  | 12 passenger Van w/o AC |  | $24M |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 18 passenger Van w/o AC |  | $30M | 0 | 100% | 0 | 0
|  |  |  | Firefighting equipment | 1ea. extinguisher cart | $1M per | 1000 | 100% | 1000 | 0
|  |  |  | Backhoe/heavy equipment |  |  | 0 | 100% | 0 | 0
|  |  |  | Compressor water wash cart |  | $10M |  | 100% | 0 | 0
|  |  |  | 250 cfm Air Compressor (trailer mtd) |  | $16M |  | 100% | 0 | 0
|  |  |  | 400 amp welder(diesel drvr, trailer) |  | $11M |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | 8 ton Crane |  | $30M (used) |  | 100% | 0 | 0
|  |  |  | Crew Boats |  | $60M (used) | 0 | 100% | 0 | 0
|  |  |  | Switch engine |  | $300M | 0 | 100% | 0 | 0
|  |  |  | Maintenance cart |  |  | 2500 | 100% | 2500 | 0
|  |  |  | Freight | 5% of cost |  | 510 | 100% | 510
O&M Mobilization BudgetProcurement ExpensesVehicles & Mobile Equipment Total | O&M Mobilization Budget | Procurement Expenses | Vehicles & Mobile Equipment | Basis: Purchasing Dept. |  | Sub-Total | 13210 |  | 13210 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment Title | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Warehouse Furnishings & Equipment
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Bins/Racks/shelves | includes Lumber, nails, materials (to construct) |  | 9000 | 100% | 9000 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Equipment/Tools | dollies, scales, carpenter tools, banding & labeling machines |  | 1500 | 100% | 1500 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Furniture | tables, desks, chairs, file cabinets |  |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment | Miscellaneous Supplies |  |  | 1000 | 100% | 1000 | 0
|  |  |  | Freight | 5% of cost |  | 575 | 100% | 575 | 0
O&M Mobilization BudgetProcurement ExpensesWarehouse Furnishings & Equipment Total | O&M Mobilization Budget | Procurement Expenses | Warehouse Furnishings & Equipment |  |  | Sub-Total | 12075 |  | 12075 | 0
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment Title | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Laboratory Equipment
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment | Laboratory Analyzers (pH, conductivity, spectrophotometer) |  |  | 3000 | 100% | 3000 | 0
|  |  |  | Glassware/Misc. Equipment (centrifuge, vacuum pump, PC,scale,oven) |  |  | 2000 | 100% | 2000 | 0
|  |  |  | Furniture, cabinets, benches, tables, refrigerator |  |  | 1000 | 100% | 1000 | 0
|  |  |  | Fuel Testing equipment | Gas Chromatogragh/Atomic Absorption |  |  | 100% | 0 | 0
|  |  |  | Freight | 5% of cost |  | 300 | 100% | 300 | 0
O&M Mobilization BudgetProcurement ExpensesLaboratory Equipment Total | O&M Mobilization Budget | Procurement Expenses | Laboratory Equipment |  |  | Sub-Total | 6300 |  | 6300 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment Title | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Shop Tools & Equipment
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Mechanic Hand Tools | tool boxes | $1200 each | 2400 | 100% | 2400 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | I/E Tech Hand Tools | tool boxes | $1500 each | 3000 | 100% | 3000 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Consumables (Cleaning, Mech. supplies, compounds, I&E supplies, hoses) |  | 8000 | 8000 | 100% | 8000 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Radios (Basis: Houston 2-way Radio - Motorola HC1000, 2 channels) |  | $1000 each | 4000 | 100% | 4000 | 0
|  |  |  | Radio Base |  | $1000 each | 1000 | 100% | 1000 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment | Mechanical Shop Tools & Equip. | High Pressure Hand Pump | $1200 each |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Nordstrom Hyper Grease Gun 5 gal. | $3015 each |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Rockwell Hand Held High Pressure Grease Gun | $960 each | 960 | 100% | 960 | 0
[5 empty] | Hydraulic Torque Wrench | $4000 each |  | 100% | 0 | 0
[5 empty] | Centrifugal Pump | $2500 each | 2500 | 100% | 2500 | 0
[5 empty] | Pneumatic diaphram pump | $1000 each | 1000 | 100% | 1000 | 0
[5 empty] | Bead Blaster | $1800 each |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Sand Blaster | $900 each | 900 | 100% | 900 | 0
[5 empty] | Portable Air Compressor | $600 each | 600 | 100% | 600 | 0
[5 empty] | Hydraulic Press - 25 ton | $1400 each | 1400 | 100% | 1400 | 0
O&M Mobilization BudgetProcurement ExpensesShop Tools & Equipment Total | O&M Mobilization Budget | Procurement Expenses | Shop Tools & Equipment |  | Post Hole Digger | $1200 each |  | 100% | 0 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids Title | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Steel Work Bench | $160 each | 160 | 100% | 160 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Employee Lockers x 6 | $250 each | 3000 | 100% | 3000 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Storage Cabinets | $300 each | 600 | 100% | 600 | 0
[5 empty] | Parts Washer | $1000 each | 1000 | 100% | 1000 | 0
[5 empty] | Bench Grinder | $400 each | 400 | 100% | 400 | 0
O&M Mobilization BudgetProcurement ExpensesChemicals, Lubricants, Hydraulic Fluids Total | O&M Mobilization Budget | Procurement Expenses | Chemicals, Lubricants, Hydraulic Fluids |  | Drill Press | $2375 each | 2375 | 100% | 2375 | 0
O&M Mobilization BudgetO&M Mobilization Fee Title | O&M Mobilization Budget | O&M Mobilization Fee |  |  | AC/DC Welder Generator | $3100 each | 3100 | 100% | 3100 | 0
O&M Mobilization BudgetO&M Mobilization Fee | O&M Mobilization Budget | O&M Mobilization Fee |  |  | Assortment Hammer Wrenches | $5000 each |  | 100% | 0 | 0
[5 empty] | Flange Spreader | $250 each | 250 | 100% | 250 | 0
[5 empty] | Hoists /Come-a-longs | $1000 each | 1000 | 100% | 1000 | 0
[5 empty] | Miscellaneous small hand tools | $5000 set | 5000 | 100% | 5000 | 0
O&M Mobilization BudgetO&M Mobilization Fee Total | O&M Mobilization Budget | O&M Mobilization Fee |  | I/E Shop Tools & Test Equipment | Gas Detector Calibration Kit | $500 each | 500 | 100% | 500 | 0
O&M Mobilization BudgetOwner Optional Items Title | O&M Mobilization Budget | Owner Optional Items |  |  | Flow, Press, & Temp Transmitter Communicators | $5000 set | 5000 | 100% | 5000 | 0
O&M Mobilization BudgetOwner Optional Items | O&M Mobilization Budget | Owner Optional Items |  |  | Digital Thickness Gauge | $1800 each | 1800 | 100% | 1800 | 0
[5 empty] | UV IR Portable Test Kit | $4000 each |  | 100% | 0 | 0
[5 empty] | IRD Vibration Meter | $8000 each |  | 100% | 0 | 0
[5 empty] | Fluke Digital Multimeter | $350 each | 700 | 100% | 700 | 0
O&M Mobilization BudgetOwner Optional Items Total | O&M Mobilization Budget | Owner Optional Items |  |  | Thermocoupler Calibrator | $950 each | 950 | 100% | 950 | 0
[5 empty] | Precision Pressure Calibrator | $5700 each | 5700 | 100% | 5700 | 0
[5 empty] | Simpson Multimeter | $300 each |  | 100% | 0 | 0
[5 empty] | RTD Calibrator | $700 each | 700 | 100% | 700 | 0
[5 empty] | Test Gauges 0 -1500 psig. | $1000 set | 1000 | 100% | 1000 | 0
[5 empty] | Gravitometer | $5850 each |  | 100% | 0 | 0
[5 empty] | PK Tester | $4065 each | 4065 | 100% | 4065 | 0
[5 empty] | Pipeline Locator | $3900 each |  | 100% | 0 | 0
|  |  |  | Test/Troubleshooting Equipment | Beta Engine Analyzer | $60,000 each |  | 100% | 0 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) Title | O&M Mobilization Budget | Capital, Operating and BOP Spares (1996$) |  |  | Oscilloscope | $3000 each |  | 100% | 0 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) | O&M Mobilization Budget | Capital, Operating and BOP Spares (1998$) |  |  | Bore Scope (probe, light source and photo) | $15,000 each |  | 100% | 0 | 0
[5 empty] | Combustible Gas Detector | $1795 each | 1795 | 100% | 1795 | 0
|  |  |  | Freight | 5% |  | 3242.75 | 100% | 3242.75 | 0
O&M Mobilization BudgetCapital, Operating and BOP Spares (1998$) Total | O&M Mobilization Budget | Capital, Operating and BOP Spares (1998$)
[6 empty] | Sub-Total | 68097.75 |  | 68097.75 | 0
Chemicals, Lubricants, Hydraulic Fluids
|  |  |  | Warehouse Stock | 1month's worth x chemicals |  | 50359.9729 | 100% | 50359.9729 | 0
0
|  |  |  | Freight | 5% of cost (included above) |  |  |  | 0
[6 empty] | Sub-Total | 50359.9729 |  | 50359.9729 | 0
O&M Mobilization Fee
|  |  |  | Basis/Justification: | Dabhol (745 MW) $0.81/MW | $600M | 10% |  | 0 | 0.1
|  |  |  | 10% of mob. money managed excluding | East Java (500 MW) $1.10/MW | $550M |  |  | 0
|  |  |  | Spares, OE and G&A | Multan (800 MW) $1.22/MW | $975M |  |  | 0
[5 empty] | Tapal (Wartsila) (126MW) $2.85/MW (18 mo.) | $360M
[6 empty] | Sub-Total | 10% |  | 0 | 0.1
Operator Overhead Charge (G&A)
|  |  |  | Basis/Justification: | US, UK and like | 10% |  |  | 0 | 0
|  |  |  | Annual % of Payroll & Burden based | India, Brazil, Argentina and like | 15%
|  |  |  | on country type | Bangladesh and like | 20%
[6 empty] | Sub-Total | 0% |  | 0 | 0
Commercial Office Mobilization
[5 empty] | See Comm Office Mob detail sheet |  | #REF! | 100% | #REF! | #REF!
|  |  |  | Basis: Eval Team Consensus |  | Sub-Total | #REF! |  | #REF! | #REF!
Owners' Engineer
|  |  |  | EECC provides Turnkey Contract | See Owners' Engineer detail sheet |  | #REF! | 100% | #REF! | #REF!
|  |  |  | Basis: Jonathan Ago estimate |  | Sub-Total | #REF! |  | #REF! | #REF!
Capital, Operating and BOP Spares
|  |  |  | (See Capital/Operating Spares) | Required Initial Spares |  | 9537924 | 100% | 9537924 | 0 | 899329.28
|  |  |  | LM6000 recommended spares | $899,329 engine spares + $100,000 package spares |  | 0 | 100% | 0 | 0 | 100000
|  |  |  | Freight | 1% of cost |  | 95379.24 | 100% | 95379.24 | 0
|  |  |  | Insurance | 0.25% of cost |  | 23844.81 | 100% | 23844.81 | 0
[6 empty] | Sub-Total | 9657148.05 |  | 9657148.05 | 0

## O&M_Estimate
AES Corp, Dallas, TX (640 MW)
Commercial Operations O&M Estimate
US $
Annual
|  |  | Year 1 | Year 2 | Year 3 | Years 4+ | Avg. (20yrs)
Payroll & Burden |  |  | 1451918.666 | 1451918.666 | 1451918.666 | 1451918.666 | 1451918.666
Administration and Operations Expenses
| Employee Expenses |  | 22650 | 22650 | 22650 | 22650 | 22650
| Environmental Expense (including permit fees) |  | 38090.8333 | 38090.8333 | 38090.8333 | 38090.8333 | 38090.8333
| Safety Expense |  | 21917.6075 | 21917.6075 | 21917.6075 | 21917.6075 | 21917.6075
| Buildings & Grounds |  | 8000 | 8000 | 8000 | 8000 | 8000
| Other Supplies & Expenses |  | 84324.5455 | 84324.5455 | 84324.5455 | 84324.5455 | 84324.5455
| Communications |  | 15600 | 15600 | 15600 | 15600 | 15600
| Operating Insurance |  | 0 | 0 | 0 | 0 | 0
| Control Room/Laboratory Expenses |  | 158269.2986 | 158269.2986 | 158269.2986 | 158269.2986 | 158269.2986
| Operations Support (Year 1 Only) |  | 0 | 0 | 0 | 0 | 0
| Total Administration & Operations Expenses |  | 348852.285 | 348852.285 | 348852.285 | 348852.285 | 348852.285
Chemicals @ Plant Load Factor (PLF) |  |  | 604319.675 | 604319.675 | 604319.675 | 604319.675 | 604319.675
Maintenance Expenses (excl. GT ScheduIed Maint. Program)
| Painting |  | 6219.9255 | 20733.0851 | 20733.0851 | 62199.2554 | 55253.6719
| Electrical & Controls |  | 4444.4444 | 4444.4444 | 4444.4444 | 13333.3333 | 12000
| Water Treatment System |  | 41466.1703 | 41466.1703 | 41466.1703 | 124398.5108 | 111958.6597
| Cooling System |  | 53017.4605 | 53017.4605 | 53017.4605 | 159052.3816 | 143147.1435
| Substation/Interconnects |  | 18701.3703 | 18701.3703 | 18701.3703 | 56104.1109 | 50493.6999
| Gas Turbines (excluding scheduled maint.) |  | 165328.0716 | 165328.0716 | 165328.0716 | 495984.2149 | 446385.7934
| Boilers |  | 100569.6031 | 100569.6031 | 100569.6031 | 301708.8094 | 271537.9285
| Steam Turbine (including Scheduled Maint.) |  | 726697.6623 | 726697.6623 | 726697.6623 | 726697.6623 | 726697.6623
| Water Supply Pipeline and Booster Station |  | 0 | 0 | 0 | 0 | 0
| Fuel Facility |  | 0 | 0 | 0 | 0 | 0
| Miscellaneous Maintenance Expense |  | 123213.763 | 123213.763 | 123213.763 | 369641.2891 | 332677.1602
| Total Maintenance |  | 1239658.4712 | 1254171.6308 | 1254171.6308 | 2309119.5677 | 2150151.7192
Sustaining Capital Expenses |  |  | 26055.5223 | 26055.5223 | 26055.5223 | 26055.5223 | 26055.5223
Total O&M Expenses (excl. GT Scheduled Maint. Program) |  |  | 3670804.6195 | 3685317.7791 | 3685317.7791 | 4740265.716 | 4581297.8675
GT Scheduled Maintenance Program |  | 20 yr total | 141072289.1304 |  |  | Annual Avg. | 7053614.4565
[6 empty] | $/Mwh @PLF | 1.3244
Total Plant O&M Expenses (incl. GT Scheduled Maint.) | [5 empty] | Annual Avg. | 11634912.324
[6 empty] | $/Mwh @ PLF | 2.1845
Total Project Operating Expenses (excl Fee) | [5 empty] | Annual Avg. | 11634912.324
|  |  |  | $/Mwh @ PLF |  |  | 2.1845
OM&A Annual Fee |  |  | 1160000 | 1160000 | 1160000 | 1160000 | 1160000
Operator Overhead Charge (G&A) | [6 empty] | 0

## Plant_Staff (hidden)
AES Corp, Dallas, TX (640 MW)
Labor Sheet
Annual Labor Escalation Factor |  | 0%
Region Used for Labor Rates |  | US - Central
Drop Down Box
| Year 1 | No. of Expats | No. of Locals | Months on Site per Year (Expat) | Months on Site per Year (Local) | Total Employees per Year | Annual Base Salary per Employee | Annual Overtime % | Benefits % on Base | Benefits % on Overtime | Total Expat Salary | Total Local Salary | 3 | US - Central
[13 empty] | 1 | US - North-East
Administration Staff | [12 empty] | 2 | US - South-East
| Plant Manager | 0 | 1 | 0 | 12 | 1 | 87000 | 0% | 70.2% | 53.1% | 0 | 148074 | 3 | US - Central
| Assistant Plant Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0 | 4 | US - South
| Plant Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0 | 5 | US - North-West
| Administration Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0 | 6 | US - California
| Controller | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0 | 7 | India
| Accountant | 0 | 0 | 0 | 0 | 0 | 0 | 10% | 70.2% | 53.1% | 0 | 0 | 8 | 0
| Administrative Assistant | 0 | 1 | 0 | 12 | 1 | 27000 | 15% | 70.2% | 53.1% | 0 | 52154.55 | 9 | 0
| Warehouse Supervisor | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0 | 10 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0 | 11 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0 | 12 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0 | 13 | 0
[13 empty] | 14 | 0
Operations Staff | [12 empty] | 15
| Operations Manager | 0 | 1 | 0 | 12 | 1 | 70000 | 0% | 70.2% | 53.1% | 0 | 119140 | 16
| Operations Shift Supervisors | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0 | 17
| Control Room Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0 | 18
| Turbine Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0 | 19
| Water System Opertors | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0 | 20
| Fuel Storage/Handling Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Utility Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Chemist | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Tech III | 0 | 4 | 0 | 12 | 4 | 52000 | 15% | 70.2% | 53.1% | 0 | 401783.2
| Tech II | 0 | 4 | 0 | 12 | 4 | 45760 | 15% | 70.2% | 53.1% | 0 | 353569.216
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
Maintenance Staff
| Maintenance Manager | 0 | 1 | 0 | 12 | 1 | 65000 | 0% | 70.2% | 53.1% | 0 | 110630
| Mechanical Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Maintenance Planner | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Mechanic | 0 | 1 | 0 | 12 | 1 | 38000 | 15% | 70.2% | 53.1% | 0 | 73402.7
| I&C Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| I&C Technician | 0 | 1 | 0 | 12 | 1 | 55000 | 15% | 70.2% | 53.1% | 0 | 106240.75
| Electrical Technician | 0 | 1 | 0 | 12 | 1 | 45000 | 15% | 70.2% | 53.1% | 0 | 86924.25
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
Totals |  | 0 | 15 |  |  | 15 |  |  |  |  | 0 | 1451918.666
[8 empty] | Total Labor for Year 1 |  |  |  | 1451918.666
| Year 2 | No. of Expats | No. of Locals | Months on Site per Year (Expat) | Months on Site per Year (Local) | Total Employees per Year | Annual Base Salary per Employee | Annual Overtime % | Benefits % on Base | Benefits % on Overtime | Total Expat Salary | Total Local Salary
Administration Staff
| Plant Manager | 0 | 1 | 0 | 12 | 1 | 87000 | 0% | 70.2% | 53.1% | 0 | 148074
| Assistant Plant Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Plant Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Administration Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Controller | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Accountant | 0 | 0 | 0 | 0 | 0 | 0 | 10% | 70.2% | 53.1% | 0 | 0
| Administrative Assistant | 0 | 1 | 0 | 12 | 1 | 27000 | 15% | 70.2% | 53.1% | 0 | 52154.55
| Warehouse Supervisor | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
Operations Staff
| Operations Manager | 0 | 1 | 0 | 12 | 1 | 70000 | 0% | 70.2% | 53.1% | 0 | 119140
| Operations Shift Supervisors | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Control Room Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Turbine Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Water System Opertors | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Fuel Storage/Handling Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Utility Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Chemist | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Tech III | 0 | 4 | 0 | 12 | 4 | 52000 | 15% | 70.2% | 53.1% | 0 | 401783.2
| Tech II | 0 | 4 | 0 | 12 | 4 | 45760 | 15% | 70.2% | 53.1% | 0 | 353569.216
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
Maintenance Staff
| Maintenance Manager | 0 | 1 | 0 | 12 | 1 | 65000 | 0% | 70.2% | 53.1% | 0 | 110630
| Mechanical Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Maintenance Planner | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Mechanic | 0 | 1 | 0 | 12 | 1 | 38000 | 15% | 70.2% | 53.1% | 0 | 73402.7
| I&C Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| I&C Technician | 0 | 1 | 0 | 12 | 1 | 55000 | 15% | 70.2% | 53.1% | 0 | 106240.75
| Electrical Technician | 0 | 1 | 0 | 12 | 1 | 45000 | 15% | 70.2% | 53.1% | 0 | 86924.25
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
Totals |  | 0 | 15 |  |  | 15 |  |  |  |  | 0 | 1451918.666
[8 empty] | Total Labor for Year 2 |  |  |  | 1451918.666
| Year 3 | No. of Expats | No. of Locals | Months on Site per Year (Expat) | Months on Site per Year (Local) | Total Employees per Year | Annual Base Salary per Employee | Annual Overtime % | Benefits % on Base | Benefits % on Overtime | Total Expat Salary | Total Local Salary
Administration Staff
| Plant Manager | 0 | 1 | 0 | 12 | 1 | 87000 | 0% | 70.2% | 53.1% | 0 | 148074
| Assistant Plant Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Plant Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Administration Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Controller | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Accountant | 0 | 0 | 0 | 0 | 0 | 0 | 10% | 70.2% | 53.1% | 0 | 0
| Administrative Assistant | 0 | 1 | 0 | 12 | 1 | 27000 | 15% | 70.2% | 53.1% | 0 | 52154.55
| Warehouse Supervisor | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
Operations Staff
| Operations Manager | 0 | 1 | 0 | 12 | 1 | 70000 | 0% | 70.2% | 53.1% | 0 | 119140
| Operations Shift Supervisors | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Control Room Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Turbine Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Water System Opertors | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Fuel Storage/Handling Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Utility Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Chemist | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Tech III | 0 | 4 | 0 | 12 | 4 | 52000 | 15% | 70.2% | 53.1% | 0 | 401783.2
| Tech II | 0 | 4 | 0 | 12 | 4 | 45760 | 15% | 70.2% | 53.1% | 0 | 353569.216
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
Maintenance Staff
| Maintenance Manager | 0 | 1 | 0 | 12 | 1 | 65000 | 0% | 70.2% | 53.1% | 0 | 110630
| Mechanical Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Maintenance Planner | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Mechanic | 0 | 1 | 0 | 12 | 1 | 38000 | 15% | 70.2% | 53.1% | 0 | 73402.7
| I&C Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| I&C Technician | 0 | 1 | 0 | 12 | 1 | 55000 | 15% | 70.2% | 53.1% | 0 | 106240.75
| Electrical Technician | 0 | 1 | 0 | 12 | 1 | 45000 | 15% | 70.2% | 53.1% | 0 | 86924.25
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
Totals |  | 0 | 15 |  |  | 15 |  |  |  |  | 0 | 1451918.666
[8 empty] | Total Labor for Year 3 |  |  |  | 1451918.666
| Year 4 | No. of Expats | No. of Locals | Months on Site per Year (Expat) | Months on Site per Year (Local) | Total Employees per Year | Annual Base Salary per Employee | Annual Overtime % | Benefits % on Base | Benefits % on Overtime | Total Expat Salary | Total Local Salary
Administration Staff
| Plant Manager | 0 | 1 | 0 | 12 | 1 | 87000 | 0% | 70.2% | 53.1% | 0 | 148074
| Assistant Plant Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Plant Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Administration Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Controller | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Accountant | 0 | 0 | 0 | 0 | 0 | 0 | 10% | 70.2% | 53.1% | 0 | 0
| Administrative Assistant | 0 | 1 | 0 | 12 | 1 | 27000 | 15% | 70.2% | 53.1% | 0 | 52154.55
| Warehouse Supervisor | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
Operations Staff
| Operations Manager | 0 | 1 | 0 | 12 | 1 | 70000 | 0% | 70.2% | 53.1% | 0 | 119140
| Operations Shift Supervisors | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Control Room Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Turbine Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Water System Opertors | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Fuel Storage/Handling Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Utility Operators | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Chemist | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Tech III | 0 | 4 | 0 | 12 | 4 | 52000 | 15% | 70.2% | 53.1% | 0 | 401783.2
| Tech II | 0 | 4 | 0 | 12 | 4 | 45760 | 15% | 70.2% | 53.1% | 0 | 353569.216
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
Maintenance Staff
| Maintenance Manager | 0 | 1 | 0 | 12 | 1 | 65000 | 0% | 70.2% | 53.1% | 0 | 110630
| Mechanical Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 70.2% | 53.1% | 0 | 0
| Maintenance Planner | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Mechanic | 0 | 1 | 0 | 12 | 1 | 38000 | 15% | 70.2% | 53.1% | 0 | 73402.7
| I&C Engineer | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| I&C Technician | 0 | 1 | 0 | 12 | 1 | 55000 | 15% | 70.2% | 53.1% | 0 | 106240.75
| Electrical Technician | 0 | 1 | 0 | 12 | 1 | 45000 | 15% | 70.2% | 53.1% | 0 | 86924.25
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 15% | 70.2% | 53.1% | 0 | 0
Totals |  | 0 | 15 |  |  | 15 |  |  |  |  | 0 | 1451918.666
[8 empty] | Total Labor for Year 4 |  |  |  | 1451918.666

## Labor_ Lookup (hidden)
Labor / Benefits Lookup Sheet
Regional Salaries in U.S. Dollars
1 |  |  | US - North-East | US - South-East | US - Central | US - South | US - North-West | US - California | India
2 | Annual Base Salary (USD)
3
4 | Administration Staff
5 |  | Plant Manager | 87000 | 87000 | 87000 | 87000 | 87000 | 87000
6 |  | Assistant Plant Manager | 75000 | 75000 | 75000 | 75000 | 75000 | 75000
7 |  | Plant Engineer | 65000 | 65000 | 65000 | 65000 | 65000 | 65000
8 |  | Administration Manager | 60000 | 60000 | 60000 | 60000 | 60000 | 60000
9 |  | Controller | 45000 | 45000 | 45000 | 45000 | 45000 | 45000
10 |  | Accountant | 40000 | 40000 | 40000 | 40000 | 40000 | 40000
11 |  | Administrative Assistant | 27000 | 27000 | 27000 | 27000 | 27000 | 27000
12 |  | Warehouse Supervisor | 30000 | 30000 | 30000 | 30000 | 30000 | 30000
13 |  | Other
14 |  | Other
15 |  | Other
16
17 | Operations Staff
18 |  | Operations Manager | 70000 | 70000 | 70000 | 70000 | 70000 | 70000
19 |  | Operations Shift Supervisors | 60000 | 60000 | 60000 | 60000 | 60000 | 60000
20 |  | Control Room Operators | 55000 | 55000 | 55000 | 55000 | 55000 | 55000
21 |  | Turbine Operators | 45000 | 45000 | 45000 | 45000 | 45000 | 45000
22 |  | Water System Opertors | 35000 | 35000 | 35000 | 35000 | 35000 | 35000
23 |  | Fuel Storage/Handling Operators | 30000 | 30000 | 30000 | 30000 | 30000 | 30000
24 |  | Utility Operators | 33000 | 33000 | 33000 | 33000 | 33000 | 33000
25 |  | Chemist | 40000 | 40000 | 40000 | 40000 | 40000 | 40000
26 |  | Tech III | 52000 | 52000 | 52000 | 52000 | 52000 | 52000
27 |  | Tech II | 45760 | 45760 | 45760 | 45760 | 45760 | 45760
28 |  | Other
29
30 | Maintenance Staff
31 |  | Maintenance Manager | 65000 | 65000 | 65000 | 65000 | 65000 | 65000
32 |  | Mechanical Engineer | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
33 |  | Maintenance Planner | 40000 | 40000 | 40000 | 40000 | 40000 | 40000
34 |  | Mechanic | 38000 | 38000 | 38000 | 38000 | 38000 | 38000
35 |  | I&C Engineer | 60000 | 60000 | 60000 | 60000 | 60000 | 60000
36 |  | I&C Technician | 55000 | 55000 | 55000 | 55000 | 55000 | 55000
37 |  | Electrical Technician | 45000 | 45000 | 45000 | 45000 | 45000 | 45000
38 |  | Other
39 |  | Other
40 |  | Other
41 |  | Other
42
43
44 | Benefits
45
46 |  | Annual Base Wage to calculate benefits | 57857.1429 | 57857.1429 | 57857.1429 | 57857.1429 | 57857.1429 | 57857.1429
87 |  | Standard Enron Benefits on Base (%)
|  | Payroll Tax Burdens | 14.34% | 14.34% | 14.34% | 14.34% | 14.34% | 14.34%
|  | Workers Compensation Ins. | 7.78% | 7.78% | 7.78% | 7.78% | 7.78% | 7.78%
|  | Overhead Allocation | 25% | 25% | 25% | 25% | 25% | 25%
|  | Group Insurance Premium | 9.126% | 9.126% | 9.126% | 9.126% | 9.126% | 9.126%
|  | General Liability | 1% | 1% | 1% | 1% | 1% | 1%
|  | Pension | 5% | 5% | 5% | 5% | 5% | 5%
|  | ESOP | 5% | 5% | 5% | 5% | 5% | 5%
|  | 401K | 3% | 3% | 3% | 3% | 3% | 3%
|  | Total Enron Benefits on Base (%) | 70.25% | 70.25% | 70.25% | 70.25% | 70.25% | 70.25%
|  | Standard Enron Benefits on Overtime (%) | 53.12% | 53.12% | 53.12% | 53.12% | 53.12% | 53.12%
64 |  | Country Mandated Benefits
65 |  | Health Insurance (%)
66 |  | Social Security Provident Fund (%)
67 |  | Super Annuization (%)
68 |  | Mandatory Medical
69 |  | Bonus (%)
70 |  | Terminal Benefit for Years of Service (In Months)
71 |  | Vacation/Leave
72 |  | Housing
73 |  | Wedding, Sick Leave, Seniority
74 |  | Mandatory Profit Sharing
75 |  | Training Funding
Other Benefits
Other Benefits
Other Benefits
Other Benefits
76 |  | Other Benefits
77
78
79 |  | Taxes, Exemptions, Deductions
80 |  | Host Country (National + Local) Tax Rate (%)
81 |  | Host Country Standard Deduction
82 |  | Retained Employee Tax Payment
83 |  | Retained Employee Housing Payment
84 |  | USA Exemptions (Dependents, Housing, Deductions)
85 |  | Federal Tax Rate (USA)
86 |  | State Tax Rate (USA)
88 |  | Max Overtime Rate
89 |  | Max Hours in a Shift (8 or 12)
Expatriate Benefits
47 |  | Uplift & Danger Pay (%)
48 |  | Goods & Services Uplift
49 |  | Lodging (House rent / Hotel)
50 |  | Home Leave
51 |  | Dependent Schools
52 |  | Transportation for Employees
53 |  | Utility
54 |  | Food
55 |  | Laundry/Cleaning Service
56 |  | Travel from Base to Site (Roundtrip)
57 |  | Other Benefits
58 |  | Other Benefits
59 |  | Other Benefits
60 |  | Other Benefits
61 |  | Other Benefits
62 |  | Other Benefits
63 |  | Other Benefits
Other Benefits
90
91
92 | Expatriate Benefits
93
94 |  |  | Family (Spouse + two) |  | Family (Spouse + two) |  | Family (Spouse + two)
95 |  |  | Operations Manager |  | Plant Manager |  | Plant Manager
96 |  |  | from Phillipines |  | from USA |  | from UK
97
98 |  | Bonus | 5% of Base |  | 5% of Base |  | 8% of Base
|  | Foreign Service Premium | 15% of Base |  | 45% of Base |  | 40% of Base
|  | Tax Protection/Equalization | 188 % of Base |  | 185 % of Base |  | 55 % of Base
|  | C&S Allowance | 20600 |  | 2200 |  | 0
|  | Housing & Utilities2 | 59000 |  | 60000 |  | 79833
|  | Educational Assistance | 15000 |  | 15000 |  | 11150
|  | Home Leave | 4500 |  |  |  | 21200
|  | R&R Leave |  |  | $3,900 x 4 = $15,600 |  | 0
|  | Relocation Expenses1 | 11000 |  | 22000 |  | 17900
|  | Foreign Duty Allowance | 1000 |  | 1000 |  | 250
|  | Total | 191% of Base + $34,018 |  | 235% of Base + $115,800 |  | 103% of Base + $130,333
|  | Benefits Loading Factor (of Base) | 344.7% |  | 379.1% |  | 256.4% | Without Housing Colony
[7 empty] | 225.1% | With Housing Colony
|  | Source: Enron HR | these in red need to be replaced. Awaiting update from HR
Notes:
1/ Relocation expenses is an annual average over a 3 yr period.
2/ Housing and Utilities assumed to be paid for the plant manager, but required for the commercial manager, if an Expat.

## O&M Backup_Detail (hidden)
AES Corp, Dallas, TX (640 MW)
O&M Estimate Backup/Detail Sheet
| Plant Configuration Lookup | GE 7FA | None | None
Line Item |  | Total (US $) | % Variable | % Local | Detail/Basis | Fixed (USD) | Variable (USD) | Local | Foreign |  | 3 | GE 7FA |  | 6 | None | 6 | None
Payroll & Burden | [5 empty] | 100% | 0% | 100% | 0% |  | 1 | GE LM6000 |  | 1 | GE LM6000 | 1 | GE LM6000
| Expats: Salaries & Benefits | 0 | 0% | 0% | Year 1 | 0 | 0 | 0 | 0 |  | 2 | GE 7EA |  | 2 | GE 7EA | 2 | GE 7EA
| Local: Salaries & Benefits | 1451.9187 | 0% | 100% | Year 1 | 1451.9187 | 0 | 1451.9187 | 0 |  | 3 | GE 7FA |  | 3 | GE 7FA | 3 | GE 7FA
[6 empty] | 0 | 0 | 0 | 0 |  | 4 | W501D5 |  | 4 | W501D5 | 4 | W501D5
| Sub-Total | 1451.9187 |  |  | Basis: HR data | 1451.9187 | 0 | 1451.9187 | 0 |  | 5 | W501D5A |  | 5 | W501D5A | 5 | W501D5A
Employee Expenses | [5 empty] | 100% | 0% | 100% | 0% |  | 6 | None |  | 6 | None | 6 | None
| Travel Expenses/Overtime Meals | 4500 | 0% | 100% | scaled by Subic: $33,000 x 51people/110people | 4500 | 0 | 4500 | 0 |  | 7 | GE 6B |  | 7 | GE 6B | 7 | GE 6B
| Conferences/Training | 5727.2727 | 0% | 100% | scaled by Subic: $42,000 x 51people/110people | 5727.2727 | 0 | 5727.2727 | 0 |  | 8 | BOILERS |  | 8 | BOILERS | 8 | BOILERS
| Employees Expense | 3409.0909 | 0% | 100% | scaled by Subic: $25,000 x 51people/110people | 3409.0909 | 0 | 3409.0909 | 0 |  | 9 | 0 |  | 9 | 0 | 9 | 0
| Interviews/Relocations | 3750 | 0% | 100% |  | 3750 | 0 | 3750 | 0 |  | 10 | 0 |  | 10 | 0 | 10 | 0
| Professional Dues | 4500 | 0% | 100% | same as Subic | 4500 | 0 | 4500 | 0 |  | 11 | 0 |  | 11 | 0 | 11 | 0
| Entertainment Expense | 763.6364 | 0% | 100% | scaled by Subic: $5,600 x 51people/110peoplex | 763.6364 | 0 | 763.6364 | 0 |  | 12 | 0 |  | 12 | 0 | 12 | 0
| Daily Meal Allowance | 0 | 0% | 100% | $2/day/employee x 235 days x # staff | 0 | 0 | 0 | 0 |  | 13 | 0 |  | 13 | 0 | 13 | 0
| Other | 0 | 0% |  |  | 0 | 0 |  |  |  | 14 | 0 |  | 14 | 0 | 14 | 0
| Sub-Total | 22650 |  |  | Basis: Subic 1996 Budget | 22650 | 0 | 22650 | 0 |  | 15 | 0 |  | 15 | 0 | 15 | 0
Permanent Contract Labor | [5 empty] | 0% | 100% | 0% | 100%
| Contract Labor | 0 | 0% | 100% | see Contract Labor page | 0 | 0 | 0 | 0
| Other | 0 | 0% |  |  | 0 | 0 |  |  |  | 3 | 3 |  | 1 | 1 | 1 | 1
| Sub-Total | 0 |  |  | Basis: | 0 | 0 | 0 | 0 |  | 2 | combined |  | 0 |  | 0
Environmental Expense (including permit fees) | [5 empty] | 100% | 0% | 100% | 0% |  | 0 |  |  | 0 |  | 0
| Training/Awards | 3315 | 0% | 100% | Scaled on Ilijan (500/1200) x $11,700 | 3315 | 0 | 3315 | 0 |  | 1 | simple |  | 1 | simple | 1 | simple
| Permits | 10908.3333 | 0% | 100% | Scaled on Ilijan (500/1200) x $38,500 | 10908.3333 | 0 | 10908.3333 | 0 |  | 2 | combined |  | 2 | combined | 2 | combined
| Materials & Supplies | 3867.5 | 0% | 100% | Scaled on Ilijan (500/1200) x $13,650 | 3867.5 | 0 | 3867.5 | 0 |  | 3 | simple/Cogen |  | 3 | simple/Cogen | 3 | simple/Cogen
| Technical/Professional Services | 0 | 0% | 100% | 1 trip x $3M/trip + 7 days perdiem x $25/day (guesthouse) | 0 | 0 | 0 | 0 |  | 4 |  |  | 4 |  | 4
| Other Outside Services (RATA) | 20000 | 0% | 100% | 80 manhrs x $75/hr (audit) | 20000 | 0 | 20000 | 0 |  | 5 |  |  | 5 |  | 5
| Non-Hazardous Waste Handling | 0 | 0% | 100% | Stack Testing/Modeling - Scaled on Ilijan $14,000 x 500/1200 | 0 | 0 | 0 | 0 |  | 6 |  |  | 6 |  | 6
| Other | 0 | 0% | 100% |  | 0 | 0 | 0 | 0 |  | 7 |  |  | 7 |  | 7
| Other | 0 | 0% | 100% |  | 0 | 0 | 0 | 0 |  | 8 |  |  | 8 |  | 8
| Sub-Total | 38090.8333 |  |  | Basis: Memo from Bal Wong dtd 7/29/96 | 38090.8333 | 0 | 38090.8333 | 0 |  | 9 |  |  | 9 |  | 9
Safety Expense | [5 empty] | 100% | 0% | 100% | 0% |  | 10 |  |  | 10 |  | 10
| Training/Awards | 4238.7097 | 0% | 100% | 17,520x51/62 (50% scaled from Ilijan personnel) | 4238.7097 | 0 | 4238.7097 | 0 |  | 11 |  |  | 11 |  | 11
| Permits | 10908.3333 | 0% | 100% | 38,500x500/1200 (scaled from Ilijan) | 10908.3333 | 0 | 10908.3333 | 0 |  | 12 |  |  | 12 |  | 12
| Company Membership & Dues | 0 | 0% | 100% |  | 0 | 0 | 0 | 0 |  | 13 |  |  | 13 |  | 13
| Routine Safety Supplies | 6770.5645 | 0% | 100% | 27,985x51/62 (scaled from Ilijan personnel) | 6770.5645 | 0 | 6770.5645 | 0 |  | 14 |  |  | 14 |  | 14
| Technical/Professional Services | 0 | 0% | 100% | 1 trip x $3M/trip + 7 days perdiem x $25/day (guesthouse) | 0 | 0 | 0 | 0 |  | 15 |  |  | 15 |  | 15
| Safety Equipment Rentals | 0 | 0% | 100% | 80 manhrs x $75/hr (audit) | 0 | 0 | 0 | 0
| Sub-Total | 21917.6075 |  |  | Basis: Memo from Bal Wong dtd 7/29/96 | 21917.6075 | 0 | 21917.6075 | 0
Buildings & Grounds | [5 empty] | 100% | 0% | 75% | 25% |  | Gas Turbines |  | Quantity |  | Cycle
| Security training and facilities | 0 | 0% | 100% | 80 manhrs x $100/hr Crisis response training (audit) | 0 | 0 | 0 | 0
| Building repairs & painting | 6000 | 0% | 100% | $22,900 x 75% | 6000 | 0 | 6000 | 0 | #1
| Road repairs | 0 | 0% | 100% | (Same as ClearLk/TxCity Avg Actuals x 75% labor factor) | 0 | 0 | 0 | 0
| Technical/Professional Services | 0 | 0% | 100% | 1 trip x $6M/trip + 7 days perdiems x $25/day (guest house) | 0 | 0 | 0 | 0 | #2
| Outside services Contract labor | 0 | 0% | 100% | same as Subic | 0 | 0
| Equipment Rentals | 2000 | 0% | 100% |  | 2000 | 0 |  |  | #3
| Other Rents | 0 | 0% | 100% |  | 0 | 0
| Supplies | 0 | 0% | 100% |  | 0 | 0
| Other | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 8000 |  |  | Basis: Subic 1996 Budget | 8000 | 0 | 6000 | 0
Other Supplies & Expenses | [5 empty] | 100% | 0% | 100% | 0%
| Office Supplies & Expenses | 4090.9091 | 0% | 100% | Scaled from Subic personnel: $30,000 x 51/110 | 4090.9091 | 0 | 4090.9091 | 0
| Materials & Supplies | 2045.4545 | 0% | 100% | Scaled from Subic personnel: $15,000 x 51/110 | 2045.4545 | 0 | 2045.4545 | 0
| Outside Services Contract Labor | 818.1818 | 0% | 100% | Scaled from Subic personnel: $6,000 x 51/110 | 818.1818 | 0 | 818.1818 | 0
| Technical/Professional Services | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Legal | 10000 | 0% | 100% | 80 manhrs x $125/hr | 10000 | 0 | 10000 | 0
| Accounting | 2400 | 0% | 100% | 160 manhrs x $75/hr + 1 trip x $6M/trip + 14 days perdiem x $25/day | 2400 | 0 | 2400 | 0
| Office Equipment Maint. | 2000 | 0% | 100% |  | 2000 | 0 | 2000 | 0
| Tax | 6000 | 0% | 100% | 80 manhrs x $75/hr | 6000 | 0 | 6000 | 0
| Regional Technical Support | 12000 | 0% | 100% | 80 manhrs x $75/hr + 2 trips x $3M/trip + 14 days perdiem x $25/day | 12000 | 0 | 12000 | 0
| Customs | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Regulatory | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Other Outside Services | 2000 | 0% | 100% |  | 2000 | 0 | 2000 | 0
| Office Equipment Rental | 2400 | 0% | 100% | Garbage & Trash | 2400 | 0 | 2400 | 0
| Other Rents | 0 | 0% | 100% | $200/month | 0 | 0 | 0 | 0
| Radio parts/repair | 1000 | 0% | 100% |  | 1000 | 0 | 1000 | 0
| PC Hardware (purchase) | 3000 | 0% | 100% | 50% of Subic | 3000 | 0 | 3000 | 0
| PC Software | 2000 | 0% | 100% | Same as Subic for items < $1000, otherwise in Sus. Capital | 2000 | 0 | 2000 | 0
| PC Hardware Rental/Lease | 0 | 0% | 100% | 4 licenses x $500 ea. | 0 | 0 | 0 | 0
| PC Maintenance | 1000 | 0% | 100% |  | 1000 | 0 | 1000 | 0
| Postage & Freight Expenses | 3600 | 0% | 100% | 33% Subic | 3600 | 0 | 3600 | 0
| Utilities (office water, power, gas) | 12000 | 0% | 100% | same as Subic | 12000 | 0 | 12000 | 0
| Public relations/Contributions | 1000 | 0% | 100% | Assumed in Plant's House Load | 1000 | 0 | 1000 | 0
| Boat maintenance/repair | 0 | 0% | 100% | (covered in Commercial office) | 0 | 0 | 0 | 0
| Vehicle maintenance/repair | 2000 | 0% | 100% |  | 2000 | 0 | 2000 | 0
| Vehicle fuel | 14970 | 0% | 100% | $500/vehicle/year | 14970 | 0 | 14970 | 0
| Boat fuel | 0 | 0% | 100% | see detail below | 0 | 0 | 0 | 0
| Other | 0 | 0% | 100% | see detail below | 0 | 0 | 0
| Sub-Total | 84324.5455 |  |  | Basis: Subic 1996 Budget & Rino Manzano ccMail dtd 8/8/96 | 84324.5455 | 0 | 84324.5455 | 0
Communications | [5 empty] | 100% | 0% | 100% | 0%
| Phone service | 12000 | 0% | 100% | 12x$4M/month | 12000 | 0 | 12000 | 0
| Cellular phone service | 3600 | 0% | 100% | 5 phones x $300/month | 3600 | 0 | 3600 | 0
| VSAT | 0 | 0% |  | none assumed for this project | 0 | 0
| Sub-Total | 15600 |  |  | Basis: Hainan Plant actuals (Overseas experience) | 15600 | 0 | 15600 | 0
Operating Insurance | [5 empty] | 0% | 100% | 0% | 100%
| Operating Insurance | 0 | 0% | 0% | Estimated by Risk Management | 0 | 0 | 0 | 0
| Other | 0 | 0% | 0% | It will add incrementally to the Enron Pool of insured assets | 0 | 0
| Sub-Total | 0 |  |  | Basis: | 0 | 0 | 0 | 0
Control Room/Laboratory Expenses | [5 empty] | 100% | 0% | 100% | 0%
| Technical/Professional Services | 122299.0035 | 0% | 100% | 75% of US CCPP costs | 122299.0035 | 0 | 122299.0035 | 0
| Reagents & Supplies | 35970.2951 | 0% | 100% |  | 35970.2951 | 0 | 35970.2951 | 0
| Rental Equipment | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Analyzer Repairs | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Contract Labor/Temporaries | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Other Outside Services | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Freight | 0 | 0% | 100% | 5% of 75% of total | 0 | 0 | 0 | 0
| Other | 0 | 0% | 100% |  | 0 | 0 |  | 0
| Sub-Total | 158269.2986 |  |  | Basis: 13 years of Actuals from Tx City/Clear Lake Plants | 158269.2986 | 0 | 158269.2986 | 0
Operations Support (Year 1 Only) | [5 empty] | 0% | 100% | 0% | 100%
| Operations Support Personnel | 0 | 0% | 100% | 2ea.x$350/dayx180days (includes benefits) | 0 | 0 | 0 | 0
| Per diem | 0 | 0% | 100% | 2ea.x$25/dayx180days (stay in Guest House) | 0 | 0 | 0 | 0
| Home leave, travel | 0 | 0% | 100% | 2ea.x$3000 trip x 2trips (coach class) | 0 | 0 | 0 | 0
| Tax Protection (over 6 months) | 0 | 0% | 100% | 66% of wages | 0 | 0 | 0 | 0
| Other | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 0 |  |  | 2 US Expats for 6 months to aid in Initial Operating Period | 0 | 0 | 0 | 0
Chemicals (including Water treatment & Lubricity Agent) | [5 empty] | 0% | 100% | 100% | 0%
| Technical/Professional Services | 0 | 100% | 100% | 1 trip x $3M | 0 | 0 | 0 | 0
| Pretreatment chemicals | 0 | 100% | 100% | Chlorine/Clarifier/filter | 0 | 0 | 0 | 0
| Demin Acid/Caustic | 0 | 100% | 100% |  | 0 | 0 | 0 | 0
| Resin Replacement | 0 | 100% | 100% | Boiler/Steam Cycle Treatment | 0 | 0 | 0 | 0
| CT Chemicals | 86446.2753 | 100% | 100% |  | 0 | 86446.2753 | 86446.2753 | 0
| Boiler Chemicals | 96819.8283 | 100% | 100% |  | 0 | 96819.8283 | 96819.8283 | 0
| SCR Ammonia | 421053.5714 | 100% | 100% |  | 0 | 421053.5714 | 421053.5714 | 0
| Potable Water Chemicals | 0 | 100% | 100% |  | 0 | 0 | 0 | 0
| Hydrogen (generators) | 0 | 100% | 100% | Assume air cooled | 0 | 0 | 0 | 0
| Waste Water Treatment | 0 | 100% | 100% |  | 0 | 0 | 0 | 0
| Lubricity Agent | 0 | 100% | 100% | n/a with PCFD installed on GTs (GTs will have PCFD per Dev. Eng.) | 0 | 0 | 0 | 0
| Taxes/freight | 0 | 100% | 100% | 10% of total | 0 | 0 | 0 | 0
| Other | 0 | 100% | 100% |  | 0 | 0 | 0 | 0
| Sub-Total | 604319.675 |  |  | Basis: Water model estimate using Hyundai Water Balance @ 80% PLF | 0 | 604319.675 | 604319.675 | 0
Painting | [5 empty] | 100% | 0% | 100% | 0%
| Paint & Materials | 31099.6277 | 0% | 100% | Scaled on MW | 31099.6277 | 0 | 31099.6277 | 0
| Technical/Professional Services | 12439.8511 | 0% | 100% | $70,000 x (500MW/414MW)^0.6*.75 | 12439.8511 | 0 | 12439.8511
| Outside Contract Services | 12439.8511 | 0% | 100% | 75% factor for lower local labor | 12439.8511 | 0 | 12439.8511
| Equipment rental | 6219.9255 | 0% | 100% |  | 6219.9255 | 0 | 6219.9255
| Miscellaneous | 0 | 0% | 100% |  | 0 | 0 | 0
| Other | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 62199.2554 |  |  | Basis: 13 years of Actuals from Tx City/Clear Lake Plants | 62199.2554 | 0 | 62199.2554 | 0
Electrical & Controls | [5 empty] | 100% | 0% | 100% | 0%
| Repair Parts | 6666.6667 | 0% | 100% | Scaled on MW and # Generators | 6666.6667 | 0 | 6666.6667 | 0
| Outside Repair Services | 2666.6667 | 0% | 100% | $30,000 x (4gens/4.5gens) x (500MW/414MW)^0.6 x 75% | 2666.6667 | 0 | 2666.6667 | 0
| Technical/Professional Services | 1333.3333 | 0% | 100% | 75% factor for lower local labor | 1333.3333 | 0 | 1333.3333 | 0
| Outside Contract Services | 2000 | 0% | 100% |  | 2000 | 0 | 2000 | 0
| Equipment rental | 666.6667 | 0% | 100% |  | 666.6667 | 0 | 666.6667 | 0
| Freight | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Other | 0 | 0% | 100% | 5% of 75% of total | 0 | 0 | 0 | 0
| Other | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 13333.3333 |  |  | Basis: 13 years of Actuals from Tx City/Clear Lake Plants | 13333.3333 | 0 | 13333.3333 | 0
Water Treatment System | [5 empty] | 100% | 0% | 100% | 0%
| Repair Parts | 62199.2554 | 0% | 100% | Scaled on Steam Turbine MW | 62199.2554 | 0 | 62199.2554 | 0
| Outside Repair Services | 24879.7022 | 0% | 100% | $140,000 x (1ST/1ST) x (178MW/140MW)^0.6 x 75% | 24879.7022 | 0 | 24879.7022 | 0
| Technical/Professional Services | 12439.8511 | 0% | 100% | 75% factor for lower local labor | 12439.8511 | 0 | 12439.8511 | 0
| Outside Contract Labor | 18659.7766 | 0% | 100% |  | 18659.7766 | 0 | 18659.7766 | 0
| Equipment rental | 6219.9255 | 0% | 100% |  | 6219.9255 | 0 | 6219.9255 | 0
| Miscellaneous | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Freight | 0 | 0% | 100% | 5% of 75% of total | 0 | 0 | 0 | 0
| Sub-Total | 124398.5108 |  |  | Basis: 7 years of Actuals from Tx City Plant | 124398.5108 | 0 | 124398.5108 | 0
Cooling System | [5 empty] | 100% | 0% | 100% | 0%
| Repair Parts | 79526.1908 | 0% | 100% | Scaled on MW | 79526.1908 | 0 | 79526.1908 | 0
| Outside Repair Services | 31810.4763 | 0% | 100% | scaled: $179,000 x (500MW/414MW)^0.6*75%labor | 31810.4763 | 0 | 31810.4763 | 0
| Technical/Professional Services | 15905.2382 | 0% | 100% | 75% factor for lower local labor | 15905.2382 | 0 | 15905.2382 | 0
| Outside Contract Labor | 23857.8572 | 0% | 100% |  | 23857.8572 | 0 | 23857.8572 | 0
| Equipment rental | 7952.6191 | 0% | 100% |  | 7952.6191 | 0 | 7952.6191 | 0
| Miscellaneous (chillers) | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Freight | 0 | 0% | 100% | 5% of 75% of total | 0 | 0 | 0 | 0
| Other | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 159052.3816 |  |  | Basis: 13 years of Actuals from Tx City/Clear Lake Plants | 159052.3816 | 0 | 159052.3816 | 0
Substation/Interconnects | [5 empty] | 100% | 0% | 100% | 0%
| Repair Parts | 28052.0555 | 0% | 100% | Scaled on genrator MW and # generators | 28052.0555 | 0 | 28052.0555 | 0
| Electric Meter Calibration & Testing | 11220.8222 | 0% | 100% | Scaled cost = Labor Cost + Materials Cost | 11220.8222 | 0 | 11220.8222 | 0
| Outside Repair Services | 5610.4111 | 0% | 100% | Labor cost (50% of total) = 50% x $94,000 x 50% | 5610.4111 | 0 | 5610.4111 | 0
| Technical/Professional Services | 2805.2055 | 0% | 100% | Material Cost (50% of total) = 50% x $94,000 x (4gens/4.5gens) | 2805.2055 | 0 | 2805.2055 | 0
| Outside Contract Labor | 5610.4111 | 0% | 100% | x (112MW/104MW)^0.6 | 5610.4111 | 0 | 5610.4111 | 0
| Equipment rental | 2805.2055 | 0% | 100% |  | 2805.2055 | 0 | 2805.2055 | 0
| Miscellaneous | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Freight | 0 | 0% | 100% | 5% of 11% of total | 0 | 0 | 0 | 0
| Other | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 56104.1109 |  |  | Basis: 12 years of Actuals from Tx City/Clear Lake Plants | 56104.1109 | 0 | 56104.1109 | 0
Gas Turbines (excluding scheduled maint.) | [5 empty] | 0.0369% | 99.96% | 100% | 0%
| Repair Parts | 247992.1074 | 90% | 100% | Scaled on # turbines and turbine MW | 24799.2107 | 223192.8967 | 247992.1074 | 0
| Outside Repair Services | 99196.843 | 90% | 100% | $554,000 x (3 GTs/3 GTs) x (112MW/104MW)^0.6 x 75% labor factor | 9919.6843 | 89277.1587 | 99196.843 | 0
| Technical/Professional Services | 49598.4215 | 90% | 100% | 75% factor for lower local labor | 4959.8421 | 44638.5793 | 49598.4215 | 0
| Outside Contract Labor | 74397.6322 | 90% | 100% |  | 7439.7632 | 66957.869 | 74397.6322 | 0
| Equipment rental | 24799.2107 | 90% | 100% |  | 2479.9211 | 22319.2897 | 24799.2107 | 0
| Miscellaneous | 0 | 90% | 100% |  | 0 | 0 | 0 | 0
| Freight | 0 | 90% | 100% | 5% of 75% of total | 0 | 0 | 0 | 0
| Other | 0 | 90% | 100% |  | 0 | 0
| Sub-Total | 495984.2149 |  |  | Basis: 13 years of Actuals from Tx City/Clear Lake Plants | 49598.4215 | 446385.7934 | 495984.2149 | 0
Boilers | [5 empty] | 60% | 40% | 100% | 0%
| Repair Parts | 150854.4047 | 40% | 100% | Scaled on Gas Turbine MW. | 90512.6428 | 60341.7619 | 150854.4047 | 0
| Outside Repair Services | 60341.7619 | 40% | 100% | $337,000 x (3GTs/3GTs) x (112MW/104MW)^0.6 x 75% x 75% | 36205.0571 | 24136.7048 | 60341.7619 | 0
| Technical/Professional Services | 30170.8809 | 40% | 100% | 75% factor due to Tx City/Clear Lk were cogen plants & suppl. fired | 18102.5286 | 12068.3524 | 30170.8809 | 0
| Outside Contract Labor | 45256.3214 | 40% | 100% | 75% factor for lower local labor | 27153.7928 | 18102.5286 | 45256.3214 | 0
| Equipment rental | 15085.4405 | 40% | 100% | Triple pressure boilers | 9051.2643 | 6034.1762 | 15085.4405 | 0
| Miscellaneous | 0 | 40% | 100% |  | 0 | 0 | 0 | 0
| Freight | 0 | 40% | 100% | 5% of 75% of total | 0 | 0 | 0 | 0
| Other | 0 | 40% | 100% | Assume non-local manufacturer | 0 | 0
| Sub-Total | 301708.8094 |  |  | Basis: 13 years of Actuals from Tx City/Clear Lake Plants | 181025.2856 | 120683.5238 | 301708.8094 | 0
Steam Turbine (including Scheduled Maint.) | [5 empty] | 60% | 40% | 100% | 0%
| Non-scheduled maint. parts/repairs | 363348.8311 | 40% | 100% | Scaled on Steam Turbine MW | 218009.2987 | 145339.5325 | 363348.8311 | 0
| Outside Repair Services | 145339.5325 | 40% | 100% | $460,000x(178MW/140MW)^.6x75% labor factor | 87203.7195 | 58135.813 | 145339.5325 | 0
| Technical/Professional Services | 72669.7662 | 40% | 100% | 75% factor for lower local labor | 43601.8597 | 29067.9065 | 72669.7662 | 0
| Scheduled Maint. | 109004.6493 | 40% | 100% |  | 65402.7896 | 43601.8597 | 109004.6493 | 0
| Equipment rental | 36334.8831 | 40% | 100% | this includes annualized cost for Major Maint Program | 21800.9299 | 14533.9532 | 36334.8831 | 0
| Miscellaneous | 0 | 40% | 100% | This is an ANNUALIZED FIGURE for ST MMR planning | 0 | 0 | 0 | 0
| Auxiliary Parts | 0 | 40% | 100% |  | 0 | 0 | 0 | 0
| Freight | 0 | 40% | 100% | 1% of 75% of total | 0 | 0 | 0 | 0
| Other | 0 | 40% | 100% |  | 0 | 0
| Sub-Total | 726697.6623 |  |  | Basis: 7 yrs of TX City Plant actuals on 140MW steam turbine including Schedule Maint. | 436018.5974 | 290679.0649 | 726697.6623 | 0
Water Supply Pipeline and Booster Station | [5 empty] | 0% | 100% | 0% | 100%
| Repair Parts | 0 | 75% | 100% | 1.5% of TIC ($6,000,000) | 0 | 0 | 0 | 0
| Outside Repair Services | 0 | 75% | 100% | ROW maint., pigging, pump repair, cathodic protection | 0 | 0 | 0 | 0
| Technical/Professional Services | 0 | 75% | 100% | 61 kms of 16" cast iron pipe | 0 | 0 | 0 | 0
| Outside Contract Labor | 0 | 75% | 100% |  | 0 | 0 | 0 | 0
| Equipment rental | 0 | 75% | 100% | Deleted from scope | 0 | 0 | 0 | 0
| Miscellaneous | 0 | 75% | 100% |  | 0 | 0 | 0 | 0
| Freight | 0 | 75% | 100% |  | 0 | 0 | 0 | 0
| Other | 0 | 75% |  |  | 0 | 0
| Sub-Total | 0 |  |  |  | 0 | 0 | 0 | 0
Fuel Facility | [5 empty] | 0% | 100% | 0% | 100%
| Repair Parts | 0 | 75% | 100% | Misc. repairs (yearly average) | 0 | 0 | 0 | 0
| Outside Repair Services | 0 | 75% | 100% | plus Dredging cost ($200M every 2 years) | 0 | 0 | 0 | 0
| Technical/Professional Services | 0 | 75% | 100% |  | 0 | 0 | 0 | 0
| Outside Contract Labor | 0 | 75% | 100% |  | 0 | 0 | 0 | 0
| Equipment rental | 0 | 75% | 100% |  | 0 | 0 | 0 | 0
| Miscellaneous | 0 | 75% | 100% | Deleted from Scope | 0 | 0 | 0 | 0
| Freight | 0 | 75% | 100% |  | 0 | 0 | 0 | 0
| Other | 0 | 75% |  |  | 0 | 0
| Sub-Total | 0 |  |  |  | 0 | 0 | 0 | 0
Miscellaneous Maintenance Expense | [5 empty] | 75% | 25% | 100% | 0%
| Warehouse Supplies | 369641.2891 | 25% | 100% | Scaled on plant MW | 277230.9668 | 92410.3223 | 369641.2891 | 0
| Vehicle Fuel/Gasoline | 0 | 25% | 100% | scaled: $416,000 x (500MW/414MW)^0.6 x 75% labor factor | 0 | 0 | 0 | 0
| Vehicle Repairs & Maintenance | 0 | 25% | 100% | 75% factor for lower local labor | 0 | 0 | 0 | 0
| Vehicle Lease | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Equipment rent/lease | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Lubricants/Turbine Oil/Grease/Compounds | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Tools & Tool Repair | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Maint. Materials & Supplies | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Technical/Professional Services | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Contact Labor/Temporaries | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Outside Repair Services | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Outside Services Contract Labor | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Radio Parts and repairs | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| BOP Repairs | 0 | 25% | 100% |  | 0 | 0 | 0 | 0
| Hydrogen | 0 | 25% | 100% | included in chemicals | 0 | 0 | 0 | 0
| Freight | 0 | 25% | 100% | 5% of 75% of total | 0 | 0 | 0 | 0
| Other | 0 | 25% | 100% |  | 0 | 0
| Sub-Total | 369641.2891 |  |  | Basis: 11 years of Actuals from Tx City/Clear Lake Plants | 277230.9668 | 92410.3223 | 369641.2891 | 0
O&M Annual Fee | [5 empty] | 100% | 0% | 100% | 0%
| Basis/Justification: | 1160000 | 0% | 100% | Raiwind (BC Hydro) (120MW) $3.67/MW | 1160000 | 0 | 1160000 | 0
|  | 0 | 0% | 100% | Dabhol (2150 MW) $1.72/MW | 0 | 0
Use 10% of O&M costs managed |  | 0 | 0% | 100% | East Java (500 MW)(GE quote) $2.00/MW | 0 | 0
including Comm. Office and GT |  | 0 | 0% | 100% | Multan (800 MW) $2.50/MW | 0 | 0
Scheduled Maint. |  | 0 | 0% | 100% | Hainan (150 MW) $4.40/MW | 0 | 0
|  | 0 | 0% | 100% | Guam (88 MW) $6.81/MW | 0 | 0
|  | 0 | 0% | 100% | Tapal (Wartsila) (126 MW) $1.90/MW (18 mo.) | 0 | 0
| Sub-Total | 1160000 |  |  |  | 1160000 | 0 | 1160000 | 0
Operator Overhead Charge (G&A) | [5 empty] | 100% | 0% | 0% | 100%
| Basis/Justification: | 0 | 0% | 100% | US, UK and like | 0 | 0 | 0 | 0
| Annual % of Payroll & Burden based | 4.1 | 0% | 100% | India, Brazil, Argentina and like | 4.1 | 0
| on country type (10%, 15%, 20%) | 0 | 0% | 100% | Bangladesh and like | 0 | 0
| 0 | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 410% |  |  | Basis: Eval team concensus | 4.1 | 0 | 0 | 0
Major Equipment Maintenance Program (20 year total) | [5 empty] | 71.09% | 28.91% | 100% | 0%
| Labor & Engineering | 5238380 | 95% | 100% | 1.0 x Labor & Engineering | 261919 | 4976461 | 5238380 | 0
| Repairs | 100023570.684 | 0% | 100% | 1.0 x Repairs | 100023570.684 | 0 | 100023570.684 | 0
| New parts | 35810338.4464 | 100% | 100% | 1.0 x (New parts) | 0 | 35810338.4464 | 35810338.4464 | 0
| total cost (LM 6000) | 0 | 100% | 100% |  | 0 | 0
| Other | 0 | 100% | 100% |  | 0 | 0
| Sub-Total | 141072289.1304 |  |  |  | 100285489.684 | 40786799.4464 | 141072289.1304 | 0
Commercial Office Expenses | [5 empty] | 0% | 100% | 0% | 100%
| Administrative/Technical | 0 | 0% | 100% |  | 0 | 0 | 0 | 0
| Other | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 0 |  |  | Basis: | 0 | 0 | 0 | 0
Sustaining Project Expenses | [5 empty] | 100% | 0% | 100% | 0%
| Project Expenses | 26055.5223 | 0% | 100% | 10% of procurement items | 26055.5223 | 0 | 26055.5223 | 0
| Other | 0 | 0% | 100% |  | 0 | 0
| Sub-Total | 26055.5223 |  |  | Basis: Eval team concensus | 26055.5223 | 0 | 26055.5223 | 0
Vehicular Fuel Usage | [5 empty] | 50% | 50% | 100% | 0%
| 3 Trucks: | 0 |  |  |  | 0 | 0
| 3 x gal/15 miles x $1.5/gal x 20000 miles/yr | 6000 | 50% | 100% |  | 3000 | 3000 | 6000 | 0
| 1 Van & 1 Flat-bed Truck: | 0 |  |  |  | 0 | 0
| 2 x gal/ 10 miles x $1.5/gal x 20 miles/day x 365 days/year | 2190 | 50% | 100% |  | 1095 | 1095 | 2190 | 0
| 2 Forklifts: | 0 |  |  |  | 0 | 0
| 2 x 2 gal/hr x $1.5/gal x 2 hr/day x 365 days/yr | 4380 | 50% | 100% |  | 2190 | 2190 | 4380 | 0
| 1 Crane: | 0 |  |  |  | 0 | 0
| 5 gal/hr x $1.5/gal x 40 days/yr x 8 hours/day | 0 | 50% | 100% |  | 0 | 0 | 0 | 0
| 1 Crew Boats: | 0 |  |  |  | 0 | 0
| 20 gal/hr x 1hr/30 miles x 30 miles x 2rd trips/d x365 days/yr x $1.5/gal x 2.0 (idle factor) | 0 | 50% | 100% |  | 0 | 0 | 0 | 0
| Sub-Total | 12570 |  |  | Basis: | 6285 | 6285 | 12570 | 0
Note:
1/ Fixed Maintenance costs are assumed to be 50% parts, 25% labor, 25% consumables.
2/ The 75% labor and parts factor is computed as follows:
- 25% component of the fixed maintenance costs are discounted 75% due to low labor rates in country --> .25 X .25= .0625
- 25% component of the fixed maintenance costs are discounted 25% due to the assumed lower consumables cost in country --> .25 X .75 = .1875
- 50% component of the fixed maintenance costs are not discounted and assumed imported or local full price --> .5 X 1.0 = .5
- Therefore, total discount factor off full costs equals 75%.
3/ Customs duty rate of 49.75% is not applied to all foreign imported parts and consumables (assumed to be 75% of total "foreign" amount).
4/ Customer duty for various types of equipment needs to be confirmed by EI tax specialists.

## Plant Configuration (hidden)
Plant Configuration Lookup Table
Assumes United States location and gas fuel
1 | Plant Configuration |  | GE LM6000 | GE 7EA | GE 7FA | W501D5 | W501D5A | None | GE 6B | BOILERS
2 | Number of Units |  | 0 | 0 | 2 | 0 | 0 |  | 0 | 0
3 | Capacity |  | 0 | 0 | 340 | 0 | 0 |  | 0 | 0
4 | Operational Hours per year |  | 0 | 0 | 8322 | 0 | 0 |  | 0 | 0
5
6 | Plant Labor (Number of personnel) |  | 0 | 0 | 15 | 0 | 0 |  | 0 | 0
7
8 | Administration Staff
9 |  | Plant Manager |  |  | 1
10 |  | Assistant Plant Manager
11 |  | Plant Engineer
12 |  | Administration Manager
13 |  | Controller
14 |  | Accountant
15 |  | Administrative Assistant |  |  | 1
16 |  | Warehouse Supervisor
17 |  | Other
18 |  | Other
19 |  | Other
20
21 | Operations Staff
22 |  | Operations Manager |  |  | 1
23 |  | Operations Shift Supervisors
24 |  | Control Room Operators
25 |  | Turbine Operators
26 |  | Water System Opertors
27 |  | Fuel Storage/Handling Operators
28 |  | Utility Operators
29 |  | Chemist
30 |  | Tech III |  |  | 4
31 |  | Tech II |  |  | 4
32 |  | Other
33
34 | Maintenance Staff
35 |  | Maintenance Manager |  |  | 1
36 |  | Mechanical Engineer
37 |  | Maintenance Planner
38 |  | Mechanic |  |  | 1
39 |  | I&C Engineer
40 |  | I&C Technician |  |  | 1
41 |  | Electrical Technician |  |  | 1
42 |  | Other
43 |  | Other
44 |  | Other
45 |  | Other
46
47 | Operations & Maintenance (Annual)
48 | Employee Expenses
49 |  | Travel Expenses/Overtime Meals | 0 | 0 | 4500 | 0 | 0 |  | 0 | 0
50 |  | Conferences/Training | 0 | 0 | 5727.2727 | 0 | 0 |  | 0 | 0
51 |  | Employees Expense | 0 | 0 | 3409.0909 | 0 | 0 |  | 0 | 0
52 |  | Interviews/Relocations | 0 | 0 | 3750 | 0 | 0 |  | 0 | 0
53 |  | Professional Dues | 0 | 0 | 4500 | 0 | 0 |  | 0 | 0
54 |  | Entertainment Expense | 0 | 0 | 763.6364 | 0 | 0 |  | 0 | 0
55 |  | Daily Meal Allowance | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
56 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
57 |  | Sub-Total | 0 | 0 | 22650 | 0 | 0 |  | 0 | 0
58 | Permanent Contract Labor
59 |  | Contract Labor | [6 empty] | 0 | 0
60 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
61 |  | Sub-Total | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
62 | Environmental Expense (inc. permit fees)
63 |  | Training/Awards | 0 | 0 | 3315 | 0 | 0 |  | 0 | 0
64 |  | Permits | 0 | 0 | 10908.3333 | 0 | 0 |  | 0 | 0
65 |  | Materials & Supplies | 0 | 0 | 3867.5 | 0 | 0 |  | 0 | 0
66 |  | Technical/Professional Services | 0 | 0 | 0 | 1 | 1 |  | 0 | 0
67 |  | Other Outside Services (RATA) | 0 | 0 | 20000 | 0 | 0 |  | 0 | 0
68 |  | Non-Hazardous Waste Handling | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
69 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
70 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
71 |  | Sub-Total | 0 | 0 | 38090.8333 | 1 | 1 |  | 0 | 0
72 | Safety Expense
73 |  | Training/Awards | 0 | 0 | 4238.7097 | 0 | 0 |  | 0 | 0
74 |  | Permits | 0 | 9625 | 10908.3333 | 0 | 0 |  | 0 | 0
75 |  | Company Membership & Dues
76 |  | Routine Safety Supplies | 0 | 0 | 6770.5645 | 0 | 0 |  | 0 | 0
77 |  | Technical/Professional Services | 6000 | 0 | 0 | 0 | 0 |  | 6000 | 0
78 |  | Safety Equipment Rentals
79 |  | Sub-Total | 6000 | 9625 | 21917.6075 | 0 | 0 |  | 6000 | 0
80 | Buildings & Grounds
81 |  | Security training and facilities | 8000 | 0 | 0 | 0 | 0 |  | 0 | 0
82 |  | Building repairs & painting | 0 | 0 | 6000 | 0 | 0 |  | 0 | 0
83 |  | Road repairs
84 |  | Technical/Professional Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
85 |  | Outside services Contract labor | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
86 |  | Equipment Rentals | 0 | 0 | 2000 | 0 | 0 |  | 0 | 0
87 |  | Other Rents | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
88 |  | Supplies | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
89 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
90 |  | Sub-Total | 8000 | 0 | 8000 | 0 | 0 |  | 0 | 0
91 | Other Supplies & Expenses
92 |  | Office Supplies & Expenses | 0 | 0 | 4090.9091 | 0 | 0 |  | 0 | 0
93 |  | Materials & Supplies | 0 | 0 | 2045.4545 | 0 | 0 |  | 0 | 0
94 |  | Outside Services Contract Labor | 0 | 0 | 818.1818 | 0 | 0 |  | 0 | 0
95 |  | Technical/Professional Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
96 |  | Legal | 10000 | 10000 | 10000 | 10000 | 10000 |  | 10000 | 10000
97 |  | Accounting | 2400 | 2400 | 2400 | 2400 | 2400 |  | 2400 | 2400
98 |  | Office Equipment Maint. | 2000 | 2000 | 2000 | 2000 | 2000 |  | 2000 | 2000
99 |  | Tax | 6000 | 6000 | 6000 | 6000 | 6000 |  | 6000 | 6000
100 |  | Regional Technical Support | 12000 | 12000 | 12000 | 12000 | 12000 |  | 12000 | 12000
101 |  | Customs | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
102 |  | Regulatory | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
103 |  | Other Outside Services | 2000 | 2000 | 2000 | 2000 | 2000 |  | 2000 | 2000
104 |  | Office Equipment Rental | 2400 | 2400 | 2400 | 2400 | 2400 |  | 2400 | 2400
105 |  | Other Rents | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
106 |  | Radio parts/repair | 1000 | 1000 | 1000 | 1000 | 1000 |  | 1000 | 1000
107 |  | PC Hardware (purchase) | 3000 | 3000 | 3000 | 3000 | 3000 |  | 3000 | 3000
108 |  | PC Software | 2000 | 2000 | 2000 | 2000 | 2000 |  | 2000 | 2000
109 |  | PC Hardware Rental/Lease | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
110 |  | PC Maintenance | 1000 | 1000 | 1000 | 1000 | 1000 |  | 1000 | 1000
111 |  | Postage & Freight Expenses | 3600 | 3600 | 3600 | 3600 | 3600 |  | 3600 | 3600
112 |  | Utilities (office water, power, gas) | 12000 | 12000 | 12000 | 12000 | 12000 |  | 12000 | 12000
113 |  | Public relations/Contributions | 1000 | 1000 | 1000 | 1000 | 1000 |  | 1000 | 1000
114 |  | Boat maintenance/repair | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
115 |  | Vehicle maintenance/repair | 2000 | 2000 | 2000 | 2000 | 2000 |  | 2000 | 2000
116 |  | Vehicle fuel | 14970 | 14970 | 14970 | 14970 | 14970 |  | 14970 | 14970
117 |  | Boat fuel | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
118 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
119 |  | Sub-Total | 77370 | 77370 | 84324.5455 | 77370 | 77370 |  | 77370 | 77370
120 | Communications
121 |  | Phone service | 12000 | 0 | 12000 | 12000 | 12000 |  | 12000 | 12000
122 |  | Cellular phone service | 3600 | 0 | 3600 | 3600 | 3600 |  | 3600 | 3600
123 |  | VSAT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
124 |  | Sub-Total | 15600 | 0 | 15600 | 15600 | 15600 |  | 15600 | 15600
125 | Operating Insurance
126 |  | Operating Insurance | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
127 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
128 |  | Sub-Total | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
129 | Control Room/Laboratory Expenses
130 |  | Technical/Professional Services | 0 | 0 | 122299.0035 | 0 | 0 |  | 0 | 0
131 |  | Reagents & Supplies | 0 | 0 | 35970.2951 | 0 | 0 |  | 0 | 0
132 |  | Rental Equipment | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
133 |  | Analyzer Repairs | 0 | 0 | 0 | 0 | 0 |  | 0 | 500
134 |  | Contract Labor/Temporaries | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
135 |  | Other Outside Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
136 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
137 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
138 |  | Sub-Total | 0 | 0 | 158269.2986 | 0 | 0 |  | 0 | 500
139 | Operations Support (Year 1 Only)
140 |  | Operations Support Personnel | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
141 |  | Per diem | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
142 |  | Home leave, travel | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
143 |  | Tax Protection (over 6 months) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
144 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
145 |  | Sub-Total | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
146 | Chemicals (including Water treatment & Lubricity Agent)
147 |  | Technical/Professional Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
148 |  | Pretreatment chemicals | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
149 |  | Demin Acid/Caustic | 0 | 0 | 0 | 0 | 0 |  | 0 | 4360.8005
150 |  | Resin Replacement | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
151 |  | CT Chemicals | 0 | 0 | 86446.2753 | 0 | 0 |  | 0 | 0
152 |  | Boiler Chemicals | 0 | 0 | 96819.8283 | 0 | 0 |  | 0 | 83251.098
153 |  | SCR Ammonia | 0 | 0 | 421053.5714 | 0 | 0 |  | 0 | 0
154 |  | Potable Water Chemicals | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
155 |  | Hydrogen (generators) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
156 |  | Waste Water Treatment | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
157 |  | Lubricity Agent | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
158 |  | Taxes/freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
159 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
160 |  | Sub-Total | 0 | 0 | 604319.675 | 0 | 0 |  | 0 | 87611.8985
161 | Painting
162 |  | Paint & Materials | 0 | 0 | 31099.6277 | 0 | 0 |  | 0 | 0
163 |  | Technical/Professional Services | 0 | 0 | 12439.8511 | 0 | 0 |  | 0 | 0
164 |  | Outside Contract Services | 0 | 0 | 12439.8511 | 0 | 0 |  | 0 | 0
165 |  | Equipment rental | 0 | 0 | 6219.9255 | 0 | 0 |  | 0 | 0
166 |  | Miscellaneous | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
167 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
168 |  | Sub-Total | 0 | 0 | 62199.2554 | 0 | 0 |  | 0 | 0
169 | Electrical & Controls
170 |  | Repair Parts | 0 | 0 | 6666.6667 | 0 | 0 |  | 0 | 0
171 |  | Outside Repair Services | 0 | 0 | 2666.6667 | 0 | 0 |  | 0 | 0
172 |  | Technical/Professional Services | 0 | 0 | 1333.3333 | 0 | 0 |  | 0 | 0
173 |  | Outside Contract Services | 0 | 0 | 2000 | 0 | 0 |  | 0 | 0
174 |  | Equipment rental | 0 | 0 | 666.6667 | 0 | 0 |  | 0 | 0
175 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
176 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
177 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
178 |  | Sub-Total | 0 | 0 | 13333.3333 | 0 | 0 |  | 0 | 0
179 | Water Treatment System
180 |  | Repair Parts | 0 | 0 | 62199.2554 | 0 | 0 |  | 0 | 0
181 |  | Outside Repair Services | 0 | 0 | 24879.7022 | 0 | 0 |  | 0 | 0
182 |  | Technical/Professional Services | 0 | 0 | 12439.8511 | 0 | 0 |  | 0 | 0
183 |  | Outside Contract Labor | 0 | 0 | 18659.7766 | 0 | 0 |  | 0 | 0
184 |  | Equipment rental | 0 | 0 | 6219.9255 | 0 | 0 |  | 0 | 0
185 |  | Miscellaneous | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
186 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
187 |  | Sub-Total | 0 | 0 | 124398.5108 | 0 | 0 |  | 0 | 0
188 | Cooling System
189 |  | Repair Parts | 0 | 0 | 79526.1908 | 0 | 0 |  | 0 | 0
190 |  | Outside Repair Services | 0 | 0 | 31810.4763 | 0 | 0 |  | 0 | 0
191 |  | Technical/Professional Services | 0 | 0 | 15905.2382 | 0 | 0 |  | 0 | 0
192 |  | Outside Contract Labor | 0 | 0 | 23857.8572 | 0 | 0 |  | 0 | 0
193 |  | Equipment rental | 0 | 0 | 7952.6191 | 0 | 0 |  | 0 | 0
194 |  | Miscellaneous (chillers) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
195 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
196 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
197 |  | Sub-Total | 0 | 0 | 159052.3816 | 0 | 0 |  | 0 | 0
198 | Substation/Interconnects
199 |  | Repair Parts | 0 | 0 | 28052.0555 | 0 | 0 |  | 0 | 0
200 |  | Electric Meter Calibration & Testing | 0 | 0 | 11220.8222 | 0 | 0 |  | 0 | 0
201 |  | Outside Repair Services | 0 | 0 | 5610.4111 | 0 | 0 |  | 0 | 0
202 |  | Technical/Professional Services | 0 | 0 | 2805.2055 | 0 | 0 |  | 0 | 0
203 |  | Outside Contract Labor | 0 | 0 | 5610.4111 | 0 | 0 |  | 0 | 0
204 |  | Equipment rental | 0 | 0 | 2805.2055 | 0 | 0 |  | 0 | 0
205 |  | Miscellaneous | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
206 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
207 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
208 |  | Sub-Total | 0 | 0 | 56104.1109 | 0 | 0 |  | 0 | 0
209 | Gas Turbines (excluding scheduled maint.)
210 |  | Repair Parts | 0 | 0 | 247992.1074 | 0 | 0 |  | 0 | 0
211 |  | Outside Repair Services | 0 | 0 | 99196.843 | 0 | 0 |  | 0 | 0
212 |  | Technical/Professional Services | 0 | 0 | 49598.4215 | 0 | 0 |  | 0 | 0
213 |  | Outside Contract Labor | 0 | 0 | 74397.6322 | 0 | 0 |  | 0 | 0
214 |  | Equipment rental | 0 | 0 | 24799.2107 | 0 | 0 |  | 0 | 0
215 |  | Miscellaneous | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
216 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
217 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
218 |  | Sub-Total | 0 | 0 | 495984.2149 | 0 | 0 |  | 0 | 0
219 | Boilers
220 |  | Repair Parts | 0 | 0 | 150854.4047 | 0 | 0 |  | 0 | 0
221 |  | Outside Repair Services | 0 | 0 | 60341.7619 | 0 | 0 |  | 0 | 0
222 |  | Technical/Professional Services | 0 | 0 | 30170.8809 | 0 | 0 |  | 0 | 0
223 |  | Outside Contract Labor | 0 | 0 | 45256.3214 | 0 | 0 |  | 0 | 0
224 |  | Equipment rental | 0 | 0 | 15085.4405 | 0 | 0 |  | 0 | 0
225 |  | Miscellaneous | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
226 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
227 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
228 |  | Sub-Total | 0 | 0 | 301708.8094 | 0 | 0 |  | 0 | 0
229 | Steam Turbine (including Scheduled Maint.)
230 |  | Non-scheduled maint. parts/repairs | 0 | 0 | 363348.8311 | 0 | 0 |  | 0 | 0
231 |  | Outside Repair Services | 0 | 0 | 145339.5325 | 0 | 0 |  | 0 | 0
232 |  | Technical/Professional Services | 0 | 0 | 72669.7662 | 0 | 0 |  | 0 | 0
233 |  | Scheduled Maint. | 0 | 0 | 109004.6493 | 0 | 0 |  | 0 | 0
234 |  | Equipment rental | 0 | 0 | 36334.8831 | 0 | 0 |  | 0 | 0
235 |  | Miscellaneous | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
236 |  | Auxiliary Parts | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
237 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
238 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
239 |  | Sub-Total | 0 | 0 | 726697.6623 | 0 | 0 |  | 0 | 0
240 | Water Supply Pipeline and Booster Station
241 |  | Repair Parts | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
242 |  | Outside Repair Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
243 |  | Technical/Professional Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
244 |  | Outside Contract Labor | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
245 |  | Equipment rental | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
246 |  | Miscellaneous | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
247 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
248 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
249 |  | Sub-Total | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
250 | Fuel Facility (Gas Compression)
251 |  | Repair Parts | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
252 |  | Outside Repair Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
253 |  | Technical/Professional Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
254 |  | Outside Contract Labor | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
255 |  | Equipment rental | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
256 |  | Miscellaneous | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
257 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
258 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
259 |  | Sub-Total | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
260 | Miscellaneous Maintenance Expense
261 |  | Warehouse Supplies | 0 | 0 | 369641.2891 | 0 | 0 |  | 0 | 0
262 |  | Vehicle Fuel/Gasoline | 0 | 0 | 0 | 0 | 0 |  | 2 | 0
263 |  | Vehicle Repairs & Maintenance | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
264 |  | Vehicle Lease | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
265 |  | Equipment rent/lease | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
266 |  | Lubricants/Turbine Oil/Grease/Compounds | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
267 |  | Tools & Tool Repair | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
268 |  | Maint. Materials & Supplies | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
269 |  | Technical/Professional Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
270 |  | Contact Labor/Temporaries | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
271 |  | Outside Repair Services | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
272 |  | Outside Services Contract Labor | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
273 |  | Radio Parts and repairs | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
274 |  | BOP Repairs | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
275 |  | Hydrogen | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
276 |  | Freight | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
277 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
278 |  | Sub-Total | 0 | 0 | 369641.2891 | 0 | 0 |  | 2 | 0
279 | O&M Annual Fee
280 |  | Basis/Justification: | 0 | 0 | 1160000 | 0 | 0 |  | 0 | 0
281
282
283
284
285
286 |  | (Use 10% of O&M costs managed)
287 |  | Sub-Total | 0 | 0 | 1160000 | 0 | 0 |  | 0 | 0
288 | Operator Overhead Charge (G&A)
289 |  | Basis/Justification:
290 |  | Annual % of Payroll & Burden based | 10% | 410% | 410% | 510% | 510%
291 |  | on country type (10%, 15%, 20%)
292
293 |  | Sub-Total | 10% | 410% | 410% | 510% | 510% |  | 0% | 0%
294 | Major Equipment Maintenance (20 year total)
295 |  | Labor & Engineering | 0 | 0 | 5238380 | 0 | 0 |  | 0
296 |  | Repairs | 0 | 0 | 100023570.684 | 0 | 0 |  | 1961532
297 |  | New parts | 0 | 0 | 35810338.4464 | 0 | 0 |  | 0
298 |  | total cost (LM 6000) | 0 | 0 | 0 | 0 | 0 |  | 0
299 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0
300 |  | Sub-Total | 0 | 0 | 141072289.1304 | 0 | 0 |  | 1961532
301 | Commercial Office Expenses
302 |  | Administrative/Technical | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
303 |  | Other | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
304 |  | Sub-Total | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
305 | Sustaining Project Expenses
306 |  | Project Expenses | 0 | 0 | 26055.5223 | 0 | 0 |  | 0 | 0
307 |  | Other
308 |  | Sub-Total | 0 | 0 | 26055.5223 | 0 | 0 |  | 0 | 0
309 | Vehicular Fuel Usage
310 |  | 3 Trucks:
311 |  | 3 x gal/15 miles x $1.5/gal x 20000 miles/yr | 6000 | 6000 | 6000 | 6000 | 6000 |  | 6000 | 0
312 |  | 1 Van & 1 Flat-bed Truck:
313 |  | 2 x gal/ 10 miles x $1.5/gal x 20 miles/day x 365 days/year | 2190 | 2190 | 2190 | 2190 | 2190 |  | 2190 | 0
314 |  | 2 Forklifts:
315 |  | 2 x 2 gal/hr x $1.5/gal x 2 hr/day x 365 days/yr | 4380 | 4380 | 4380 | 4380 | 4380 |  | 4380 | 0
316 |  | 1 Crane:
317 |  | 5 gal/hr x $1.5/gal x 40 days/yr x 8 hours/day | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
318 |  | 1 Crew Boats:
319 |  | 20 gal/hr x 1hr/30 miles x 30 miles x 2rd trips/d x365 days/yr x $1.5/gal x 2.0 (idle factor) | 0 | 0 | 0 | 4 | 4 |  | 4 | 0
320 |  | Sub-Total | 12570 | 12570 | 12570 | 12574 | 12574 |  | 12574 | 0
321
322 |  | GT MW @ ISO | 45 | 85 | 170 | 100 | 120 |  | 35 | 450
323
324
325
326
327
328
329
330
331
332
333

## Initial_Spares(7EA) (hidden)
AES Corp, Dallas, TX (640 MW)
Initial Operating Spares
| Parts Discount = | 0%
COMBUSTION TURBINES & GENERATORS |  | GE 7EA | GE 7FA | Sets
COMBUSTION LINERS |  | 0 | 0
TRANSITION PIECES |  | 0 | 0
FUEL NOZZLES |  | 0 | 0
STAGE 1 NOZZLES |  | 0 | 0
STAGE 2 NOZZLES |  | 0 | 0
STAGE 3 NOZZLES |  | 0 | 0
STAGE 1 BUCKETS |  | 0 | 0
STAGE 2 BUCKETS |  | 0 | 0
STAGE 3 BUCKETS |  | 0 | 0
ROW 1 SUPPORT RING |  | 0
1ST STAGE SHROUD BLOCKS |  | 0 | 0
2ND STAGE SHROUD BLOCKS |  | 0 | 0
3RD STAGE SHROUD BLOCKS |  | 0 | 0
EXTENDER KITS |  | 0 | 0
OPERATIONAL SPARES (INCLUDES MKV CONTROL & EX 2000 SPARES) |  | 0 | 0
GAS TURBINE BEARING LINERS |  | 0 | 0
CI CONSUMABLES |  | 0 | 0
HGP INSPECTION CONSUMABLES |  | 0 | 0
MI CONSUMABLES |  | 0 | 0
GT GENERATOR SPARES |  | 0 | 0
GENERATOR INSPECTION CONSUMABLES |  | 0 | 0
SUB-TOTAL |  | 0 | 0
STEAM TURBINE & GENERATOR
RECOMMENDED OPERATIONAL SPARES |  | 0 | 0
| Sub-Total | 0 | 0
BALANCE OF PLANT |  | 0 | 0
SUB-TOTAL |  | 0 | 0
INSURANCE @ 0.25% |  | 0 | 0
FREIGHT @ 1% |  | 0 | 0
TOTAL |  | 0 | 0

## Initial_Spares(7FA) (hidden)
AES Corp, Dallas, TX (640 MW)
Initial Operating Spares
| Parts Discount = | 0%
COMBUSTION TURBINES & GENERATORS |  | GE 7FA | GE 7FA | Sets
COMBUSTION LINERS |  | 573256 | 0 | 1
TRANSITION PIECES |  | 1246131 | 0 | 1
FUEL NOZZLES |  | 1297423 | 0 | 1
STAGE 1 NOZZLES |  | 1604924 | 0 | 1
STAGE 2 NOZZLES |  | 0 | 0
STAGE 3 NOZZLES |  | 0 | 0
STAGE 1 BUCKETS |  | 3214992 | 0 | 1
STAGE 2 BUCKETS |  | 0 | 0
STAGE 3 BUCKETS |  | 0 | 0
ROW 1 SUPPORT RING |  | 0
1ST STAGE SHROUD BLOCKS |  | 721443 | 0 | 1
2ND STAGE SHROUD BLOCKS |  | 0 | 0
3RD STAGE SHROUD BLOCKS |  | 0 | 0
EXTENDER KITS |  | 0 | 0
OPERATIONAL SPARES (INCLUDES MKV CONTROL & EX 2000 SPARES) |  | 0 | 0
GAS TURBINE BEARING LINERS |  | 0 | 0
CI CONSUMABLES |  | 108508 | 0 | 2
HGP INSPECTION CONSUMABLES |  | 62032 | 0 | 1
MI CONSUMABLES |  | 209215 | 0 | 1
GT GENERATOR SPARES |  | 0 | 0
GENERATOR INSPECTION CONSUMABLES |  | 0 | 0
SUB-TOTAL |  | 9037924 | 0
STEAM TURBINE & GENERATOR
RECOMMENDED OPERATIONAL SPARES |  | 0 | 0
| Sub-Total | 9037924 | 0
BALANCE OF PLANT |  | 500000 | 0
SUB-TOTAL |  | 9537924 | 0
INSURANCE @ 0.25% |  | 23844.81 | 0
FREIGHT @ 1% |  | 95379.24 | 0
TOTAL |  | 9657148.05 | 0

## Initial_Spares(W501D5) (hidden)
AES Corp, Dallas, TX (640 MW)
Initial Operating Spares
| Parts Discount = | 0%
COMBUSTION TURBINES & GENERATORS |  | W501D5 | GE 7FA | Sets
BASKETS |  | 0 | 0
TRANSITION PIECES |  | 0 | 0
TRANSITION SEALS |  | 0 | 0
FUEL NOZZLES |  | 0 | 0
CLAMSHELLS |  | 0 | 0
ROW 1 BLADES |  | 0 | 0
ROW 2 BLADES |  | 0 | 0
ROW 3 BLADES |  | 0 | 0
ROW 4 BLADES |  | 0 | 0
ROW 1 VANES |  | 0 | 0
ROW 2 VANES |  | 0 | 0
ROW 3 VANES |  | 0 | 0
ROW 4 VANES |  | 0 | 0
ROW 1 RING SEGMENTS |  | 0 | 0
ROW 2 RING SEGMENTS |  | 0 | 0
ROW 3 RINGS SEGMENTS |  | 0 | 0
ROW 4 RINGS SEGMENTS |  | 0 | 0
COMP ROTOR BLADES |  | 0 | 0
COMP DIAPHRAGMS |  | 0 | 0
CI CONSUMABLES |  | 0 | 0
HGP INSPECTION CONSUMABLES |  | 0 | 0
MI CONSUMABLES |  | 0
SUB-TOTAL |  | 0
BALANCE OF PLANT
0
SUB-TOTAL |  | 0 | 0
INSURANCE @ 0.25% |  | 0 | 0
FREIGHT @ 1% |  | 0 | 0
TOTAL |  | 0 | 0
0
0

## GT sched cost (LM6000) (hidden)
2xGE LM6000 - Major Maintenance Reserve
Gas Fired Operation |  |  |  |  | Project Life |  | 20 | Years
Lease Club Membership Fees Not Included | [6 empty] | 32740800 | total cost
[7 empty] | 16370400 | cost per engine
Total Number of Installed Units |  |  | 2 |  |  |  | 818520 | cost per year
[7 empty] | 98.3562 | cost per FIRED hour
Inputs
Annual Lease Club Fees |  |  | 0 | per engine |  |  | $201,368 for LM6000 DLE (PD) & 20% increase for liquid fuel operation
Lease Engine Usage Fee |  |  | 83650 | per week (1-26 weeks) |  |  | 50,000 hour engine refurbishment assumes assumes 12 week usage of lease engine
Preventative Maintenance |  |  | 0 | per year |  |  | Semi-Annual Preventative Maintenance
Hot Section Refurbishment / 24,000 hrs |  |  | 1403000 | per GT | (rotable exchange) |  | excludes DLE adder
Engine Refurbishment / 48,000 hrs |  |  | 3000000 | per GT |  |  | excluding 20% adder for DLN
Labor & Engineering / Hot Section |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Labor & Engineering / Major |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Dispatch |  | 8322 | Fired hrs/yr
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Hours (EOY) |  | 8322 | 16644 | 24966 | 33288 | 41610 | 49932 | 58254 | 66576 | 74898 | 83220 | 91542 | 99864 | 108186 | 116508 | 124830 | 133152 | 141474 | 149796 | 158118 | 166440
Maint Inspection (C, H or M) |  |  |  | h |  |  | m |  |  | h |  |  | m |  |  | h |  |  | m
Comb., Hot Sec & Major Maint. Cost | 0 | 0 | 0 | 2806000 | 0 | 0 | 6000000 | 0 | 0 | 2806000 | 0 | 0 | 6000000 | 0 | 0 | 2806000 | 0 | 0 | 6000000 | 0 | 0
Preventative Miantenance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Labor & Engineering | 0 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0
Lease Program |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Engine Usage Fee | 0 | 0 | 0 | 0 | 0 | 0 | 2007600 | 0 | 0 | 0 | 0 | 0 | 2007600 | 0 | 0 | 0 | 0 | 0 | 2007600 | 0 | 0
Yearly Totals | 0 | 0 | 0 | 2856000 | 0 | 0 | 8057600 | 0 | 0 | 2856000 | 0 | 0 | 8057600 | 0 | 0 | 2856000 | 0 | 0 | 8057600 | 0 | 0 | 32740800
Assumptions:
1. Hot Gas Path inspection conducted at 25,000 fired hour intervals and Major at 50,000 hour intervals.
2. Pricing in 1999 USD and escalated by 3% to arrive at 2000 USD. Does not include escalation beyond that.
3. Maintenance and lease costs from George Graham/Stewart & Stevenson 12/10/99 e-mail.
BASE LOAD CASE
Gas Fired Operation |  |  |  |  | Project Life |  | 20 | Years
Lease Club Membership Fees Included | [6 empty] | 28438800 | total cost
[7 empty] | 14219400 | cost per engine
Total Number of Installed Units |  |  | 1 |  |  |  | 710970 | cost per year
[7 empty] | 88.8713 | cost per FIRED hour
Inputs
Annual Lease Club Fees |  |  | 0 | per engine |  |  | $201,368 for LM6000 DLE (PD) & 20% increase for liquid fuel operation
Lease Engine Usage Fee |  |  | 23900 | per week (1-26 weeks) |  |  | 48,000 hour engine refurbishment assumes assumes 12 week usage of lease engine
Preventative Maintenance |  |  | 0 | per year |  |  | Semi-Annual Preventative Maintenance
Hot Section Refurbishment / 24,000 hrs |  |  | 1403000 | per GT | (rotable exchnage) |  | excludes DLE adder
Engine Refurbishment / 48,000 hrs |  |  | 3000000 | per GT |  |  | excluding 20% adder for DLN
Labor & Engineering / Hot Section |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Labor & Engineering / Major |  |  | 25000 |  |  |  | Travel & diem for GE personnel
Dispatch |  | 8000 | Fired hrs/yr
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Hours (EOY) |  | 8000 | 16000 | 24000 | 32000 | 40000 | 48000 | 56000 | 64000 | 72000 | 80000 | 88000 | 96000 | 104000 | 112000 | 120000 | 128000 | 136000 | 144000 | 152000 | 160000
Maint Inspection (H or M) |  |  |  | H |  |  | M |  |  |  | H |  | M |  |  | H |  |  | M
Hot Sec & Major Maint. | 0 | 0 | 0 | 2806000 | 0 | 0 | 6000000 | 0 | 0 | 0 | 2806000 | 0 | 6000000 | 0 | 0 | 2806000 | 0 | 0 | 6000000 | 0 | 0
Preventative Miantenance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Labor & Engineering | 0 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0 | 0 | 50000 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0 | 50000 | 0 | 0
Lease Program |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lease Engine Usage Fee | 0 | 0 | 0 | 0 | 0 | 0 | 573600 | 0 | 0 | 0 | 0 | 0 | 573600 | 0 | 0 | 0 | 0 | 0 | 573600 | 0 | 0
| 0 | 0 | 0 | 2856000 | 0 | 0 | 6623600 | 0 | 0 | 0 | 2856000 | 0 | 6623600 | 0 | 0 | 2856000 | 0 | 0 | 6623600 | 0 | 0
|  | 0 | 0 | 2856000 | 2856000 | 2856000 | 9479600 | 9479600 | 9479600 | 9479600 | 12335600 | 12335600 | 18959200 | 18959200 | 18959200 | 21815200 | 21815200 | 21815200 | 28438800 | 28438800 | 28438800
Assumptions:
1. Hot Gas Path inspection conducted at 25,000 fired hour intervals.
2. Major inspection conducted at 50,000 fired hour intervals.
3. Maintenance and lease costs from George Graham/Stewart & Stevenson 12/10/99 e-mail.

## GT schd cost(7EA) (hidden)
0xGE-Frame 7EA GT Scheduled Maintenance Cost
YEAR |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Subtotal
UNIT 1
UNIT 2
UNIT 3
UNIT 4
LABOR |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NEW PARTS |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Unit Price | Initial SP
Combustion Liners | 1058.9 | [21 empty] | 0
Transition Pieces | 463.064 | [21 empty] | 0
Fuel Nozzles | 489.47 | [21 empty] | 0
Stage 1 Nozzles | 899.488 | [21 empty] | 0
Stage 2 Nozzles | 926.971 | [21 empty] | 0
Stage 3 Nozzles | 986.568 | [21 empty] | 0
Stage 1 Buckets | 910.54 | [21 empty] | 0
Stage 2 Buckets | 901.965 | [21 empty] | 0
Stage 3 Buckets | 791.255 | [21 empty] | 0
Row 1 Support Ring | 36.558 | [21 empty] | 0
1st Stage Shroud Blocks | 182.902 | [21 empty] | 0
2nd Stage Shroud Blocks | 137.414 | [21 empty] | 0
3rd Stage Shroud Blocks | 74.762 | [21 empty] | 0
Renewables--CI | 20.332 | [21 empty] | 0
Renewables--HGP | 32.328 | [21 empty] | 0
Renewables--Major | 154.464 | [21 empty] | 0
Sub-Total Parts |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parts Discount | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Parts(w freight) | 3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR COST |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Repair Price
Combustion Liners | 18 | 0 | [20 empty] | 0
Transition Pieces | 18.5 | [21 empty] | 0
Fuel Nozzles | 120 | [21 empty] | 0
Stage 1 Nozzles | 46 | [21 empty] | 0
Stage 2 Nozzles | 29.5 | [21 empty] | 0
Stage 3 Nozzles | 26 | [21 empty] | 0
Stage 1 Buckets | 74.5 | [21 empty] | 0
Stage 2 Buckets | 39 | [21 empty] | 0
Stage 3 Buckets | 42 | [21 empty] | 0
Row 1 Support Ring | 25 | [21 empty] | 0
1st Stage Shroud Blocks | 15.4 | [21 empty] | 0
2nd Stage Shroud Blocks | 14.4 | [21 empty] | 0
3rd Stage Shroud Blocks | 13.4 | [21 empty] | 0
Repairs (w discunt) | 2% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Repairs (w freight) | 1% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRAND TOTAL (Parts,labor,& Repairs) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Initial_Spares(W501D5A) (hidden)
AES Corp, Dallas, TX (640 MW)
Initial Operating Spares
| Parts Discount = | 0%
COMBUSTION TURBINES & GENERATORS |  | W501D5 | GE 7FA | Sets
BASKETS |  | 0 | 0
TRANSITION PIECES |  | 0 | 0
TRANSITION SEALS |  | 0 | 0
FUEL NOZZLES |  | 0 | 0
CLAMSHELLS |  | 0 | 0
ROW 1 BLADES |  | 0 | 0
ROW 2 BLADES |  | 0 | 0
ROW 3 BLADES |  | 0 | 0
ROW 4 BLADES |  | 0 | 0
ROW 1 VANES |  | 0 | 0
ROW 2 VANES |  | 0 | 0
ROW 3 VANES |  | 0 | 0
ROW 4 VANES |  | 0 | 0
ROW 1 RING SEGMENTS |  | 0 | 0
ROW 2 RING SEGMENTS |  | 0 | 0
ROW 3 RINGS SEGMENTS |  | 0 | 0
ROW 4 RINGS SEGMENTS |  | 0 | 0
COMP ROTOR BLADES |  | 0 | 0
COMP DIAPHRAGMS |  | 0 | 0
CI CONSUMABLES |  | 0 | 0
HGP INSPECTION CONSUMABLES |  | 0 | 0
MI CONSUMABLES |  | 0
SUB-TOTAL |  | 0
BALANCE OF PLANT
0
SUB-TOTAL |  | 0 | 0
INSURANCE @ 0.25% |  | 0 | 0
FREIGHT @ 1% |  | 0 | 0
TOTAL |  | 0 | 0
0
0

## GT schd cost(W501D5) (hidden)
0xW501D5 GT Scheduled Maintenance Cost
YEAR |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Subtotal
UNIT 1
UNIT 2
UNIT 3
UNIT 4
LABOR |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NEW PARTS |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Unit Price | Initial SP
Baskets | 259.854 | [21 empty] | 0
Transition Pieces | 335.468 | [21 empty] | 0
Transition Seals | 48.174 | [21 empty] | 0
Fuel Nozzles | 522.34 | [21 empty] | 0
Clamshells | 92.4 | [21 empty] | 0
Row 1 Blades | 459.675 | [21 empty] | 0
Row 2 Blades | 435.445 | [21 empty] | 0
Row 3 Blades | 506.66 | [21 empty] | 0
Row 4 Blades | 627.861 | [21 empty] | 0
Row 1 Vanes | 785.952 | [21 empty] | 0
Row 2 Vanes | 568.976 | [21 empty] | 0
Row 3 Vanes | 619.22 | [21 empty] | 0
Row 4 Vanes | 709.604 | [21 empty] | 0
Row 1 ring segments | 106.368 | [21 empty] | 0
Row 2 ring segments | 108.624 | [21 empty] | 0
Row 3 rings segments | 64.74 | [21 empty] | 0
Row 4 rings segments | 66.136 | [21 empty] | 0
Comp Rotor Blades | 606.922 | [21 empty] | 0
Comp Diaphragms | 1725.86 | [21 empty] | 0
Sub-Total Parts |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parts wiscount | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Parts(w freight) | 3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR COST |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Repair Price
Baskets | 57.96 | 0 | [20 empty] | 0
Transition Pieces | 105.65 | [21 empty] | 0
Transition Seals | 15 | [21 empty] | 0
Fuel Nozzles | 92.3 | [21 empty] | 0
Clamshells | 14.7 | [21 empty] | 0
Row 1 Blades | 73.5 | [21 empty] | 0
Row 2 Blades | 68.4 | [21 empty] | 0
Row 3 Blades | 56.7 | [21 empty] | 0
Row 4 Blades | 79.17 | [21 empty] | 0
Row 1 Vanes | 105.36 | [21 empty] | 0
Row 2 Vanes | 84.68 | [21 empty] | 0
Row 3 Vanes | 77.4 | [21 empty] | 0
Row 4 Vanes | 70.95 | [21 empty] | 0
Row 1 ring segments | 14.5 | [21 empty] | 0
Row 2 ring segments | 14.5 | [21 empty] | 0
Row 3 rings segments | 13 | [21 empty] | 0
Row 4 rings segments | 13 | [21 empty] | 0
Comp Rotor Blades | 63 | [21 empty] | 0
Comp Diaphragms | 63 | [21 empty] | 0
Repairs (w discunt) | 2% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Repairs (w freight) | 1% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRAND TOTAL (Parts,labor,& Repairs) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## rotation(W501D5) (hidden)
Information Enter
Spare Parts Rotation Plan | [21 empty] | W501D5 | Phase 1 | Phase2 |  | Base On
Year |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Operating Years | 20 | 0
Hours |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EOH or EOS per year | 0 | 8000 |  |  |  | 1
[22 empty] | Number of units | 0
minor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | minor interval | 8000
HGP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HGP interval | 24000
Major | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Major interval | 48000
minor
HGP
Major
[22 empty] | Parts' Name | Repair Interval | Replace / Repair Interval | Spare part Sets for rotation | Initial Spare part sets | Maint. Cost
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Baskets | 8000 | 6 | 2 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Transition Pieces | 8000 | 6 | 2 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Transition Seals | 8000 | 3 | 2 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fuel Nozzles | 8000 | 12 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Clamshells | 8000 | 8 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 1 Blades | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 2 Blades | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 3 Blades | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 4 Blades | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 1 Vanes | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 2 Vanes | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 3 Vanes | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 4 Vanes | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 1 ring segments | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 2 ring segments | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 3 rings segments | 48000 | 1.5 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 4 rings segments | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Comp Rotor Blades | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Comp Diaphragms | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
EOH
EOS

## GTDB(W501D5) (hidden)
Gas Turbine Scheduled Maintenance Data Base
Data Base ID | W501D5
GT TYPE | W501D5
Date of Data Base Updated | 2000-05-17
Updated By | RB
| Interval (EOH) | Labor Cost (k$) | Consumables (K$) |  | Interval (EOS)
Combustion Inspection | 8000 | 106 | 90.1 |  | 400
HGP Inspection | 24000 | 212 | 121.9 |  | 800
Major maintenance | 48000 | 598.9 | 174.9 |  | 2400
Name of Parts | Repair Interval (H) | Replace interval | price of repair (K$) | Price of Replace (K$) | Repare on starts | Replace/Repair
Baskets | 8000 | 6 | 57.96 | 259.854 | 400 | 4
Transition Pieces | 8000 | 6 | 105.65 | 335.468 | 400 | 4
Transition Seals | 8000 | 3 | 15 | 48.174 | 400 | 2
Fuel Nozzles | 8000 | 12 | 92.3 | 522.34 | 400 | 8
Clamshells | 8000 | 8 | 14.7 | 92.4 | 400 | 5
Row 1 Blades | 24000 | 2 | 73.5 | 459.675 | 800 | 2
Row 2 Blades | 24000 | 3 | 68.4 | 435.445 | 800 | 3
Row 3 Blades | 48000 | 2 | 56.7 | 506.66 | 1600 | 2
Row 4 Blades | 48000 | 2 | 79.17 | 627.861 | 1600 | 2
Row 1 Vanes | 24000 | 2 | 105.36 | 785.952 | 800 | 2
Row 2 Vanes | 24000 | 3 | 84.68 | 568.976 | 800 | 3
Row 3 Vanes | 48000 | 2 | 77.4 | 619.22 | 800 | 4
Row 4 Vanes | 48000 | 2 | 70.95 | 709.604 | 1600 | 2
Row 1 ring segments | 24000 | 2 | 14.5 | 106.368 | 800 | 2
Row 2 ring segments | 24000 | 2 | 14.5 | 108.624 | 800 | 2
Row 3 rings segments | 48000 | 1.5 | 13 | 64.74 | 1600 | 1.5
Row 4 rings segments | 48000 | 2 | 13 | 66.136 | 1600 | 2
Comp Rotor Blades | 48000 | 2 | 63 | 606.922 | 1600 | 2
Comp Diaphragms | 48000 | 2 | 63 | 1725.86 | 1600 | 2
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
Remark:
Pricing provided by fax sent by Stacie Carter on 5/15/00.

## GT schd cost(W501D5A) (hidden)
0xW501D5A GT Scheduled Maintenance Cost
YEAR |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Subtotal
UNIT 1
UNIT 2
UNIT 3
UNIT 4
LABOR |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NEW PARTS |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Unit Price | Initial SP
Baskets | 490.588 | [21 empty] | 0
Transition Pieces | 714 | [21 empty] | 0
Transition Seals | 49.938 | [21 empty] | 0
Fuel Nozzles | 521.64 | [21 empty] | 0
Clamshells | 81.9 | [21 empty] | 0
Row 1 Blades | 560.115 | [21 empty] | 0
Row 2 Blades | 470.12 | [21 empty] | 0
Row 3 Blades | 491.92 | [21 empty] | 0
Row 4 Blades | 984.656 | [21 empty] | 0
Row 1 Vanes | 900.336 | [21 empty] | 0
Row 2 Vanes | 617.056 | [21 empty] | 0
Row 3 Vanes | 660.002 | [21 empty] | 0
Row 4 Vanes | 709.604 | [21 empty] | 0
Row 1 ring segments | 128.88 | [21 empty] | 0
Row 2 ring segments | 117.504 | [21 empty] | 0
Row 3 rings segments | 64.74 | [21 empty] | 0
Row 4 rings segments | 125.075 | [21 empty] | 0
Comp Rotor Blades | 654.335 | [21 empty] | 0
Comp Diaphragms | 1817.532 | [21 empty] | 0
Sub-Total Parts |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parts wiscount | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Parts(w freight) | 3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR COST |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Repair Price
Baskets | 117.6 | 0 | [20 empty] | 0
Transition Pieces | 98.2 | [21 empty] | 0
Transition Seals | 15 | [21 empty] | 0
Fuel Nozzles | 96.75 | [21 empty] | 0
Clamshells | 14.7 | [21 empty] | 0
Row 1 Blades | 137.2 | [21 empty] | 0
Row 2 Blades | 115 | [21 empty] | 0
Row 3 Blades | 111.13 | [21 empty] | 0
Row 4 Blades | 113.93 | [21 empty] | 0
Row 1 Vanes | 177.5 | [21 empty] | 0
Row 2 Vanes | 132.3 | [21 empty] | 0
Row 3 Vanes | 77.4 | [21 empty] | 0
Row 4 Vanes | 90.405 | [21 empty] | 0
Row 1 ring segments | 14.5 | [21 empty] | 0
Row 2 ring segments | 14.5 | [21 empty] | 0
Row 3 rings segments | 13 | [21 empty] | 0
Row 4 rings segments | 13 | [21 empty] | 0
Comp Rotor Blades | 63 | [21 empty] | 0
Comp Diaphragms | 63 | [21 empty] | 0
Repairs (w discunt) | 2% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Repairs (w freight) | 1% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRAND TOTAL (Parts,labor,& Repairs) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## rotation(W501D5A) (hidden)
Information Enter
Spare Parts Rotation Plan | [21 empty] | W501D5A | Phase 1 | Phase2 |  | Base On
Year |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Operating Years | 20 | 0
Hours |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EOH or EOS per year | 0 | 8000 |  |  |  | 1
[22 empty] | Number of units | 0
minor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | minor interval | 8000
HGP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HGP interval | 24000
Major | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Major interval | 48000
minor
HGP
Major
[22 empty] | Parts' Name | Repair Interval | Replace / Repair Interval | Spare part Sets for rotation | Initial Spare part sets | Maint. Cost
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Baskets | 8000 | 6 | 2 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Transition Pieces | 8000 | 6 | 2 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Transition Seals | 8000 | 3 | 2 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fuel Nozzles | 8000 | 8 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Clamshells | 8000 | 8 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 1 Blades | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 2 Blades | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 3 Blades | 24000 | 4 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 4 Blades | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 1 Vanes | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 2 Vanes | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 3 Vanes | 24000 | 4 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 4 Vanes | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 1 ring segments | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 2 ring segments | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 3 rings segments | 48000 | 1.5 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 4 rings segments | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Comp Rotor Blades | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Comp Diaphragms | 48000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
EOH
EOS

## GTDB(W501D5A) (hidden)
Gas Turbine Scheduled Maintenance Data Base
Data Base ID | W501D5A
GT TYPE | W501D5A
Date of Data Base Updated | 2000-05-17
Updated By | RB
| Interval (EOH) | Labor Cost (k$) | Consumables (K$) |  | Interval (EOS)
Combustion Inspection | 8000 | 106 | 90.1 |  | 400
HGP Inspection | 24000 | 212 | 121.9 |  | 800
Major maintenance | 48000 | 598.9 | 174.9 |  | 2400
Name of Parts | Repair Interval (H) | Replace interval | price of repair (K$) | Price of Replace (K$) | Repare on starts | Replace/Repair
Baskets | 8000 | 6 | 117.6 | 490.588 | 400 | 4
Transition Pieces | 8000 | 6 | 98.2 | 714 | 400 | 4
Transition Seals | 8000 | 3 | 15 | 49.938 | 400 | 2
Fuel Nozzles | 8000 | 8 | 96.75 | 521.64 | 400 | 5
Clamshells | 8000 | 8 | 14.7 | 81.9 | 400 | 5
Row 1 Blades | 24000 | 2 | 137.2 | 560.115 | 800 | 2
Row 2 Blades | 24000 | 3 | 115 | 470.12 | 800 | 3
Row 3 Blades | 24000 | 4 | 111.13 | 491.92 | 1600 | 2
Row 4 Blades | 48000 | 2 | 113.93 | 984.656 | 1600 | 2
Row 1 Vanes | 24000 | 2 | 177.5 | 900.336 | 800 | 2
Row 2 Vanes | 24000 | 3 | 132.3 | 617.056 | 800 | 3
Row 3 Vanes | 24000 | 4 | 77.4 | 660.002 | 800 | 4
Row 4 Vanes | 48000 | 2 | 90.405 | 709.604 | 1600 | 2
Row 1 ring segments | 24000 | 2 | 14.5 | 128.88 | 800 | 2
Row 2 ring segments | 24000 | 2 | 14.5 | 117.504 | 800 | 2
Row 3 rings segments | 48000 | 1.5 | 13 | 64.74 | 1600 | 1.5
Row 4 rings segments | 48000 | 2 | 13 | 125.075 | 1600 | 2
Comp Rotor Blades | 48000 | 2 | 63 | 654.335 | 1600 | 2
Comp Diaphragms | 48000 | 2 | 63 | 1817.532 | 1600 | 2
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
[5 empty] | 9999999 | 999
Remark:
Pricing provided by fax sent by Stacie Carter on 5/15/00.

## rotation(7EA) (hidden)
Information Enter
Spare Parts Rotation Plan | [21 empty] | GE-7EA-H-V0 | Phase 1 | Phase2 |  | Base On
Year |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Operating Years | 20 | 0
Hours |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EOH or EOS per year | 0 | 8000 |  |  |  | 1
[22 empty] | Number of units | 0
minor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | minor interval | 8000
HGP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HGP interval | 24000
Major | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Major interval | 48000
minor
HGP
Major
[22 empty] | Parts' Name | Repair Interval | Replace / Repair Interval | Spare part Sets for rotation | Initial Spare part sets | Maint. Cost
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combustion Liners | 8000 | 5 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Transition Pieces | 8000 | 6 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
REPAIR |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | 0 | #REF!
BUY |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fuel Nozzles | 8000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stage 1 Nozzles | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stage 2 Nozzles | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stage 3 Nozzles | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stage 1 Buckets | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stage 2 Buckets | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stage 3 Buckets | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row 1 Support Ring | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1st Stage Shroud Blocks | 24000 | 2 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Stage Shroud Blocks | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3rd Stage Shroud Blocks | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EOH
EOS

## GTDB(7EA) (hidden)
Gas Turbine Scheduled Maintenance Data Base
Data Base ID | GE-7EA-H-V0
GT TYPE | GE-Frame 7EA
Date of Data Base Updated | 2000-03-15
Updated By | RB
| Interval (EOH) | Labor Cost (k$) | Consumables (K$) |  | Interval (EOS)
Combustion Inspection | 8000 | 27.9 | 20.332 |  | 800
HGP Inspection | 24000 | 123 | 32.328 |  | 1200
Major maintenance | 48000 | 220 | 154.464 |  | 2400
Name of Parts | Repair Interval (H) | Replace interval | price of repair (K$) | Price of Replace (K$) | Repare on starts | Replace/Repair
Combustion Liners | 8000 | 5 | 18 | 1058.9 | 800 | 5
Transition Pieces | 8000 | 6 | 18.5 | 463.064 | 800 | 6
Fuel Nozzles | 8000 | 3 | 120 | 489.47 | 800 | 3
Stage 1 Nozzles | 24000 | 3 | 46 | 899.488 | 1200 | 3
Stage 2 Nozzles | 24000 | 3 | 29.5 | 926.971 | 1200 | 3
Stage 3 Nozzles | 24000 | 3 | 26 | 986.568 | 1200 | 3
Stage 1 Buckets | 24000 | 3 | 74.5 | 910.54 | 1200 | 3
Stage 2 Buckets | 24000 | 3 | 39 | 901.965 | 1200 | 4
Stage 3 Buckets | 24000 | 3 | 42 | 791.255 | 1200 | 4
Row 1 Support Ring | 24000 | 3 | 25 | 36.558 | 1200 | 3
1st Stage Shroud Blocks | 24000 | 2 | 15.4 | 182.902 | 1200 | 2
2nd Stage Shroud Blocks | 24000 | 3 | 14.4 | 137.414 | 1200 | 4
3rd Stage Shroud Blocks | 24000 | 3 | 13.4 | 74.762 | 1200 | 4
Remark:

## Initial_Spares(6B) (hidden)
AES Corp, Dallas, TX (640 MW)
Initial Operating Spares (GE 6B)
| Parts Discount = | 0%
COMBUSTION TURBINES & GENERATORS |  | US $
FUEL NOZZLES |  | 0
CROSSFIRE TUBES |  | 0
COMBUSTION LINERS |  | 0
TRANSITION PIECES |  | 0
1ST STAGE BUCKETS |  | 0
2ND STAGE BUCKETS |  | 0
3RD STAGE BUCKETS |  | 0
1ST STAGE SHROUDS |  | 0
2ND STAGE SHROUDS |  | 0
3RD STAGE SHROUDS |  | 0
1ST STAGE NOZZLES |  | 0
2ND STAGE NOZZLES |  | 0
3RD STAGE NOZZLES |  | 0
OPERATIONAL SPARES (INCLUDES MKV CONTROL & EX 2000 SPARES) |  | 0
GAS TURBINE BEARING LINERS |  | 0
CI CONSUMABLES |  | 0
HGP INSPECTION CONSUMABLES |  | 0
MI CONSUMABLES |  | 0
GT GENERATOR SPARES |  | 0
GENERATOR INSPECTION CONSUMABLES |  | 0
SUB-TOTAL |  | 0
STEAM TURBINE & GENERATOR
RECOMMENDED OPERATIONAL SPARES
| Sub-Total | 0
BALANCE OF PLANT
SUB-TOTAL |  | 0
INSURANCE @ 0.25% |  | 0
FREIGHT @ 1% |  | 0
TOTAL |  | 0

## GT schd cost(6B) (hidden)
0xGE-Frame 6B GT Scheduled Maintenance Cost
YEAR |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Subtotal
LABOR |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NEW PARTS |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Unit Price | Initial SP
FUEL NOZZLES | 13 |  | 2: 26 | 26
CROSSFIRE TUBES | 10.5 |  | 2: 21 | 21
COMBUSTION LINERS | 87 |  | 2: 87 | 87
TRANSITION PIECES | 127 |  | 2: 127 | 127
1ST STAGE BUCKETS | 375 |  | 3: 750 | 750
2ND STAGE BUCKETS | 275 |  | 3: 275 | 275
3RD STAGE BUCKETS | 270 |  | 3: 270 | 270
1ST STAGE SHROUDS | 75 |  | 3: 75 | 75
2ND STAGE SHROUDS | 65 |  | 3: 130 | 130
3RD STAGE SHROUDS | 40 |  | 3: 40 | 40
1ST STAGE NOZZLES | 315 |  | 3: 315 | 315
2ND STAGE NOZZLES | 370 | [21 empty] | 0
3RD STAGE NOZZLES | 325 | [21 empty] | 0
Renewables--CI | 34 | [21 empty] | 0
Renewables--HGP | 44 | [21 empty] | 0
Renewables--Major | 162 | [21 empty] | 0
Sub-Total Parts |  | 0 | 0 | 261 | 1855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2116
Parts Discount | 10% | 0 | 0 | 234.9 | 1669.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1904.4
Total Parts(w freight) | 3% | 0 | 0 | 241.947 | 1719.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1961.532
REPAIR COST |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Repair Price
FUEL NOZZLES | 8 | 0 | [20 empty] | 0
CROSSFIRE TUBES | 2 | [21 empty] | 0
COMBUSTION LINERS | 14.575 | [21 empty] | 0
TRANSITION PIECES | 20.4 | [21 empty] | 0
1ST STAGE BUCKETS | 86.4 | [21 empty] | 0
2ND STAGE BUCKETS | 39.84 | [21 empty] | 0
3RD STAGE BUCKETS | 42.13 | [21 empty] | 0
1ST STAGE SHROUDS | 15.6 | [21 empty] | 0
2ND STAGE SHROUDS | 11 | [21 empty] | 0
3RD STAGE SHROUDS | 12.9 | [21 empty] | 0
1ST STAGE NOZZLES | 65.5 | [21 empty] | 0
2ND STAGE NOZZLES | 33 |  | 3: 33 | 33
3RD STAGE NOZZLES | 25.07 | [21 empty] | 0
Repairs (w discunt) | 2% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Repairs (w freight) | 1% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRAND TOTAL (Parts,labor,& Repairs) |  |  | 0 | 241.947 | 1719.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1961.532

## rotation(6B) (hidden)
Information Enter
Spare Parts Rotation Plan | [21 empty] | GE-7EA-H-V0 | Phase 1 | Phase2 |  | Base On
Year |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Operating Years | 20 | 0
Hours |  | 8322 | 16644 | 24966 | 33288 | 41610 | 49932 | 58254 | 66576 | 74898 | 83220 | 91542 | 99864 | 108186 | 116508 | 124830 | 133152 | 141474 | 149796 | 158118 | 166440 | EOH or EOS per year | 8322 | 8000 |  |  |  | 1
[22 empty] | Number of units | 0
minor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | minor interval | 12000
HGP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HGP interval | 24000
Major | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Major interval | 48000
minor
HGP
Major
[22 empty] | Parts' Name | Repair Interval | Replace / Repair Interval | Spare part Sets for rotation | Initial Spare part sets | Maint. Cost
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL NOZZLES | 12000 | 3 | 2 | 0 | 26
BUY |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CROSSFIRE TUBES | 12000 | 3 | 2 | 0 | 21
BUY |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMBUSTION LINERS | 12000 | 5 | 1 | 0 | 87
BUY |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRANSITION PIECES | 12000 | 6 | 1 | 0 | 127
BUY |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1ST STAGE BUCKETS | 24000 | 2 | 2 | 0 | 750
BUY |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2ND STAGE BUCKETS | 24000 | 3 | 1 | 0 | 275
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3RD STAGE BUCKETS | 24000 | 3 | 1 | 0 | 270
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1ST STAGE SHROUDS | 24000 | 2 | 1 | 0 | 75
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2ND STAGE SHROUDS | 24000 | 3 | 2 | 0 | 130
BUY |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3RD STAGE SHROUDS | 24000 | 3 | 1 | 0 | 40
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1ST STAGE NOZZLES | 24000 | 3 | 1 | 0 | 315
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2ND STAGE NOZZLES | 24000 | 3 | 1 | 0 | 33
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3RD STAGE NOZZLES | 24000 | 3 | 1 | 0 | 0
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EOH
EOS

## GTDB(6B) (hidden)
Gas Turbine Scheduled Maintenance Data Base
Data Base ID | GE-7EA-H-V0
GT TYPE | GE-Frame 6B
Date of Data Base Updated | 2000-03-15
Updated By | RB
| Interval (EOH) | Labor Cost (k$) | Consumables (K$) |  |  |  | Interval (EOS)
Combustion Inspection | 12000 | 45.744 | 34 |  | 45744 | 34000 | 1200
HGP Inspection | 24000 | 84.124 | 44 |  | 84124 | 44000 | 1200
Major maintenance | 48000 | 178.908 | 162 |  | 178908 | 162000 | 2400
Name of Parts | Repair Interval (H) | Replace interval | price of repair (K$) | Price of Replace (K$) |  |  | Repare on starts | Replace/Repair
FUEL NOZZLES | 12000 | 3 | 8 | 13 | 8000 | 13000 | 1200 | 3
CROSSFIRE TUBES | 12000 | 3 | 2 | 10.5 | 2000 | 10500 | 1200 | 3
COMBUSTION LINERS | 12000 | 5 | 14.575 | 87 | 14575 | 87000 | 1200 | 5
TRANSITION PIECES | 12000 | 6 | 20.4 | 127 | 20400 | 127000 | 1200 | 6
1ST STAGE BUCKETS | 24000 | 2 | 86.4 | 375 | 86400 | 375000 | 1200 | 3
2ND STAGE BUCKETS | 24000 | 3 | 39.84 | 275 | 39840 | 275000 | 1200 | 4
3RD STAGE BUCKETS | 24000 | 3 | 42.13 | 270 | 42130 | 270000 | 1200 | 4
1ST STAGE SHROUDS | 24000 | 2 | 15.6 | 75 | 15600 | 75000 | 1200 | 2
2ND STAGE SHROUDS | 24000 | 3 | 11 | 65 | 11000 | 65000 | 1200 | 4
3RD STAGE SHROUDS | 24000 | 3 | 12.9 | 40 | 12900 | 40000 | 1200 | 4
1ST STAGE NOZZLES | 24000 | 3 | 65.5 | 315 | 65500 | 315000 | 1200 | 3
2ND STAGE NOZZLES | 24000 | 3 | 33 | 370 | 33000 | 37000000% | 1200 | 3
3RD STAGE NOZZLES | 24000 | 3 | 25.07 | 325 | 25070 | 325000 | 1200 | 3
COMB. CONSUMABLES |  |  |  | 34 |  | 34000 | 1200
HGP CONSUMABLES |  |  |  | 44 |  | 44000 | 1200
MAJOR CONSUMABLES |  |  |  | 162 |  | 162000 | 1200
GEN CONSUMABLES |  |  |  | 11.07 |  | 11070 | 1200
Remark:

## GT schd cost(7FA)
2xGE-Frame 7FA GT Scheduled Maintenance Cost
YEAR |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Subtotal
UNIT 1 |  |  | C | C | H | C | C | M | C | C | H | C | C | M | C | C | H | C | C | M | C | C
UNIT 2 |  |  | C | C | H | C | C | M | C | C | H | C | C | M | C | C | H | C | C | M | C | C
UNIT 3
UNIT 4
LABOR |  |  | 115.6 | 115.6 | 344.76 | 115.6 | 115.6 | 861.9 | 115.6 | 115.6 | 344.76 | 115.6 | 115.6 | 861.9 | 115.6 | 115.6 | 344.76 | 115.6 | 115.6 | 861.9 | 115.6 | 115.6 | 5238.38
NEW PARTS |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Unit Price | Initial SP
Combustion Liners | 573.256 | 573.256 | 7: 1146.512; 8: 573.256; 14: 573.256; 15: 1146.512 | 3439.536
Transition Pieces | 1246.131 | 1246.131 | 7: 2492.262; 8: 1246.131; 14: 1246.131; 15: 2492.262 | 7476.786
Fuel Nozzles | 1297.423 | 1297.423 | 4: 2594.846; 5: 1297.423; 8: 1297.423; 9: 2594.846; 13: 2594.846; 14: 1297.423; 17: 1297.423; 18: 2594.846 | 15569.076
Stage 1 Nozzles | 1604.924 | 1604.924 | 6: 1604.924; 9: 3209.848; 15: 1604.924; 18: 3209.848 | 9629.544
Stage 2 Nozzles | 1540.727 |  | 3: 1540.727; 12: 3081.454; 15: 1540.727 | 6162.908
Stage 3 Nozzles | 1467.168 |  | 3: 1467.168; 12: 2934.336; 15: 1467.168 | 5868.672
Stage 1 Buckets | 3214.992 | 3214.992 | 12: 6429.984; 15: 3214.992 | 9644.976
Stage 2 Buckets | 1977.593 |  | 3: 1977.593; 6: 1977.593; 9: 3955.186; 15: 1977.593; 18: 3955.186 | 13843.151
Stage 3 Buckets | 2251.78 |  | 3: 4503.56; 6: 4503.56; 9: 4503.56; 12: 4503.56; 15: 4503.56; 18: 4503.56 | 27021.36
Row 1 Support Ring | 44.516 |  | 3: 44.516; 6: 44.516; 9: 89.032; 15: 44.516; 18: 89.032 | 311.612
1st Stage Shroud Blocks | 721.443 | 721.443 | 12: 1442.886; 15: 721.443 | 2164.329
2nd Stage Shroud Blocks | 487.958 |  | 3: 487.958; 12: 975.916; 15: 487.958 | 1951.832
3rd Stage Shroud Blocks | 417.479 |  | 3: 417.479; 12: 834.958; 15: 417.479 | 1669.916
Renewables--CI | 54.254 |  | 108.508 | 108.508 |  | 108.508 | 108.508 |  | 108.508 | 108.508 |  | 108.508 | 108.508 |  | 108.508 | 108.508 |  | 108.508 | 108.508 |  | 108.508 | 108.508 | 1519.112
Renewables--HGP | 62.032 |  | 3: 124.064; 9: 124.064; 15: 124.064 | 372.192
Renewables--Major | 209.215 |  | 6: 418.43; 12: 418.43; 18: 418.43 | 1255.29
Sub-Total Parts |  | 8658.169 | 108.508 | 108.508 | 10563.065 | 2703.354 | 1405.931 | 8549.023 | 3747.282 | 3225.318 | 14476.536 | 108.508 | 108.508 | 20621.524 | 2703.354 | 3225.318 | 19743.198 | 108.508 | 1405.931 | 14770.902 | 108.508 | 108.508 | 107900.292
Parts Discount | 10% | 7792.3521 | 97.6572 | 97.6572 | 9506.7585 | 2433.0186 | 1265.3379 | 7694.1207 | 3372.5538 | 2902.7862 | 13028.8824 | 97.6572 | 97.6572 | 18559.3716 | 2433.0186 | 2902.7862 | 17768.8782 | 97.6572 | 1265.3379 | 13293.8118 | 97.6572 | 97.6572 | 97110.2628
Total Parts(w freight) | 3% | 8026.1227 | 100.5869 | 100.5869 | 9791.9613 | 2506.0092 | 1303.298 | 7924.9443 | 3473.7304 | 2989.8698 | 13419.7489 | 100.5869 | 100.5869 | 19116.1527 | 2506.0092 | 2989.8698 | 18301.9445 | 100.5869 | 1303.298 | 13692.6262 | 100.5869 | 100.5869 | 100023.5707
REPAIR COST |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
GAS TURBINE | Repair Price
Combustion Liners | 191.58 | 0 | 383.16 | 383.16 | 383.16 | 383.16 | 383.16 | 383.16 |  | 191.58 | 383.16 | 383.16 | 383.16 | 383.16 | 383.16 | 191.58 |  | 383.16 | 383.16 | 383.16 | 383.16 | 383.16 | 6513.72
Transition Pieces | 196.73 |  | 393.46 | 393.46 | 393.46 | 393.46 | 393.46 | 393.46 |  | 196.73 | 393.46 | 393.46 | 393.46 | 393.46 | 393.46 | 196.73 |  | 393.46 | 393.46 | 393.46 | 393.46 | 393.46 | 6688.82
Fuel Nozzles | 73.13 |  | 146.26 | 146.26 | 146.26 |  | 73.13 | 146.26 | 146.26 | 73.13 |  | 146.26 | 146.26 | 146.26 |  | 73.13 | 146.26 | 146.26 | 73.13 |  | 146.26 | 146.26 | 2047.64
Stage 1 Nozzles | 400.67 |  | 3: 801.34; 6: 400.67; 12: 801.34; 15: 400.67 | 2404.02
Stage 2 Nozzles | 306.94 |  | 3: 613.88; 6: 613.88; 9: 613.88; 15: 306.94; 18: 613.88 | 2762.46
Stage 3 Nozzles | 144.2 |  | 3: 288.4; 6: 288.4; 9: 288.4; 15: 144.2; 18: 288.4 | 1297.8
Stage 1 Buckets | 973.762 |  | 3: 1947.524; 6: 1947.524; 9: 1947.524; 15: 973.762; 18: 1947.524 | 8763.858
Stage 2 Buckets | 370.8 |  | 3: 741.6; 6: 370.8; 12: 741.6; 15: 370.8 | 2224.8
Stage 3 Buckets | 422.1646 | [21 empty] | 0
Row 1 Support Ring | 23.175 |  | 3: 46.35; 6: 23.175; 12: 46.35; 15: 23.175 | 139.05
1st Stage Shroud Blocks | 123.6 |  | 3: 247.2; 6: 247.2; 9: 247.2; 15: 123.6; 18: 247.2 | 1112.4
2nd Stage Shroud Blocks | 123.6 |  | 3: 247.2; 6: 247.2; 9: 247.2; 15: 123.6; 18: 247.2 | 1112.4
3rd Stage Shroud Blocks | 123.6 |  | 3: 247.2; 6: 247.2; 9: 247.2; 15: 123.6; 18: 247.2 | 1112.4
Repairs (w discunt) | 2% |  | 904.4224 | 904.4224 | 5981.5025 | 761.0876 | 832.755 | 5202.7504 | 143.3348 | 452.2112 | 4280.6635 | 904.4224 | 904.4224 | 2461.9266 | 761.0876 | 452.2112 | 2681.8749 | 904.4224 | 832.755 | 4280.6635 | 904.4224 | 904.4224 | 35455.7806
Total Repairs (w freight) | 1% |  | 913.4666 | 913.4666 | 6041.3175 | 768.6985 | 841.0825 | 5254.7779 | 144.7681 | 456.7333 | 4323.4702 | 913.4666 | 913.4666 | 2486.5459 | 768.6985 | 456.7333 | 2708.6936 | 913.4666 | 841.0825 | 4323.4702 | 913.4666 | 913.4666 | 35810.3384
GRAND TOTAL (Parts,labor,& Repairs) |  |  | 1129.6535 | 1129.6535 | 16178.0388 | 3390.3076 | 2259.9806 | 14041.6222 | 3734.0986 | 3562.2031 | 18087.979 | 1129.6535 | 1129.6535 | 22464.5986 | 3390.3076 | 3562.2031 | 21355.3982 | 1129.6535 | 2259.9806 | 18877.9963 | 1129.6535 | 1129.6535 | 141072.2891

## rotation(7FA) (hidden)
Information Enter
Spare Parts Rotation Plan | [21 empty] | GE-7FA-H-V0 | Phase 1 | Phase2 |  | Base On
Year |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Operating Years | 20 | 0
Hours |  | 8322 | 16644 | 24966 | 33288 | 41610 | 49932 | 58254 | 66576 | 74898 | 83220 | 91542 | 99864 | 108186 | 116508 | 124830 | 133152 | 141474 | 149796 | 158118 | 166440 | EOH or EOS per year | 8322 | 8000 |  |  |  | 1
[22 empty] | Number of units | 2
minor | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | minor interval | 8000
HGP | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | HGP interval | 24000
Major | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | Major interval | 48000
minor | bar: 1 to 2; 4 to 5; 7 to 8; 10 to 11; 13 to 14; 16 to 17; 19 to 20
HGP | bar: 3; 9; 15
Major | bar: 6; 12; 18
[22 empty] | Parts' Name | Repair Interval | Replace / Repair Interval | Spare part Sets for rotation | Initial Spare part sets | Maint. Cost
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2
REPAIR |  | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 2 | 2 | 2 | 2 | 2 | Combustion Liners | 8000 | 5 | 1 | 1 | 9953.256
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2
REPAIR |  | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 2 | 2 | 2 | 2 | 2 | Transition Pieces | 8000 | 5 | 1 | 1 | 14165.606
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
REPAIR |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | 0 | #REF!
BUY |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Round of Buy |  | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4
REPAIR |  | 2 | 2 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 2 | 2 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | 2 | 2 | Fuel Nozzles | 8000 | 3 | 1 | 1 | 17616.716
BUY |  | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 1 | 2 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Stage 1 Nozzles | 24000 | 2 | 1 | 1 | 12033.564
BUY |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | Stage 2 Nozzles | 24000 | 3 | 1 | 0 | 8925.368
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | Stage 3 Nozzles | 24000 | 3 | 1 | 0 | 7166.472
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | Stage 1 Buckets | 24000 | 3 | 1 | 1 | 18408.834
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Stage 2 Buckets | 24000 | 2 | 1 | 0 | 16067.951
BUY |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0
Round of Buy |  | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
REPAIR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Stage 3 Buckets | 24000 | 1 | 1 | 0 | 27021.36
BUY |  | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Row 1 Support Ring | 24000 | 2 | 1 | 0 | 450.662
BUY |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 1st Stage Shroud Blocks | 24000 | 3 | 1 | 1 | 3276.729
BUY |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 2nd Stage Shroud Blocks | 24000 | 3 | 1 | 0 | 3064.232
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Round of Buy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
REPAIR |  | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 3rd Stage Shroud Blocks | 24000 | 3 | 1 | 0 | 2782.316
BUY |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
EOH
EOS

## GTDB(7FA) (hidden)
Gas Turbine Scheduled Maintenance Data Base
Data Base ID | GE-7FA-H-V0
GT TYPE | GE-Frame 7FA
Date of Data Base Updated | 2000-03-15
Updated By | RB
| Interval (EOH) | Labor Cost (k$) | Consumables (K$) |  | Interval (EOS)
Combustion Inspection | 8000 | 57.8 | 54.254 |  | 400
HGP Inspection | 24000 | 172.38 | 62.032 |  | 900
Major maintenance | 48000 | 430.95 | 209.215 |  | 2400
Name of Parts | Repair Interval (H) | Replace interval | price of repair (K$) | Price of Replace (K$) | Repare on starts | Replace/Repair
Combustion Liners | 8000 | 5 | 191.58 | 573.256 | 400 | 5
Transition Pieces | 8000 | 5 | 196.73 | 1246.131 | 400 | 6
Fuel Nozzles | 8000 | 3 | 73.13 | 1297.423 | 400 | 3
Stage 1 Nozzles | 24000 | 2 | 400.67 | 1604.924 | 900 | 3
Stage 2 Nozzles | 24000 | 3 | 306.94 | 1540.727 | 900 | 3
Stage 3 Nozzles | 24000 | 3 | 144.2 | 1467.168 | 900 | 3
Stage 1 Buckets | 24000 | 3 | 973.762 | 3214.992 | 900 | 3
Stage 2 Buckets | 24000 | 2 | 370.8 | 1977.593 | 900 | 4
Stage 3 Buckets | 24000 | 1 | 422.1646 | 2251.78 | 900 | 4
Row 1 Support Ring | 24000 | 2 | 23.175 | 44.516 | 900 | 3
1st Stage Shroud Blocks | 24000 | 3 | 123.6 | 721.443 | 900 | 2
2nd Stage Shroud Blocks | 24000 | 3 | 123.6 | 487.958 | 900 | 4
3rd Stage Shroud Blocks | 24000 | 3 | 123.6 | 417.479 | 900 | 4
Remark: