## COVER
Desert Sky
MONTHLY REPORT
FOR
April '02
**ALL TIMES ARE GMT**

## WTG Down
DESERT SKY
SIGNIFICANT WTG DOWN TIME
Month: | April '02 |  |  |  | Reason: F=fault, U=unscheduled maint. S= scheduled maint. C=curtail O=other.
WTG # | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
105 | 2002-04-01 | 0000 | 2002-04-02 | 1300 | 37 | F | 3K1 coil shorted in hub.
31 | 2002-04-01 | 0700 | 2002-04-02 | 1730 | 34.5 | F | Axis 3 lost zero/safety chain
43 | 2002-04-01 | 1700 | 2002-04-02 | 1200 | 19 | F | Motor protection top box
4 | 2002-04-01 | 0000 | 2002-04-02 | 1130 | 35.5 | F | Motor protection top box/ratio gen to rotor speed
70 | 2002-04-01 | 0000 | 2002-04-05 | 1500 | 111 | F | Top generator fan motor shaft broke.
100 | 2002-04-01 | 1430 | 2002-04-03 | 0930 | 43 | F | MS-3 failed
35 | 2002-04-02 | 2300 | 2002-04-03 | 1600 | 17 | F | Axis 3 lost zero.
69 | 2002-04-03 | 1630 | 2002-04-04 | 0930 | 17 | F | Feedback CCU. Loose U/V coil microswitch
89 | 2002-04-03 | 1600 | 2002-04-04 | 1000 | 18 | F | Mains failure. High impedance on L1.
92 | 2002-04-03 | 1600 | 2002-04-04 | 1030 | 18.5 | F | Lost commissioning due to defective SEG K-5 relay
70 | 2002-04-05 | 1500 | 2002-04-22 | 1200 | 405 | F | Replaced bad VEM generator
89 | 2002-04-07 | 1730 | 2002-04-09 | 1200 | 42.5 | F | VEM front fan motor went phase to phase
100 | 2002-04-07 | 0400 | 2002-04-08 | 1500 | 35 | F | MS-3 failed
62 | 2002-04-08 | 0400 | 2002-04-09 | 800 | 28 | F | MS-3 failed
40 | 2002-04-08 | 1500 | 2002-04-09 | 1300 | 22 | F | MS-3 failed
107 | 2002-04-14 | 1430 | 2002-04-15 | 830 | 18 | F | Lost commissioning due to defective SEG K-5 relay
34 | 2002-04-14 | 1130 | 2002-04-15 | 1530 | 28 | F | No activity can bus CCU
106 | 2002-04-14 | 1300 | 2002-04-15 | 1500 | 26 | F | Lost commissioning due to defective SEG K-5 relay
77 | 2002-04-11 | 2100 | 2002-04-17 | 930 | 132.5 | F | Replaced bad VEM generator
121 | 2002-04-18 | 1400 | 2002-04-22 | 1700 | 99 | F | Replaced front VEM fan motor (bad bearing)
67 | 2002-04-01 | 0000 | 2002-04-29 | 200 | 674 | F | Tower cables burned. Replaced cables
105 | 2002-04-29 | 2200 | 2002-04-30 | 1700 | 19 | F | 3K2 contacts defective in hub.
59 | 2002-04-28 | 2030 | 2002-04-30 | 1300 | 40.5 | F | Blade closeout fell out and broke both limitswitches
53 | 2002-04-13 | 0800 | 2002-04-15 | 1630 | 56.5 | O | Engineering was repairing some instrumentation
53 | 2002-04-27 | 1200 | 2002-04-29 | 1815 | 54.25 | O | Engineering was repairing some instrumentation
39 | 2002-04-27 | 0200 | 2002-04-29 | 1200 | 58 | F | SEG had bad CSC HUR
62 | 2002-04-14 | 0430 | 2002-04-16 | 1330 | 57 | F | Replaced broken Loher generator j-box mounting bolts
107 | 2002-04-14 | 1730 | 2002-04-15 | 1030 | 17 | F | Lost commissioning due to defective SEG K-5 relay

## GRID
DESERT SKY
GRID VARIANCE
Chargeable to: A=AEP, N=Force Majeure, E=Enron, T= TXU
Month: | April '02 |  |  | Reason: U=unscheduled outage, S= scheduled outage, F=fluctuation
Charge | Date off | Time off | Date on | Time on | Hrs. | Reason | Comments
N/A | N/A | N/A | N/A | N/A | N/A | N/A | No grid downtime

## WEATHER
DESERT SKY
WEATHER EVENTS
Month: | April '02
Date | Time | Event | Comments
N/A | N/A | N/A | No weather events

## RECALL
DESERT SKY
CREW CALL-OUTS
Month: | April '02
Date | Time | Who | Reason
N/A | N/A | N/A | No call-outs

## PARTS
DESERT SKY
PARTS USAGE
Month: | April '02
Date | WTG # | EW Part # | Description | Qty. | Comments
2002-04-01 | 23 | UX56137094800 | Fiber Optic Cable | 1
2002-04-01 | 35 | UX59901000128 | Pitch Encoder | 1
2002-04-01 | 4 | T56031019947 | HUR CONTROLLER | 1
2002-04-01 | 78 |  | 1026 Vibration Monitor | 1
2002-04-01 | 82 | T56604010213 | auxilliary relay | 1
2002-04-01 | 68 | T56604031882 | timing relay | 3
2002-04-01 | 59 | UX59901000004 | close coil 110-120v | 1
2002-04-01 | 59 | UX59901000008 | UV trip 110-120v | 1
2002-04-01 | 59 | UX56201000004 | Switch Assembly | 1
2002-04-01 | 68 | T5602069718 | Interference suppression device | 1
2002-04-01 | 70 |  | fan motor for Vem Generator | 1
2002-04-01 | 70 |  | fan for Vem Generator | 1
2002-04-01 | 70 |  | Key Way | 1
2002-04-02 | 35 | T5622503810 | Positioning Controller | 1
2002-04-02 | 35 | UX59901000104 | Oil level indicator | 1
2002-04-03 | 35 | T5622503810 | Positioning Controller | 1
2002-04-03 | 85 | T56031155076 | Skiip 310 RAC | 1
2002-04-03 | 35 | T56225811954 | DC rotational speed regulator | 1
2002-04-03 | 35 | UX56205000810 | FAA light bulb | 1
2002-04-03 | 62 | UX59901000029 | 50 A FUSE | 2
2002-04-03 | 85 | T56031020178 | Ignition unit with fiber optic control | 1
2002-04-03 | 14 | T56031020396 | MS3 | 1
2002-04-03 | 84 | UX56201000004 | Switch Assembly | 1
2002-04-03 | 4 | T56225102700 | Battery Charger 166v | 1
2002-04-03 | 4 | T56137899700 | PLC digital input 32x | 1
2002-04-03 | 105 | T56602209714 | Relay | 1
2002-04-03 | 31 | T56622120013 | Roller Lever wh/roller | 1
2002-04-03 | 31 | T56622100005 | drive for rotational axis | 1
2002-04-03 | 31 | T56622110001 | 90 degree limit switch | 1
2002-04-05 | 70 | T85121221000 | SIKAFLEX | 1
2002-04-05 | 64 | T56779400916 | hub light | 1
2002-04-05 | 17 | UX59901000079 | PC card w/8MB Memory,Bachmann | 1
2002-04-05 | 35 | UX59901000128 | Pitch Motor Encoder | 1
2002-04-05 | 92 | T56604010213 | auxilliary relay | 1
2002-04-05 | 89 | T56604010213 | auxilliary relay | 1
2002-04-05 | 30 | T56031020396 | MS3 | 1
2002-04-05 | 100 | T56031020396 | MS3 | 1
2002-04-05 | 106 | T56031020396 | MS3 | 1
2002-04-05 | 117 | T56031020396 | MS3 | 1
2002-04-05 | 70 | UX56205000810 | bulb, FAA L810 | 1
2002-04-08 | 17 | T56137909700 | PLC analog In/Out | 1
2002-04-08 | 17 | T56137909700 | PLC analog In/Out | 1
2002-04-08 | 14 | T83706043128 | Wind Vane | 1
2002-04-08 | 118 | T83706043128 | Wind Vane | 1
2002-04-08 | 57 | T56114788948 | Over protection for USV MT-2PE/S 120AC-0LA | 1
2002-04-08 | 57 | T56114798844 | Overvoltage protection 230V | 6
2002-04-08 | 56 | T56114830540 | Overvoltage protection N->PE F-MS as-TT | 2
2002-04-08 | 17 | T56137965000 | PLC Com-interface Visualisation | 1
2002-04-08 | 17 | T56137932300 | PLC power supply Bachmann | 1
2002-04-08 | 17 | T56137049700 | PLC digital input 32x | 1
2002-04-08 | 17 | T56137049500 | FM211 | 1
2002-04-08 | 17 | T56137900400 | DO216 | 1
2002-04-09 | 67 | UX56100901063 | Ground cable | 63ft
2002-04-11 | 70 |  | VEM Generator | 1
2002-04-12 | 77 |  | VEM Generator | 1
2002-04-16 | 20 | T56031020396 | MS3 | 1
2002-04-16 | 67 | UX59901000060 | Terminal Block SAK 6/35 | 2
2002-04-16 | 67 | UX59901000056 | Terminal Block Sak 2.5/35 | 1
2002-04-16 | 106 | UX59901000008 | UV trip 110-120v | 1
2002-04-16 | 67 | UX59901000206 | 1x output filter D/DT | 1
2002-04-16 | 67 | UX59901000215 | Middle cable for 1x output filter D/DT | 1
2002-04-16 |  |  | Logitech Mouse | 5
2002-04-16 | 114 | T56836060333 | Computer, 60Hz, TZ1.5 | 1
2002-04-16 | 117 | T56836060333 | Computer, 60Hz, TZ1.5 | 1
2002-04-16 | 67 | T56836060333 | Computer, 60Hz, TZ1.5 | 1
2002-04-16 | DVAR | T56836060333 | Computer, 60Hz, TZ1.5 | 1
2002-04-18 | 114 | T56836060333 | Computer, 60Hz, TZ1.5 | 1
2002-04-18 | 115 | UX59901000128 | Pitch Motor Encoder | 1
2002-04-18 | 91 | T56137965000 | PLC Com-interface Visualisation | 1
2002-04-18 | 80 | T56870000204 | Operation Panel | 1
2002-04-18 | 5 | T56137991800 | PLC Com 1-4 interface | 1
2002-04-18 | 79 | T56604010213 | auxilliary relay | 1
2002-04-18 | 70 |  | Shrink element for rotor on VEM generator | 1
2002-04-09 | 89 |  | Front Fan Motor for VEM generator | 1
2002-04-19 | 67 | T56470009000 | Kallems Grips for 750 cable | 15
2002-04-19 | 121 |  | Front Fan Motor for VEM generator | 1
2002-04-19 | 105 |  | Front Fan Motor for VEM generator | 1
2002-04-22 | 121 | UX74182870785 | Plenum | 1
2002-04-22 | 91 | UX74182715870 | Plenum | 1
2002-04-22 | 21 |  | 8" oil level indicator | 1
2002-04-26 | 67 | T56031020396 | MS3 | 1
2002-04-26 | 67 | UX69001300400 | Tubing, cold shrink | 150
2002-04-26 | 67 | T56260102001 | Rotor-overspeed monitor | 1
2002-04-26 | 67 | T56137070900 | PLC INC 1 INC 2 | 1
2002-04-26 | 67 | UX59901000145 | PLC "CAN"BUS MASTER | 1
2002-04-26 | 67 | T56137965000 | PLC Com-interface Visualisation | 1
2002-04-26 | 67 | T56111000005 | twist cable | 1
2002-04-26 | 121 | T56225038310 | Positioning Controller | 1
2002-04-26 | 114 | UX59901000106 | Nut M24 | 1
2002-04-26 | 67 | T56137049800 | PLC Fast Bus Slave | 1
2002-04-26 | 67 | T56137049800 | PLC Fast Bus Slave | 1
2002-04-26 | 41 | T56360800000 | rotational transducer | 1
2002-04-26 | 67 | UX59901000103 | Oil site glass | 1
2002-04-26 | 78 | T56137991800 | PLC Com 1-4 interface | 2
2002-04-26 | 78 | T56225038310 | Positioning Controller | 1
2002-04-26 | 121 | 901150 | UPS bracket | 1
2002-04-26 | 67 | T56137899700 | PLC digital input 32x | 1
2002-04-26 | 8 | T56151800005 | UPS | 1
2002-04-26 | 9 | T56151800005 | UPS | 1
2002-04-26 | 14 | T56151800005 | UPS | 1
2002-04-26 | 3 | 901307 | UPS bracket | 2
2002-04-26 | 4 | 901307 | UPS bracket | 2
2002-04-26 | 8 | 901307 | UPS bracket | 2
2002-04-26 | 9 | 901307 | UPS bracket | 2
2002-04-26 | 14 | 901307 | UPS bracket | 2
2002-04-26 | 67 | UX59901000128 | Pitch Motor Encoder | 3
2002-04-26 | 20 | T56225038310 | Positioning Controller | 1
2002-04-26 | 67 | UX56400000004 | IC, F/O RECEIVER.HP | 11
2002-04-26 | 108 | T56031020396 | MS3 | 1
2002-04-26 | 108 | T56031027722 | Overvoltage arrestor | 3
2002-04-26 | 64 | T56031020396 | MS3 | 1
2002-04-26 | 68 | T56733952350 | Interface realy | 2
2002-04-26 | 55 | T56031020396 | MS3 | 1
2002-04-26 | 80 | Y56604010213 | auxilliary relay | 1
2002-04-26 | 69 | UX56750030070 | Sensor, Prox, 7M Cable | 1
2002-04-26 | 3 | T56151800005 | UPS | 1
2002-04-26 | 4 | T56151800005 | UPS | 1
2002-04-28 | 47 | 901307 | UPS bracket | 2
2002-04-28 | 46 | 901307 | UPS bracket | 2
2002-04-28 | 45 | 901307 | UPS bracket | 2
2002-04-28 | 44 | 901307 | UPS bracket | 2
2002-04-28 | 43 | 901307 | UPS bracket | 2
2002-04-28 | 42 | 901307 | UPS bracket | 2
2002-04-28 | 41 | 901307 | UPS bracket | 2
2002-04-28 | 40 | 901307 | UPS bracket | 2
2002-04-28 | 39 | 901307 | UPS bracket | 2
2002-04-28 | 38 | 901307 | UPS bracket | 2
2002-04-28 | 47 | T56151800005 | UPS | 1
2002-04-28 | 46 | T56151800005 | UPS | 1
2002-04-28 | 45 | T56151800005 | UPS | 1
2002-04-28 | 44 | T56151800005 | UPS | 1
2002-04-28 | 43 | T56151800005 | UPS | 1
2002-04-28 | 42 | T56151800005 | UPS | 1
2002-04-28 | 41 | T56151800005 | UPS | 1
2002-04-28 | 40 | T56151800005 | UPS | 1
2002-04-28 | 39 | T56151800005 | UPS | 1
2002-04-28 | 38 | T56151800005 | UPS | 1
2002-04-28 | 86 | T83701043518 | anemometer/w heating anemometer/wind speed | 1
2002-04-28 | 67 | T56031155076 | IGBT | 1
2002-04-28 | 49 | T56151800005 | UPS | 1
2002-04-28 | 50 | T56151800005 | UPS | 1
2002-04-28 | 51 | T56151800005 | UPS | 1
2002-04-28 | 52 | T56151800005 | UPS | 1
2002-04-28 | 53 | T56151800005 | UPS | 1
2002-04-28 | 54 | T56151800005 | UPS | 1
2002-04-28 | 55 | T56151800005 | UPS | 1
2002-04-28 | 56 | T56151800005 | UPS | 1
2002-04-28 | 57 | T56151800005 | UPS | 1
2002-04-28 | 58 | T56151800005 | UPS | 1
2002-04-28 | 59 | T56151800005 | UPS | 1
2002-04-28 | 106 | T56151800005 | UPS | 1
2002-04-28 | 49 | 901307 | UPS bracket | 2
2002-04-28 | 50 | 901307 | UPS bracket | 2
2002-04-28 | 51 | 901307 | UPS bracket | 2
2002-04-28 | 52 | 901307 | UPS bracket | 2
2002-04-28 | 53 | 901307 | UPS bracket | 2
2002-04-28 | 54 | 901307 | UPS bracket | 2
2002-04-28 | 55 | 901307 | UPS bracket | 2
2002-04-28 | 56 | 901307 | UPS bracket | 2
2002-04-28 | 57 | 901307 | UPS bracket | 2
2002-04-28 | 58 | 901307 | UPS bracket | 2
2002-04-28 | 59 | 901307 | UPS bracket | 2
2002-04-28 | 106 | 901307 | UPS bracket | 2
2002-04-29 | 34 | UX5990100016 | CSC HUR CAN BUS | 1
2002-04-30 | 67 | T56151800005 | UPS | 1
2002-04-30 | 68 | T56151800005 | UPS | 1
2002-04-30 | 69 | T56151800005 | UPS | 1
2002-04-30 | 67 | 901307 | UPS bracket | 2
2002-04-30 | 68 | 901307 | UPS bracket | 2
2002-04-30 | 69 | 901307 | UPS bracket | 2
2002-04-30 | 61 | T56151800005 | UPS | 1
2002-04-30 | 62 | T56151800005 | UPS | 1
2002-04-30 | 64 | T56151800005 | UPS | 1
2002-04-30 | 70 | T56151800005 | UPS | 1
2002-04-30 | 71 | T56151800005 | UPS | 1
2002-04-30 | 75 | T56151800005 | UPS | 1
2002-04-30 | 76 | T56151800005 | UPS | 1
2002-04-30 | 77 | T56151800005 | UPS | 1
2002-04-30 | 61 | 901307 | UPS bracket | 2
2002-04-30 | 62 | 901307 | UPS bracket | 2
2002-04-30 | 64 | 901307 | UPS bracket | 2
2002-04-30 | 75 | 901307 | UPS bracket | 2
2002-04-30 | 76 | 901307 | UPS bracket | 2
2002-04-30 | 77 | 901307 | UPS bracket | 2
2002-04-30 | 57 | T56031020396 | MS3 | 1
2002-04-30 | 59 | UX59901000035 | CC FUSE 5A T-D 600V | 2
2002-04-30 | 59 | T56114798844 | Overvoltage protection | 3
2002-04-30 | 59 | T56228690050 | Fuse 690v/50A | 3
2002-04-30 | 90 | 901307 | UPS bracket | 2
2002-04-30 | 91 | 901307 | UPS bracket | 2
2002-04-30 | 92 | 901307 | UPS bracket | 2
2002-04-30 | 93 | 901307 | UPS bracket | 2
2002-04-30 | 109 | 901307 | UPS bracket | 2
2002-04-30 | 90 | T56151800005 | UPS | 1
2002-04-30 | 91 | T56151800005 | UPS | 1
2002-04-30 | 92 | T56151800005 | UPS | 1
2002-04-30 | 93 | T56151800005 | UPS | 1
2002-04-30 | 109 | T56151800005 | UPS | 1

## LOW PRODUCERS
DESERT SKY
BOTTOM FIVE PRODUCERS
WTG | kW Hours | Sys. Avl | Mach. Avl | Line Avl | Reason

## CURTAILMENTS
DESERT SKY
CURTAILMENTS
Month: | April '02
WTG | Date off | Time off | Date on | Time on | Hours off | Name | CPS operator | Comments
1 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
2 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
3 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
24 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
5 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
7 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
8 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
9 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
27 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
25 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
17 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
18 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
19 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
20 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
21 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
22 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
43 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
44 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
45 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
46 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
47 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
49 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
50 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
51 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
52 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
53 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
54 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
55 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
56 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
57 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
59 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
28 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
29 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
30 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
31 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
32 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
120 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
109 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
108 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
107 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
106 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
104 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
103 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
102 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
100 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
96 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
93 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
92 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
91 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
90 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
89 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
88 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
87 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
86 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
85 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
84 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
83 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
82 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
81 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
80 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
79 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
78 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
77 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Bucky | CPS wanted 25MW on each line.
60 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
61 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
62 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
63 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
64 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
65 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
66 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
68 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
69 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
116 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
113 | 2002-04-01 | 1:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
33 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
34 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
35 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
36 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
37 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
38 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
39 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
41 | 2002-04-01 | 5:30 | 2002-04-01 | 14:00 |  | Bryan | Johnny | CPS wanted 25MW on each line.
1 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
2 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
3 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
5 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
7 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
8 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
13 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
14 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
17 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
18 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
19 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
21 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
22 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
23 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
24 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
25 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
26 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
29 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
96 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
102 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
103 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
104 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
106 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
107 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
108 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
109 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
113 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
115 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
116 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
117 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
118 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
119 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
120 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
121 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
122 | 2002-04-01 | 15:45 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
31 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
32 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
33 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
34 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
91 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
92 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
93 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
49 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
50 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
51 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
88 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
89 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
90 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
86 | 2002-04-01 | 15:50 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
52 | 2002-04-01 | 16:15 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
53 | 2002-04-01 | 16:15 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
60 | 2002-04-01 | 16:30 | 2002-04-01 | 21:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
59 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
57 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
56 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
55 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
54 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
53 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
52 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
51 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
50 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
49 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
47 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
46 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
45 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
44 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
39 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
38 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
37 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
36 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
35 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
34 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
33 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
32 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
29 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
28 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
26 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
25 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
24 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
23 | 2002-04-01 | 23:50 | 2002-04-02 | 2:30 |  | Bryan | Dole | CPS wanted 30MW on each line.
117 | 2002-04-01 | 23:50 | 2002-04-02 | 7:26 |  | Bryan | Dole | CPS wanted 30MW on each line.
118 | 2002-04-01 | 23:50 | 2002-04-02 | 7:26 |  | Bryan | Dole | CPS wanted 30MW on each line.
119 | 2002-04-01 | 23:50 | 2002-04-02 | 7:26 |  | Bryan | Dole | CPS wanted 30MW on each line.
121 | 2002-04-01 | 23:50 | 2002-04-02 | 7:26 |  | Bryan | Dole | CPS wanted 30MW on each line.
122 | 2002-04-01 | 23:50 | 2002-04-02 | 7:26 |  | Bryan | Dole | CPS wanted 30MW on each line.
1 | 2002-04-02 | 13:00 | 2002-04-02 | 19:45 |  | Jason | Johnny | CPS wanted 10MW on each line.
2 | 2002-04-02 | 13:00 | 2002-04-02 | 19:45 |  | Jason | Johnny | CPS wanted 10MW on each line.
3 | 2002-04-02 | 13:00 | 2002-04-02 | 19:45 |  | Jason | Johnny | CPS wanted 10MW on each line.
4 | 2002-04-02 | 13:00 | 2002-04-02 | 19:45 |  | Jason | Johnny | CPS wanted 10MW on each line.
5 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
7 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
8 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
9 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
13 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
14 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
15 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
17 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
18 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
19 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
20 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
21 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
22 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
23 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
24 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
25 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
26 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
27 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
28 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
29 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
30 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
32 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
33 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
34 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
36 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
37 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
39 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
40 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
41 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
42 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
43 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
44 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
45 | 2002-04-02 | 13:00 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
46 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
47 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
49 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
50 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
51 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
52 | 2002-04-02 | 13:20 | 2002-04-03 | 2:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
53 | 2002-04-02 | 13:20 | 2002-04-03 | 2:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
54 | 2002-04-02 | 13:20 | 2002-04-03 | 2:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
55 | 2002-04-02 | 13:20 | 2002-04-03 | 2:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
60 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
61 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
62 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
63 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
64 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
65 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
66 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
68 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
69 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
72 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
73 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
74 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
75 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
76 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
77 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
78 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
79 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
80 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
81 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
82 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
83 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
84 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
85 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
86 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
87 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
96 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
102 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
103 | 2002-04-02 | 13:20 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
104 | 2002-04-02 | 13:10 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
105 | 2002-04-02 | 13:10 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
106 | 2002-04-02 | 13:10 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
107 | 2002-04-02 | 13:10 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
108 | 2002-04-02 | 13:10 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
109 | 2002-04-02 | 13:10 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
113 | 2002-04-02 | 13:10 | 2002-04-02 | 21:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
117 | 2002-04-02 | 13:10 | 2002-04-03 | 2:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
118 | 2002-04-02 | 13:10 | 2002-04-03 | 2:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
119 | 2002-04-02 | 13:10 | 2002-04-03 | 2:00 |  | Jason | Johnny | CPS wanted 10MW on each line.
88 | 2002-04-04 | 19:45 | 2002-04-04 | 21:30 |  | Justin | Ben
89 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
90 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
91 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
92 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
93 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
96 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
100 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
102 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
103 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
104 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
105 | 2002-04-04 | 19:45 | 2002-04-04 | 22:15 |  | Justin | Ben
106 | 2002-04-04 | 19:45 | 2002-04-04 | 22:15 |  | Justin | Ben
107 | 2002-04-04 | 19:45 | 2002-04-04 | 22:15 |  | Justin | Ben
108 | 2002-04-04 | 19:45 | 2002-04-04 | 22:15 |  | Justin | Ben
109 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
113 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
114 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
115 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
116 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
117 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
118 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
119 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
120 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
121 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
122 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
85 | 2002-04-04 | 19:45 | 2002-04-04 | 21:30 |  | Justin | Ben
86 | 2002-04-04 | 19:45 | 2002-04-04 | 21:30 |  | Justin | Ben
87 | 2002-04-04 | 19:45 | 2002-04-04 | 21:30 |  | Justin | Ben
27 | 2002-04-04 | 19:45 | 2002-04-04 | 21:00 |  | Justin | Ben
28 | 2002-04-04 | 19:45 | 2002-04-04 | 21:00 |  | Justin | Ben
29 | 2002-04-04 | 19:45 | 2002-04-04 | 21:00 |  | Justin | Ben
30 | 2002-04-04 | 19:45 | 2002-04-04 | 21:00 |  | Justin | Ben
31 | 2002-04-04 | 19:45 | 2002-04-04 | 21:00 |  | Justin | Ben
32 | 2002-04-04 | 19:45 | 2002-04-04 | 21:00 |  | Justin | Ben
33 | 2002-04-04 | 19:45 | 2002-04-04 | 21:00 |  | Justin | Ben
34 | 2002-04-04 | 19:45 | 2002-04-04 | 21:00 |  | Justin | Ben
35 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
36 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
37 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
38 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
39 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
40 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
41 | 2002-04-04 | 19:45 | 2002-04-04 | 22:00 |  | Justin | Ben
42 | 2002-04-04 | 19:45 | 2002-04-04 | 22:15 |  | Justin | Ben
43 | 2002-04-04 | 19:45 | 2002-04-04 | 22:15 |  | Justin | Ben
44 | 2002-04-04 | 19:45 | 2002-04-04 | 22:15 |  | Justin | Ben
45 | 2002-04-04 | 19:45 | 2002-04-04 | 22:15 |  | Justin | Ben
46 | 2002-04-04 | 19:45 | 2002-04-05 | 5:00 |  | Justin | Ben
47 | 2002-04-04 | 19:45 | 2002-04-05 | 5:00 |  | Justin | Ben
49 | 2002-04-04 | 19:45 | 2002-04-05 | 5:00 |  | Justin | Ben
50 | 2002-04-04 | 19:45 | 2002-04-05 | 5:00 |  | Justin | Ben
51 | 2002-04-04 | 19:45 | 2002-04-05 | 5:00 |  | Justin | Ben
52 | 2002-04-04 | 19:45 | 2002-04-05 | 3:00 |  | Justin | Ben
53 | 2002-04-04 | 19:45 | 2002-04-05 | 3:00 |  | Justin | Ben
54 | 2002-04-04 | 19:45 | 2002-04-05 | 5:00 |  | Justin | Ben
55 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
56 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
57 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
58 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
59 | 2002-04-04 | 19:45 | 2002-04-05 | 6:15 |  | Justin | Ben
100 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
44 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
45 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
106 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
107 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
43 | 2002-04-04 | 22:30 | 2002-04-05 | 5:00 |  | Justin | Ben
42 | 2002-04-04 | 22:30 | 2002-04-05 | 5:00 |  | Justin | Ben
41 | 2002-04-04 | 22:30 | 2002-04-05 | 5:00 |  | Justin | Ben
40 | 2002-04-04 | 22:30 | 2002-04-05 | 5:00 |  | Justin | Ben
39 | 2002-04-04 | 22:30 | 2002-04-05 | 5:00 |  | Justin | Ben
38 | 2002-04-04 | 22:30 | 2002-04-05 | 6:00 |  | Justin | Ben
37 | 2002-04-04 | 22:30 | 2002-04-05 | 6:00 |  | Justin | Ben
108 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
104 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
103 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
102 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
100 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
96 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
93 | 2002-04-04 | 22:30 | 2002-04-05 | 6:15 |  | Justin | Ben
92 | 2002-04-04 | 22:30 | 2002-04-05 | 3:00 |  | Justin | Ben
91 | 2002-04-04 | 22:30 | 2002-04-05 | 3:00 |  | Justin | Ben
90 | 2002-04-04 | 22:30 | 2002-04-05 | 3:00 |  | Justin | Ben
89 | 2002-04-04 | 22:30 | 2002-04-05 | 3:00 |  | Justin | Ben
88 | 2002-04-04 | 22:30 | 2002-04-05 | 3:00 |  | Justin | Ben
34 | 2002-04-04 | 22:30 | 2002-04-05 | 6:00 |  | Justin | Ben
36 | 2002-04-04 | 22:30 | 2002-04-05 | 6:00 |  | Justin | Ben
86 | 2002-04-04 | 22:30 | 2002-04-05 | 3:00 |  | Justin | Ben
87 | 2002-04-04 | 22:30 | 2002-04-05 | 3:00 |  | Justin | Ben
33 | 2002-04-04 | 22:30 | 2002-04-05 | 6:00 |  | Justin | Ben
32 | 2002-04-04 | 23:15 | 2002-04-05 | 6:00 |  | Justin | Ben
31 | 2002-04-04 | 23:15 | 2002-04-05 | 6:00 |  | Justin | Ben
85 | 2002-04-04 | 23:15 | 2002-04-05 | 3:00 |  | Justin | Ben
84 | 2002-04-04 | 23:15 | 2002-04-05 | 3:00 |  | Justin | Ben
30 | 2002-04-04 | 23:15 | 2002-04-05 | 6:00 |  | Justin | Ben
29 | 2002-04-04 | 23:15 | 2002-04-05 | 6:00 |  | Justin | Ben
28 | 2002-04-04 | 23:15 | 2002-04-05 | 6:15 |  | Justin | Ben
27 | 2002-04-04 | 23:15 | 2002-04-05 | 6:15 |  | Justin | Ben
26 | 2002-04-04 | 23:15 | 2002-04-05 | 6:15 |  | Justin | Ben
25 | 2002-04-04 | 23:15 | 2002-04-05 | 6:15 |  | Justin | Ben
24 | 2002-04-04 | 23:15 | 2002-04-05 | 6:15 |  | Justin | Ben
85 | 2002-04-04 | 23:15 | 2002-04-05 | 3:00 |  | Justin | Ben
84 | 2002-04-04 | 23:45 | 2002-04-05 | 3:00 |  | Justin | Ben
83 | 2002-04-04 | 23:45 | 2002-04-05 | 3:00 |  | Justin | Ben
82 | 2002-04-04 | 23:45 | 2002-04-05 | 2:45 |  | Justin | Ben
81 | 2002-04-04 | 23:45 | 2002-04-05 | 2:45 |  | Justin | Ben
80 | 2002-04-04 | 23:45 | 2002-04-05 | 2:45 |  | Justin | Ben
79 | 2002-04-04 | 23:45 | 2002-04-05 | 2:45 |  | Justin | Ben
82 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
83 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
84 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
85 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
86 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
87 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
88 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 | 2.25 | Justin | Ben
89 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
90 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
91 | 2002-04-05 | 3:15 | 2002-04-05 | 5:30 |  | Justin | Ben
92 | 2002-04-05 | 3:15 | 2002-04-05 | 6:15 |  | Justin | Ben
77 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
78 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
79 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
80 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
76 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
15 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
16 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
17 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
18 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
19 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
14 | 2002-04-05 | 3:30 | 2002-04-05 | 6:15 |  | Justin | Ben
1 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
2 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
3 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
4 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
5 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
7 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
8 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
9 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
13 | 2002-04-05 | 5:30 | 2002-04-05 | 6:15 |  | Justin | Ben
84 | 2002-04-05 | 5:15 | 2002-04-05 | 6:00 |  | Charlie | Ben
85 | 2002-04-05 | 5:15 | 2002-04-05 | 6:00 |  | Charlie | Ben
86 | 2002-04-05 | 5:15 | 2002-04-05 | 6:00 |  | Charlie | Ben
87 | 2002-04-05 | 5:15 | 2002-04-05 | 6:00 |  | Charlie | Ben
88 | 2002-04-05 | 5:15 | 2002-04-05 | 6:15 |  | Charlie | Ben
89 | 2002-04-05 | 5:15 | 2002-04-05 | 6:15 |  | Charlie | Ben
90 | 2002-04-05 | 5:15 | 2002-04-05 | 6:15 |  | Charlie | Ben
91 | 2002-04-05 | 5:15 | 2002-04-05 | 6:15 |  | Charlie | Ben
1 | 2002-04-05 | 7:10 | 2002-04-05 | 9:11 |  | Charlie | Ben
2 | 2002-04-05 | 7:10 | 2002-04-05 | 9:11 |  | Charlie | Ben
3 | 2002-04-05 | 7:10 | 2002-04-05 | 9:11 |  | Charlie | Ben
4 | 2002-04-05 | 7:10 | 2002-04-05 | 9:16 |  | Charlie | Ben
5 | 2002-04-05 | 7:10 | 2002-04-05 | 9:16 |  | Charlie | Ben
7 | 2002-04-05 | 7:10 | 2002-04-05 | 9:16 |  | Charlie | Ben
8 | 2002-04-05 | 7:10 | 2002-04-05 | 9:34 |  | Charlie | Ben
9 | 2002-04-05 | 7:10 | 2002-04-05 | 9:34 |  | Charlie | Ben
13 | 2002-04-05 | 7:10 | 2002-04-05 | 9:42 |  | Charlie | Ben
14 | 2002-04-05 | 7:10 | 2002-04-05 | 9:42 |  | Charlie | Ben
15 | 2002-04-05 | 7:10 | 2002-04-05 | 9:42 |  | Charlie | Ben
17 | 2002-04-05 | 7:10 | 2002-04-05 | 9:50 |  | Charlie | Ben
18 | 2002-04-05 | 7:10 | 2002-04-05 | 9:50 |  | Charlie | Ben
26 | 2002-04-05 | 7:10 | 2002-04-05 | 8:15 |  | Charlie | Ben
27 | 2002-04-05 | 7:10 | 2002-04-05 | 8:09 |  | Charlie | Ben
28 | 2002-04-05 | 7:10 | 2002-04-05 | 8:09 |  | Charlie | Ben
29 | 2002-04-05 | 7:10 | 2002-04-05 | 8:09 |  | Charlie | Ben
30 | 2002-04-05 | 7:10 | 2002-04-05 | 8:09 |  | Charlie | Ben
31 | 2002-04-05 | 7:10 | 2002-04-05 | 8:09 |  | Charlie | Ben
32 | 2002-04-05 | 7:10 | 2002-04-05 | 8:09 |  | Charlie | Ben
33 | 2002-04-05 | 7:10 | 2002-04-05 | 7:58 |  | Charlie | Ben
34 | 2002-04-05 | 7:10 | 2002-04-05 | 7:58 |  | Charlie | Ben
19 | 2002-04-05 | 7:10 | 2002-04-05 | 9:51 |  | Charlie | Ben
20 | 2002-04-05 | 7:10 | 2002-04-05 | 9:51 |  | Charlie | Ben
21 | 2002-04-05 | 7:10 | 2002-04-05 | 10:00 |  | Charlie | Ben
22 | 2002-04-05 | 7:10 | 2002-04-05 | 10:00 |  | Charlie | Ben
23 | 2002-04-05 | 7:10 | 2002-04-05 | 8:15 |  | Charlie | Ben
24 | 2002-04-05 | 7:10 | 2002-04-05 | 8:15 |  | Charlie | Ben
25 | 2002-04-05 | 7:10 | 2002-04-05 | 8:15 |  | Charlie | Ben
49 | 2002-04-05 | 7:10 | 2002-04-05 | 8:15 |  | Charlie | Ben
50 | 2002-04-05 | 7:10 | 2002-04-05 | 7:23 |  | Charlie | Ben
51 | 2002-04-05 | 7:10 | 2002-04-05 | 7:23 |  | Charlie | Ben
52 | 2002-04-05 | 7:10 | 2002-04-05 | 7:23 |  | Charlie | Ben
53 | 2002-04-05 | 7:10 | 2002-04-05 | 7:23 |  | Charlie | Ben
54 | 2002-04-05 | 7:10 | 2002-04-05 | 7:23 |  | Charlie | Ben
55 | 2002-04-05 | 7:10 | 2002-04-05 | 7:23 |  | Charlie | Ben
56 | 2002-04-05 | 7:10 | 2002-04-05 | 7:23 |  | Charlie | Ben
87 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
88 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
89 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
90 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
91 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
93 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
96 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
100 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
102 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
103 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
104 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
105 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
106 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
107 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
108 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
109 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
120 | 2002-04-05 | 7:25 | 2002-04-05 | 8:10 |  | Charlie | Gilbert
119 | 2002-04-05 | 7:25 | 2002-04-05 | 9:36 |  | Charlie | Gilbert
121 | 2002-04-05 | 7:25 | 2002-04-05 | 9:36 |  | Charlie | Gilbert
122 | 2002-04-05 | 7:25 | 2002-04-05 | 9:36 |  | Charlie | Gilbert
113 | 2002-04-05 | 7:25 | 2002-04-05 | 8:20 |  | Charlie | Gilbert
114 | 2002-04-05 | 7:25 | 2002-04-05 | 8:20 |  | Charlie | Gilbert
115 | 2002-04-05 | 7:25 | 2002-04-05 | 8:20 |  | Charlie | Gilbert
116 | 2002-04-05 | 7:25 | 2002-04-05 | 8:20 |  | Charlie | Gilbert
92 | 2002-04-05 | 7:25 | 2002-04-05 | 8:07 |  | Charlie | Gilbert
36 | 2002-04-05 | 7:25 | 2002-04-05 | 7:43 |  | Charlie | Gilbert
37 | 2002-04-05 | 7:25 | 2002-04-05 | 7:43 |  | Charlie | Gilbert
23 | 2002-04-05 | 8:30 | 2002-04-05 | 10:00 |  | Charlie | Gilbert
24 | 2002-04-05 | 8:30 | 2002-04-05 | 10:00 |  | Charlie | Gilbert
92 | 2002-04-05 | 8:30 | 2002-04-05 | 10:00 |  | Charlie | Gilbert
118 | 2002-04-05 | 7:25 | 2002-04-05 | 14:48 |  | Charlie | Gilbert
106 | 2002-04-05 | 8:34 | 2002-04-05 | 9:44 |  | Charlie | Gilbert
107 | 2002-04-05 | 8:34 | 2002-04-05 | 9:44 |  | Charlie | Gilbert
108 | 2002-04-05 | 8:34 | 2002-04-05 | 9:44 |  | Charlie | Gilbert
109 | 2002-04-05 | 8:34 | 2002-04-05 | 9:44 |  | Charlie | Gilbert
120 | 2002-04-05 | 8:34 | 2002-04-05 | 9:44 |  | Charlie | Gilbert
25 | 2002-04-05 | 8:34 | 2002-04-05 | 13:23 |  | Charlie | Gilbert
26 | 2002-04-05 | 8:34 | 2002-04-05 | 13:23 |  | Charlie | Gilbert
27 | 2002-04-05 | 8:34 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
28 | 2002-04-05 | 8:34 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
29 | 2002-04-05 | 8:34 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
30 | 2002-04-05 | 8:45 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
31 | 2002-04-05 | 8:45 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
102 | 2002-04-05 | 8:45 | 2002-04-05 | 10:00 |  | Charlie | Gilbert
103 | 2002-04-05 | 8:45 | 2002-04-05 | 10:00 |  | Charlie | Gilbert
104 | 2002-04-05 | 8:45 | 2002-04-05 | 10:00 |  | Charlie | Gilbert
105 | 2002-04-05 | 8:45 | 2002-04-05 | 10:00 |  | Charlie | Gilbert
34 | 2002-04-05 | 9:18 | 2002-04-05 | 9:31 |  | Charlie | Gilbert
114 | 2002-04-05 | 8:30 | 2002-04-05 | 10:19 |  | Charlie | Gilbert
115 | 2002-04-05 | 8:30 | 2002-04-05 | 10:19 |  | Charlie | Gilbert
116 | 2002-04-05 | 8:30 | 2002-04-05 | 10:19 |  | Charlie | Gilbert
1 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
2 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
3 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
4 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
5 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
7 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
8 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
9 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
84 | 2002-04-05 | 12:17 | 2002-04-05 | 19:45 |  | Charlie | Gilbert
85 | 2002-04-05 | 12:17 | 2002-04-05 | 19:45 |  | Charlie | Gilbert
86 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
87 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
88 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
89 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
90 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
91 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
92 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
93 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
96 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
100 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
102 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
103 | 2002-04-05 | 12:17 | 2002-04-06 | 7:30 |  | Charlie | Gilbert
32 | 2002-04-05 | 12:30 | 2002-04-06 | 7:30 |  | Mac | Gilbert
33 | 2002-04-05 | 12:30 | 2002-04-06 | 7:30 |  | Mac | Gilbert
34 | 2002-04-05 | 12:30 | 2002-04-06 | 7:30 |  | Mac | Gilbert
82 | 2002-04-05 | 12:30 | 2002-04-05 | 14:45 |  | Mac | Gilbert
83 | 2002-04-05 | 12:30 | 2002-04-05 | 14:45 |  | Mac | Gilbert
118 | 2002-04-05 | 12:30 | 2002-04-06 | 7:30 |  | Mac | Gilbert
35 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
36 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
37 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
38 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
39 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
40 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
41 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
42 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
43 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
44 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
45 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
46 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
47 | 2002-04-05 | 13:12 | 2002-04-05 | 19:45 |  | Mac | Gilbert
102 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
103 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
104 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
105 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
106 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
107 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
108 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
109 | 2002-04-05 | 13:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
13 | 2002-04-05 | 13:45 | 2002-04-06 | 7:30 |  | Mac | Gilbert
14 | 2002-04-05 | 13:45 | 2002-04-06 | 7:30 |  | Mac | Gilbert
79 | 2002-04-05 | 13:45 | 2002-04-05 | 19:45 |  | Mac | Gilbert
80 | 2002-04-05 | 13:45 | 2002-04-05 | 19:45 |  | Mac | Gilbert
81 | 2002-04-05 | 13:45 | 2002-04-05 | 19:45 |  | Mac | Gilbert
120 | 2002-04-05 | 14:15 | 2002-04-06 | 7:30 |  | Mac | Gilbert
70 | 2002-04-05 | 15:12 | 2002-04-06 | 7:30 |  | Mac | Gilbert
24 | 2002-04-05 | 16:15 | 2002-04-06 | 7:30 |  | Mac | Gilbert
25 | 2002-04-05 | 16:15 | 2002-04-06 | 7:30 |  | Mac | Gilbert
26 | 2002-04-05 | 16:15 | 2002-04-06 | 7:30 |  | Mac | Gilbert
75 | 2002-04-05 | 17:30 | 2002-04-05 | 19:45 |  | Mac | Gilbert
77 | 2002-04-05 | 17:30 | 2002-04-05 | 19:45 |  | Mac | Gilbert
78 | 2002-04-05 | 17:30 | 2002-04-05 | 19:45 |  | Mac | Gilbert
22 | 2002-04-05 | 17:30 | 2002-04-06 | 7:30 |  | Mac | Gilbert
23 | 2002-04-05 | 17:30 | 2002-04-06 | 7:30 |  | Mac | Gilbert
39 | 2002-04-05 | 20:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
40 | 2002-04-05 | 20:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
41 | 2002-04-05 | 20:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
42 | 2002-04-05 | 20:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
92 | 2002-04-05 | 20:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
84 | 2002-04-05 | 20:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
85 | 2002-04-05 | 22:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
83 | 2002-04-05 | 22:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
82 | 2002-04-05 | 22:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
81 | 2002-04-05 | 22:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
43 | 2002-04-05 | 22:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
44 | 2002-04-05 | 22:00 | 2002-04-06 | 7:30 |  | Mac | Gilbert
7 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
8 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
9 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
13 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
14 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
15 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
17 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
22 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
24 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
25 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
34 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
38 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
39 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
40 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
41 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
42 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
43 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
44 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
45 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
46 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
47 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
49 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
50 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
51 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
52 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
53 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
54 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
55 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
56 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
57 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
58 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
59 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
60 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
62 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
68 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
72 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
73 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
74 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
77 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
78 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
79 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
84 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
91 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
93 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
96 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
100 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
102 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
103 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
104 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
105 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
106 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
107 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
108 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
109 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
120 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
113 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
114 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
115 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
116 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
117 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
118 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
119 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
121 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
122 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Justin | Gilbert
7 | 2002-04-06 | 7:30 | 2002-04-06 | 7:45 |  | Jason | Gilbert
57 | 2002-04-06 | 7:30 | 2002-04-06 | 7:45 |  | Jason | Gilbert
8 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Jason | Gilbert
9 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Jason | Gilbert
13 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Jason | Gilbert
14 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Jason | Gilbert
15 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Jason | Gilbert
17 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Jason | Gilbert
22 | 2002-04-06 | 7:30 | 2002-04-06 | 9:30 |  | Jason | Gilbert
21 | 2002-04-06 | 14:00 | 2002-04-06 | 21:30 |  | Jason | Duvall
22 | 2002-04-06 | 14:00 | 2002-04-06 | 21:30 |  | Jason | Duvall
23 | 2002-04-06 | 14:00 | 2002-04-06 | 21:30 |  | Jason | Duvall
24 | 2002-04-06 | 14:00 | 2002-04-06 | 21:30 |  | Jason | Duvall
25 | 2002-04-06 | 14:00 | 2002-04-06 | 21:30 |  | Jason | Duvall
26 | 2002-04-06 | 14:00 | 2002-04-06 | 21:30 |  | Jason | Duvall
60 | 2002-04-06 | 14:00 | 2002-04-06 | 21:30 |  | Jason | Duvall
61 | 2002-04-06 | 14:00 | 2002-04-06 | 19:30 |  | Jason | Duvall
62 | 2002-04-06 | 14:00 | 2002-04-06 | 19:30 |  | Jason | Duvall
63 | 2002-04-06 | 14:00 | 2002-04-06 | 19:30 |  | Jason | Duvall
64 | 2002-04-06 | 14:00 | 2002-04-06 | 19:30 |  | Jason | Duvall
65 | 2002-04-06 | 14:00 | 2002-04-06 | 19:30 |  | Jason | Duvall
66 | 2002-04-06 | 14:00 | 2002-04-06 | 19:30 |  | Jason | Duvall
19 | 2002-04-06 | 14:45 | 2002-04-06 | 19:30 |  | Jason | Duvall
20 | 2002-04-06 | 14:45 | 2002-04-06 | 19:30 |  | Jason | Duvall
121 | 2002-04-06 | 10:20 | 2002-04-06 | 14:45 |  | Jason | Duvall
122 | 2002-04-06 | 10:20 | 2002-04-06 | 14:45 |  | Jason | Duvall
47 | 2002-04-06 | 7:30 | 2002-04-06 | 15:15 |  | Jason | Duvall
78 | 2002-04-06 | 15:00 | 2002-04-06 | 15:15 |  | Jason | Duvall
79 | 2002-04-06 | 15:00 | 2002-04-06 | 15:15 |  | Jason | Duvall
92 | 2002-04-06 | 11:25 | 2002-04-06 | 15:15 |  | Jason | Duvall
93 | 2002-04-06 | 11:25 | 2002-04-06 | 15:15 |  | Jason | Duvall
25 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
29 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
34 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
38 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
39 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
40 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
41 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
42 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
43 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
33 | 2002-04-06 | 7:30 | 2002-04-06 | 9:35 |  | Jason | Gilbert
34 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
35 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
36 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
37 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
38 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
39 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
40 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
41 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
42 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
43 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
32 | 2002-04-06 | 9:40 | 2002-04-06 | 9:53 |  | Jason | Gilbert
60 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
62 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
68 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
72 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
32 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
60 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
62 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
73 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
74 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
75 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
76 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
84 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
91 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
92 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
93 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
96 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
100 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
102 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
103 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
104 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
105 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
106 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
107 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
108 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
109 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
113 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
116 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
117 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
118 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
119 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
120 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
114 | 2002-04-06 | 7:30 | 2002-04-06 | 10:00 |  | Jason | Gilbert
60 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
91 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
92 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
93 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
96 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
100 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
102 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
103 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
104 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
105 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
106 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
107 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
108 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
109 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
113 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
118 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
119 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Gilbert
120 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Buckey
121 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Buckey
122 | 2002-04-06 | 10:05 | 2002-04-06 | 10:20 |  | Jason | Buckey
114 | 2002-04-06 | 7:30 | 2002-04-06 | 10:35 |  | Jason | Buckey
91 | 2002-04-06 | 7:30 | 2002-04-06 | 10:35 |  | Jason | Buckey
92 | 2002-04-06 | 7:30 | 2002-04-06 | 10:35 |  | Jason | Buckey
93 | 2002-04-06 | 7:30 | 2002-04-06 | 10:35 |  | Jason | Buckey
30 | 2002-04-06 | 11:10 | 2002-04-06 | 11:25 |  | Jason | Buckey
31 | 2002-04-06 | 11:10 | 2002-04-06 | 11:25 |  | Jason | Buckey
32 | 2002-04-06 | 11:10 | 2002-04-06 | 11:25 |  | Jason | Buckey
33 | 2002-04-06 | 11:10 | 2002-04-06 | 11:25 |  | Jason | Buckey
34 | 2002-04-06 | 11:10 | 2002-04-06 | 11:25 |  | Jason | Buckey
93 | 2002-04-06 | 11:10 | 2002-04-06 | 11:25 |  | Jason | Buckey
88 | 2002-04-06 | 11:10 | 2002-04-06 | 11:45 |  | Jason | Buckey
89 | 2002-04-06 | 11:10 | 2002-04-06 | 11:45 |  | Jason | Buckey
90 | 2002-04-06 | 11:10 | 2002-04-06 | 11:45 |  | Jason | Buckey
91 | 2002-04-06 | 11:10 | 2002-04-06 | 11:45 |  | Jason | Buckey
92 | 2002-04-06 | 11:10 | 2002-04-06 | 11:45 |  | Jason | Buckey
52 | 2002-04-06 | 7:30 | 2002-04-06 | 11:45 |  | Jason | Duvall
80 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
81 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
82 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
83 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
84 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
85 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
86 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
87 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
57 | 2002-04-06 | 11:50 | 2002-04-06 | 12:45 |  | Jason | Duvall
29 | 2002-04-06 | 11:50 | 2002-04-06 | 12:50 |  | Jason | Duvall
28 | 2002-04-06 | 11:50 | 2002-04-06 | 13:15 |  | Jason | Duvall
27 | 2002-04-06 | 11:50 | 2002-04-06 | 13:15 |  | Jason | Duvall
21 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
22 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
23 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
24 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
25 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
26 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
27 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
28 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
29 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
30 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
31 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
32 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
33 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
34 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
35 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
36 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
37 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
38 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
39 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
40 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
49 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
50 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
51 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
53 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
55 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
56 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
57 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
58 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
59 | 2002-04-06 | 21:30 | 2002-04-07 | 10:30 |  | Jason | Ben
115 | 2002-04-06 | 21:30 | 2002-04-07 | 11:35 |  | Jason | Ben
116 | 2002-04-06 | 21:30 | 2002-04-07 | 11:35 |  | Jason | Ben
18 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
19 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
20 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
21 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
22 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
23 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
24 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
25 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
26 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
27 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
28 | 2002-04-07 | 12:20 | 2002-04-07 | 14:30 |  | Jason | Ben
115 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
116 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
49 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
50 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
51 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
52 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
53 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
57 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
58 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
59 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
55 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
56 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
29 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
30 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
31 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
32 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
33 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
34 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
35 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
36 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
37 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
38 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
39 | 2002-04-07 | 12:20 | 2002-04-07 | 16:20 |  | Jason | Ben
61 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
62 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
65 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
68 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
69 | 2002-04-06 | 21:30 | 2002-04-08 | 19:10 |  | Jason | Ben
71 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
72 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
73 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
74 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
75 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
77 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
79 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
83 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
84 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
85 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
91 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
92 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
93 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
96 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
106 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
107 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
108 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
109 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
117 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
119 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
121 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
122 | 2002-04-06 | 21:30 | 2002-04-07 | 11:30 |  | Jason | Ben
89 | 2002-04-06 | 21:30 | 2002-04-07 | 11:45 |  | Jason | Ben
60 | 2002-04-07 | 12:00 | 2002-04-07 | 14:30 |  | Jason | Ben
61 | 2002-04-07 | 12:00 | 2002-04-07 | 14:30 |  | Jason | Ben
62 | 2002-04-07 | 12:00 | 2002-04-07 | 14:30 |  | Jason | Ben
63 | 2002-04-07 | 12:00 | 2002-04-07 | 14:30 |  | Jason | Ben
64 | 2002-04-07 | 12:00 | 2002-04-07 | 14:30 |  | Jason | Ben
65 | 2002-04-07 | 12:50 | 2002-04-07 | 14:30 |  | Jason | Ben
66 | 2002-04-07 | 12:50 | 2002-04-07 | 14:30 |  | Jason | Ben
68 | 2002-04-07 | 12:50 | 2002-04-07 | 14:20 |  | Jason | Ben
13 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
14 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
15 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
18 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
19 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
20 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
21 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
22 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
23 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
24 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
25 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
26 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
29 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
30 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
31 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
32 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
33 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
34 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
35 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
36 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
37 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
38 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
39 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
40 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
41 | 2002-04-06 | 21:30 | 2002-04-07 | 9:00 |  | Bryan | Ben
42 | 2002-04-06 | 21:30 | 2002-04-07 | 9:00 |  | Bryan | Ben
43 | 2002-04-06 | 21:30 | 2002-04-07 | 8:00 |  | Bryan | Ben
44 | 2002-04-06 | 21:30 | 2002-04-07 | 8:00 |  | Bryan | Ben
46 | 2002-04-06 | 21:30 | 2002-04-07 | 8:00 |  | Bryan | Ben
49 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
50 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
51 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
53 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
57 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
58 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
59 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
56 | 2002-04-07 | 9:20 | 2002-04-07 | 17:00 |  | Bryan | Ben
115 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
116 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
106 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
107 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
72 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
74 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
75 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
76 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
77 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
69 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
66 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
63 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
62 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
60 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
121 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
122 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
79 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
83 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
84 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
85 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
91 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
92 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
93 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
117 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
108 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
96 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
119 | 2002-04-06 | 21:30 | 2002-04-07 | 17:00 |  | Bryan | Ben
100 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
102 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
103 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
104 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
105 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
113 | 2002-04-06 | 21:30 | 2002-04-07 | 4:00 |  | Bryan | Ben
4 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
8 | 2002-04-07 | 20:00 | 2002-04-08 | 5:30 |  | Bryan | Ben
9 | 2002-04-07 | 20:00 | 2002-04-08 | 5:00 |  | Bryan | Ben
14 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
30 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
31 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
32 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
33 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
35 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
36 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
37 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
38 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
39 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
40 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
41 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
42 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
43 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
44 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
45 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
46 | 2002-04-07 | 20:00 | 2002-04-08 | 0:15 |  | Bryan | Ben
47 | 2002-04-07 | 20:00 | 2002-04-08 | 6:30 |  | Bryan | Ben
50 | 2002-04-07 | 20:00 | 2002-04-08 | 6:30 |  | Bryan | Ben
49 | 2002-04-07 | 20:00 | 2002-04-08 | 6:30 |  | Bryan | Ben
51 | 2002-04-07 | 20:00 | 2002-04-08 | 6:30 |  | Bryan | Ben
7 | 2002-04-07 | 23:30 | 2002-04-08 | 5:15 |  | Bryan | Ben
5 | 2002-04-07 | 23:30 | 2002-04-08 | 5:15 |  | Bryan | Ben
3 | 2002-04-07 | 23:30 | 2002-04-08 | 5:15 |  | Bryan | Ben
28 | 2002-04-07 | 23:30 | 2002-04-08 | 5:15 |  | Bryan | Ben
27 | 2002-04-07 | 23:45 | 2002-04-08 | 5:00 |  | Bryan | Ben
26 | 2002-04-07 | 23:45 | 2002-04-08 | 5:00 |  | Bryan | Ben
15 | 2002-04-07 | 23:45 | 2002-04-08 | 5:00 |  | Bryan | Ben
25 | 2002-04-07 | 23:45 | 2002-04-08 | 5:00 |  | Bryan | Ben
118 | 2002-04-07 | 23:45 | 2002-04-08 | 5:30 |  | Bryan | Ben
119 | 2002-04-07 | 23:45 | 2002-04-08 | 5:30 |  | Bryan | Ben
120 | 2002-04-07 | 23:45 | 2002-04-08 | 5:30 |  | Bryan | Ben
77 | 2002-04-07 | 23:45 | 2002-04-08 | 4:00 |  | Bryan | Ben
75 | 2002-04-08 | 0:15 | 2002-04-08 | 4:00 |  | Bryan | Ben
76 | 2002-04-08 | 0:15 | 2002-04-08 | 4:00 |  | Bryan | Ben
74 | 2002-04-08 | 4:00 | 2002-04-08 | 4:00 |  | Bryan | Ben
73 | 2002-04-08 | 4:00 | 2002-04-08 | 4:00 |  | Bryan | Ben
72 | 2002-04-08 | 4:00 | 2002-04-08 | 4:00 |  | Bryan | Ben
106 | 2002-04-08 | 4:00 | 2002-04-08 | 6:00 |  | Bryan | Ben
107 | 2002-04-08 | 4:00 | 2002-04-08 | 6:00 |  | Bryan | Ben
86 | 2002-04-08 | 4:00 | 2002-04-08 | 6:00 |  | Bryan | Ben
1 | 2002-04-08 | 7:15 | 2002-04-08 | 8:15 |  | Matt | Duvall
2 | 2002-04-08 | 7:15 | 2002-04-08 | 8:15 |  | Matt | Duvall
115 | 2002-04-08 | 7:15 | 2002-04-08 | 17:20 |  | Matt | Duvall
116 | 2002-04-08 | 7:15 | 2002-04-08 | 17:20 |  | Matt | Duvall
3 | 2002-04-08 | 7:15 | 2002-04-08 | 8:15 |  | Matt | Duvall
5 | 2002-04-08 | 7:15 | 2002-04-08 | 11:50 |  | Matt | Duvall
7 | 2002-04-08 | 7:15 | 2002-04-08 | 13:35 |  | Matt | Duvall
8 | 2002-04-08 | 7:15 | 2002-04-08 | 13:35 |  | Matt | Duvall
9 | 2002-04-08 | 7:15 | 2002-04-08 | 13:35 |  | Matt | Duvall
13 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
14 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
15 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
17 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
18 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
19 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
20 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
21 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
22 | 2002-04-08 | 7:15 | 2002-04-08 | 18:10 |  | Matt | Duvall
23 | 2002-04-08 | 7:15 | 2002-04-08 | 19:00 |  | Matt | Duvall
24 | 2002-04-08 | 7:15 | 2002-04-08 | 19:00 |  | Matt | Duvall
25 | 2002-04-08 | 7:15 | 2002-04-08 | 19:00 |  | Matt | Duvall
26 | 2002-04-08 | 7:15 | 2002-04-08 | 19:00 |  | Matt | Duvall
27 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
28 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
29 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
30 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
31 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
32 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
33 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
34 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
35 | 2002-04-08 | 7:15 | 2002-04-08 | 19:50 |  | Matt | Duvall
66 | 2002-04-08 | 7:25 | 2002-04-08 | 8:17 |  | Jason | Duvall
68 | 2002-04-08 | 7:25 | 2002-04-08 | 8:17 |  | Jason | Duvall
72 | 2002-04-08 | 7:25 | 2002-04-08 | 8:17 |  | Jason | Duvall
73 | 2002-04-08 | 7:25 | 2002-04-08 | 11:20 |  | Jason | Duvall
74 | 2002-04-08 | 7:25 | 2002-04-08 | 11:20 |  | Jason | Duvall
75 | 2002-04-08 | 7:25 | 2002-04-08 | 11:50 |  | Jason | Duvall
76 | 2002-04-08 | 7:25 | 2002-04-08 | 11:50 |  | Jason | Duvall
77 | 2002-04-08 | 7:25 | 2002-04-08 | 13:30 |  | Jason | Duvall
78 | 2002-04-08 | 7:25 | 2002-04-08 | 13:30 |  | Jason | Duvall
79 | 2002-04-08 | 7:25 | 2002-04-08 | 13:30 |  | Jason | Duvall
80 | 2002-04-08 | 7:25 | 2002-04-08 | 13:30 |  | Jason | Duvall
81 | 2002-04-08 | 7:25 | 2002-04-08 | 16:45 |  | Jason | Duvall
82 | 2002-04-08 | 7:25 | 2002-04-08 | 16:45 |  | Jason | Duvall
83 | 2002-04-08 | 7:25 | 2002-04-08 | 16:45 |  | Jason | Duvall
84 | 2002-04-08 | 7:25 | 2002-04-08 | 16:45 |  | Jason | Duvall
85 | 2002-04-08 | 7:25 | 2002-04-08 | 16:45 |  | Jason | Duvall
86 | 2002-04-08 | 7:25 | 2002-04-08 | 14:10 |  | Jason | Duvall
96 | 2002-04-08 | 7:25 | 2002-04-08 | 17:20 |  | Jason | Duvall
36 | 2002-04-08 | 7:10 | 2002-04-08 | 8:12 |  | Jason | Duvall
37 | 2002-04-08 | 7:10 | 2002-04-08 | 8:12 |  | Jason | Duvall
105 | 2002-04-08 | 9:30 | 2002-04-08 | 10:00 |  | Jason | Duvall
55 | 2002-04-08 | 10:30 | 2002-04-08 | 16:05 |  | Jason | Duvall
114 | 2002-04-08 | 8:00 | 2002-04-08 | 17:45 |  | Jason | Duvall
90 | 2002-04-06 | 11:47 | 2002-04-08 | 13:00 |  | Jason | Duvall
72 | 2002-04-08 | 15:25 | 2002-04-08 | 18:00 |  | Jason | Duvall
73 | 2002-04-08 | 15:25 | 2002-04-08 | 18:00 |  | Jason | Duvall
74 | 2002-04-08 | 15:25 | 2002-04-08 | 18:00 |  | Jason | Duvall
75 | 2002-04-08 | 15:25 | 2002-04-08 | 18:15 |  | Jason | Duvall
76 | 2002-04-08 | 15:25 | 2002-04-08 | 18:15 |  | Jason | Duvall
91 | 2002-04-08 | 7:25 | 2002-04-08 | 19:10 |  | Jason | Buckey
92 | 2002-04-08 | 7:25 | 2002-04-08 | 19:10 |  | Jason | Buckey
93 | 2002-04-08 | 7:25 | 2002-04-08 | 19:10 |  | Jason | Buckey
117 | 2002-04-07 | 17:00 | 2002-04-08 | 19:10 |  | Jason | Buckey
69 | 2002-04-06 | 17:00 | 2002-04-08 | 19:10 |  | Jason | Buckey
1 | 2002-04-10 | 1:50 | 2002-04-10 | 2:50 |  | Charlie | Gilbert
2 | 2002-04-10 | 1:50 | 2002-04-10 | 2:50 |  | Charlie | Gilbert
3 | 2002-04-10 | 1:50 | 2002-04-10 | 4:30 |  | Charlie | Gilbert
4 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
5 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
7 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
8 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
9 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
13 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
14 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
15 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
17 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
18 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
19 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
20 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
21 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
22 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
23 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
24 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
25 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
26 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
27 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
28 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
29 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
30 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
31 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
32 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
33 | 2002-04-10 | 1:50 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
34 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
35 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
36 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
37 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
38 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
39 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
40 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
41 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
42 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
43 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
44 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
45 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
46 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
47 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
49 | 2002-04-10 | 2:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
50 | 2002-04-10 | 5:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
51 | 2002-04-10 | 5:00 | 2002-04-10 | 6:15 |  | Charlie | Gilbert
1 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
2 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
3 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
4 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
5 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
7 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
8 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
9 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
13 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
14 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
15 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
17 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
18 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
19 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
20 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
21 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
22 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
23 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
24 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
25 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
26 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
27 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
28 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
29 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
30 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
31 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
32 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
33 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
34 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
35 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
36 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
37 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
38 | 2002-04-10 | 6:30 | 2002-04-10 | 11:00 |  | Kenny | Ben
40 | 2002-04-10 | 6:30 | 2002-04-10 | 7:10 |  | Kenny | Ben
45 | 2002-04-10 | 7:10 | 2002-04-10 | 11:00 |  | Kenny | Ben
115 | 2002-04-10 | 7:30 | 2002-04-10 | 13:30 |  | Kenny | Ben
121 | 2002-04-10 | 8:00 | 2002-04-10 | 11:00 |  | Kenny | Ben
122 | 2002-04-10 | 8:00 | 2002-04-10 | 11:00 |  | Kenny | Ben
13 | 2002-04-10 | 17:25 | 2002-04-10 | 20:20 |  | Kenny | Ben
14 | 2002-04-10 | 17:25 | 2002-04-10 | 20:20 |  | Kenny | Ben
15 | 2002-04-10 | 17:25 | 2002-04-10 | 20:20 |  | Kenny | Ben
17 | 2002-04-10 | 17:25 | 2002-04-10 | 20:20 |  | Kenny | Ben
18 | 2002-04-10 | 17:25 | 2002-04-10 | 20:20 |  | Kenny | Ben
19 | 2002-04-10 | 17:25 | 2002-04-10 | 20:20 |  | Kenny | Ben
20 | 2002-04-10 | 17:25 | 2002-04-10 | 20:20 |  | Kenny | Ben
21 | 2002-04-10 | 17:25 | 2002-04-11 | 10:00 |  | Kenny | Ben
22 | 2002-04-10 | 17:25 | 2002-04-11 | 10:00 |  | Kenny | Ben
23 | 2002-04-10 | 17:25 | 2002-04-11 | 10:00 |  | Kenny | Ben
24 | 2002-04-10 | 17:25 | 2002-04-11 | 10:00 |  | Kenny | Ben
71 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
72 | 2002-04-10 | 17:30 | 2002-04-10 | 20:20 |  | Kenny | Ben
73 | 2002-04-10 | 17:30 | 2002-04-10 | 20:20 |  | Kenny | Ben
74 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
75 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
76 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
77 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
78 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
79 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
80 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
81 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
82 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
83 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
84 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
25 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
26 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
27 | 2002-04-10 | 17:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
28 | 2002-04-10 | 17:35 | 2002-04-11 | 10:00 |  | Kenny | Ben
29 | 2002-04-10 | 17:35 | 2002-04-11 | 10:00 |  | Kenny | Ben
30 | 2002-04-10 | 17:35 | 2002-04-11 | 10:00 |  | Kenny | Ben
31 | 2002-04-10 | 17:45 | 2002-04-11 | 10:00 |  | Kenny | Ben
32 | 2002-04-10 | 17:45 | 2002-04-11 | 10:00 |  | Kenny | Ben
33 | 2002-04-10 | 17:45 | 2002-04-11 | 10:00 |  | Kenny | Ben
34 | 2002-04-10 | 18:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
35 | 2002-04-10 | 18:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
36 | 2002-04-10 | 18:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
114 | 2002-04-10 | 18:20 | 2002-04-11 | 10:00 |  | Kenny | Ben
115 | 2002-04-10 | 18:20 | 2002-04-11 | 10:00 |  | Kenny | Ben
85 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
86 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
87 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
88 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
89 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
90 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
91 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
92 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
93 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
96 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
100 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
102 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
103 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
104 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
105 | 2002-04-10 | 18:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
37 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
38 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
39 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
40 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
41 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
42 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
43 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
44 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
45 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
46 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
47 | 2002-04-10 | 18:55 | 2002-04-11 | 10:00 |  | Kenny | Ben
60 | 2002-04-10 | 2:00 | 2002-04-10 | 5:50 |  | Charlie | Gilbert
61 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
62 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
63 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
64 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
65 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
66 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
68 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
69 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
70 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
71 | 2002-04-10 | 2:00 | 2002-04-10 | 6:20 |  | Charlie | Gilbert
72 | 2002-04-10 | 2:00 | 2002-04-10 | 7:30 |  | Charlie | Gilbert
73 | 2002-04-10 | 2:00 | 2002-04-10 | 7:30 |  | Charlie | Gilbert
74 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
75 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
76 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
77 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
78 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
79 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
80 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
81 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
82 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
83 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
84 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
85 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
86 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
87 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
88 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
89 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
90 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
91 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
92 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
93 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
96 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
100 | 2002-04-10 | 2:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
102 | 2002-04-10 | 5:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
103 | 2002-04-10 | 5:00 | 2002-04-10 | 11:00 |  | Kenny | Gilbert
49 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
50 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
51 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
52 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
53 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
105 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
107 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
108 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
109 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
113 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
120 | 2002-04-10 | 19:00 | 2002-04-11 | 10:00 |  | Kenny | Ben
72 | 2002-04-10 | 21:15 | 2002-04-11 | 10:00 |  | Kenny | Ben
73 | 2002-04-10 | 21:15 | 2002-04-11 | 10:00 |  | Kenny | Ben
54 | 2002-04-10 | 21:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
55 | 2002-04-10 | 21:30 | 2002-04-11 | 10:00 |  | Kenny | Ben
56 | 2002-04-10 | 21:35 | 2002-04-11 | 10:00 |  | Kenny | Ben
57 | 2002-04-10 | 21:35 | 2002-04-11 | 10:00 |  | Kenny | Ben
68 | 2002-04-10 | 21:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
58 | 2002-04-10 | 23:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
59 | 2002-04-10 | 23:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
116 | 2002-04-10 | 23:50 | 2002-04-11 | 10:00 |  | Kenny | Ben
1 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
2 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
3 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
4 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
5 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
7 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
8 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
9 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
13 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
14 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
15 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
17 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
18 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
19 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
20 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
59 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
58 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
57 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
56 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
55 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
54 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
53 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
52 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
51 | 2002-04-11 | 20:00 | 2002-04-12 | 4:15 |  | Bryan | Art
50 | 2002-04-11 | 20:00 | 2002-04-12 | 0:15 |  | Bryan | Art
13 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
14 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
15 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
17 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
18 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
19 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
20 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
21 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
22 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
23 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
24 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
25 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
26 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
27 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
28 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
29 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
30 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
31 | 2002-04-11 | 20:00 | 2002-04-12 | 3:15 |  | Bryan | Art
32 | 2002-04-11 | 20:00 | 2002-04-12 | 3:15 |  | Bryan | Art
33 | 2002-04-11 | 20:00 | 2002-04-12 | 3:15 |  | Bryan | Art
44 | 2002-04-11 | 20:00 | 2002-04-11 | 22:30 |  | Bryan | Art
45 | 2002-04-11 | 21:30 | 2002-04-11 | 22:30 |  | Bryan | Art
46 | 2002-04-11 | 21:30 | 2002-04-11 | 22:30 |  | Bryan | Art
47 | 2002-04-11 | 21:30 | 2002-04-11 | 22:30 |  | Bryan | Art
9 | 2002-04-11 | 21:45 | 2002-04-11 | 22:30 |  | Bryan | Art
8 | 2002-04-11 | 21:45 | 2002-04-11 | 22:30 |  | Bryan | Art
7 | 2002-04-11 | 21:45 | 2002-04-11 | 22:30 |  | Bryan | Art
34 | 2002-04-11 | 21:45 | 2002-04-12 | 0:05 |  | Bryan | Art
35 | 2002-04-11 | 21:45 | 2002-04-12 | 0:05 |  | Bryan | Art
36 | 2002-04-11 | 22:15 | 2002-04-12 | 0:05 |  | Bryan | Art
88 | 2002-04-11 | 20:00 | 2002-04-12 | 3:15 |  | Bryan | Art
115 | 2002-04-11 | 20:00 | 2002-04-12 | 3:15 |  | Bryan | Art
121 | 2002-04-11 | 20:00 | 2002-04-12 | 4:00 |  | Bryan | Art
120 | 2002-04-11 | 20:00 | 2002-04-12 | 4:00 |  | Bryan | Art
122 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
119 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
118 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
109 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
108 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
107 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
106 | 2002-04-11 | 20:00 | 2002-04-11 | 23:30 |  | Bryan | Art
100 | 2002-04-11 | 20:00 | 2002-04-11 | 23:45 |  | Bryan | Art
102 | 2002-04-11 | 20:00 | 2002-04-11 | 23:45 |  | Bryan | Art
103 | 2002-04-11 | 20:00 | 2002-04-11 | 23:45 |  | Bryan | Art
104 | 2002-04-11 | 20:00 | 2002-04-11 | 23:45 |  | Bryan | Art
105 | 2002-04-11 | 20:00 | 2002-04-11 | 23:45 |  | Bryan | Art
96 | 2002-04-11 | 20:00 | 2002-04-11 | 23:45 |  | Bryan | Art
93 | 2002-04-11 | 20:00 | 2002-04-11 | 23:45 |  | Bryan | Art
92 | 2002-04-11 | 20:00 | 2002-04-12 | 3:45 |  | Bryan | Art
91 | 2002-04-11 | 20:00 | 2002-04-12 | 3:45 |  | Bryan | Art
90 | 2002-04-11 | 20:00 | 2002-04-12 | 3:45 |  | Bryan | Art
89 | 2002-04-11 | 20:00 | 2002-04-12 | 3:45 |  | Bryan | Art
88 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
87 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
86 | 2002-04-11 | 20:00 | 2002-04-11 | 22:45 |  | Bryan | Art
84 | 2002-04-11 | 20:00 | 2002-04-11 | 22:30 |  | Bryan | Art
83 | 2002-04-11 | 20:00 | 2002-04-11 | 22:30 |  | Bryan | Art
68 | 2002-04-11 | 20:00 | 2002-04-12 | 5:50 |  | Bryan | Art
82 | 2002-04-11 | 20:00 | 2002-04-11 | 22:30 |  | Bryan | Art
81 | 2002-04-11 | 21:45 | 2002-04-11 | 22:30 |  | Bryan | Art
80 | 2002-04-11 | 21:45 | 2002-04-11 | 22:30 |  | Bryan | Art
79 | 2002-04-11 | 21:45 | 2002-04-11 | 22:30 |  | Bryan | Art
78 | 2002-04-11 | 21:45 | 2002-04-11 | 22:30 |  | Bryan | Art
77 | 2002-04-11 | 21:45 | 2002-04-11 | 22:30 |  | Bryan | Art
21 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
22 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
23 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
24 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
25 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
26 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
27 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
28 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
29 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
30 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
31 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
32 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
33 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
34 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
36 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
37 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
38 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
39 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
60 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
61 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
62 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
63 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
64 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
65 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
66 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
68 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
72 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
73 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
74 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
75 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
76 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
77 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
78 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
79 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
93 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
96 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
100 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
102 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
103 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
104 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
105 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
106 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
107 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
108 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
109 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
120 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
121 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
122 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
113 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
114 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
115 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
116 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
117 | 2002-04-11 | 11:00 | 2002-04-11 | 13:30 |  | Kenny | Ben
118 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
119 | 2002-04-11 | 11:00 | 2002-04-11 | 12:00 |  | Kenny | Ben
22 | 2002-04-13 | 1:15 | 2002-04-13 | 7:00 |  | Bryan | Art
23 | 2002-04-13 | 1:15 | 2002-04-13 | 7:00 |  | Bryan | Art
31 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Bryan | Art
32 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
33 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
34 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
36 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
37 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
38 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
39 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
40 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
41 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
115 | 2002-04-13 | 1:15 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
35 | 2002-04-13 | 1:15 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
27 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
28 | 2002-04-13 | 1:15 | 2002-04-13 | 7:00 |  | Tootie | Gilbert
29 | 2002-04-13 | 1:15 | 2002-04-13 | 6:00 |  | Tootie | Gilbert
30 | 2002-04-13 | 1:15 | 2002-04-13 | 6:00 |  | Tootie | Gilbert
21 | 2002-04-13 | 1:15 | 2002-04-13 | 6:00 |  | Tootie | Gilbert
25 | 2002-04-13 | 1:15 | 2002-04-13 | 7:30 |  | Tootie | Gilbert
20 | 2002-04-13 | 1:15 | 2002-04-13 | 7:00 |  | Tootie | Gilbert
17 | 2002-04-13 | 1:15 | 2002-04-13 | 6:00 |  | Tootie | Gilbert
18 | 2002-04-13 | 1:15 | 2002-04-13 | 6:00 |  | Tootie | Gilbert
19 | 2002-04-13 | 1:15 | 2002-04-13 | 6:00 |  | Tootie | Gilbert
52 | 2002-04-13 | 1:15 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
54 | 2002-04-13 | 2:00 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
55 | 2002-04-13 | 2:00 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
57 | 2002-04-13 | 2:00 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
58 | 2002-04-13 | 2:00 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
59 | 2002-04-13 | 2:00 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
51 | 2002-04-13 | 2:00 | 2002-04-13 | 7:40 |  | Tootie | Gilbert
115 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
114 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
113 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
49 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
50 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
51 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
52 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
57 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
58 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
59 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
1 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
2 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
3 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
4 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
5 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
7 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
8 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
9 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
13 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
14 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
15 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
17 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
18 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
19 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
1 | 2002-04-13 | 12:46 | 2002-04-13 | 13:30 |  | Tootie | Gilbert
2 | 2002-04-13 | 12:46 | 2002-04-13 | 13:30 |  | Tootie | Gilbert
3 | 2002-04-13 | 12:46 | 2002-04-13 | 13:30 |  | Tootie | Gilbert
4 | 2002-04-13 | 12:46 | 2002-04-13 | 13:30 |  | Tootie | Gilbert
5 | 2002-04-13 | 12:46 | 2002-04-13 | 13:30 |  | Tootie | Gilbert
7 | 2002-04-13 | 12:46 | 2002-04-13 | 13:30 |  | Tootie | Gilbert
8 | 2002-04-13 | 12:46 | 2002-04-13 | 13:30 |  | Tootie | Gilbert
9 | 2002-04-13 | 12:46 | 2002-04-13 | 13:30 |  | Tootie | Gilbert
13 | 2002-04-13 | 12:46 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
14 | 2002-04-13 | 12:46 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
15 | 2002-04-13 | 12:46 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
17 | 2002-04-13 | 12:46 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
114 | 2002-04-13 | 12:50 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
115 | 2002-04-13 | 12:50 | 2002-04-13 | 15:15 |  | Tootie | Gilbert
116 | 2002-04-13 | 12:50 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
60 | 2002-04-13 | 12:50 | 2002-04-13 | 13:35 |  | Tootie | Gilbert
61 | 2002-04-13 | 12:50 | 2002-04-13 | 13:35 |  | Tootie | Gilbert
63 | 2002-04-13 | 12:50 | 2002-04-13 | 13:35 |  | Tootie | Gilbert
64 | 2002-04-13 | 12:50 | 2002-04-13 | 13:35 |  | Tootie | Gilbert
65 | 2002-04-13 | 12:50 | 2002-04-13 | 13:50 |  | Tootie | Gilbert
66 | 2002-04-13 | 12:50 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
68 | 2002-04-13 | 12:50 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
18 | 2002-04-13 | 13:00 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
19 | 2002-04-13 | 13:00 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
20 | 2002-04-13 | 13:00 | 2002-04-13 | 13:45 |  | Tootie | Gilbert
21 | 2002-04-13 | 13:00 | 2002-04-13 | 14:30 |  | Tootie | Gilbert
22 | 2002-04-13 | 13:00 | 2002-04-13 | 14:30 |  | Tootie | Gilbert
23 | 2002-04-13 | 13:00 | 2002-04-13 | 14:30 |  | Tootie | Gilbert
24 | 2002-04-13 | 13:00 | 2002-04-13 | 14:30 |  | Tootie | Gilbert
25 | 2002-04-13 | 13:00 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
27 | 2002-04-13 | 13:00 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
28 | 2002-04-13 | 13:00 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
29 | 2002-04-13 | 13:00 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
30 | 2002-04-13 | 13:00 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
31 | 2002-04-13 | 13:00 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
32 | 2002-04-13 | 13:00 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
33 | 2002-04-13 | 13:00 | 2002-04-13 | 14:45 |  | Tootie | Gilbert
78 | 2002-04-13 | 13:00 | 2002-04-13 | 14:35 |  | Tootie | Gilbert
79 | 2002-04-13 | 13:00 | 2002-04-13 | 14:35 |  | Tootie | Gilbert
80 | 2002-04-13 | 13:00 | 2002-04-13 | 14:35 |  | Tootie | Gilbert
81 | 2002-04-13 | 13:00 | 2002-04-13 | 14:35 |  | Tootie | Gilbert
82 | 2002-04-13 | 13:00 | 2002-04-13 | 14:35 |  | Tootie | Gilbert
83 | 2002-04-13 | 13:00 | 2002-04-13 | 14:35 |  | Tootie | Gilbert
84 | 2002-04-13 | 13:00 | 2002-04-13 | 14:40 |  | Tootie | Gilbert
85 | 2002-04-13 | 13:00 | 2002-04-13 | 14:40 |  | Tootie | Gilbert
86 | 2002-04-13 | 13:00 | 2002-04-13 | 14:40 |  | Tootie | Gilbert
35 | 2002-04-13 | 13:10 | 2002-04-13 | 14:55 |  | Tootie | Gilbert
36 | 2002-04-13 | 13:50 | 2002-04-13 | 14:55 |  | Tootie | Gilbert
37 | 2002-04-13 | 14:00 | 2002-04-13 | 14:55 |  | Tootie | Gilbert
38 | 2002-04-13 | 14:00 | 2002-04-13 | 14:55 |  | Tootie | Gilbert
75 | 2002-04-13 | 12:55 | 2002-04-13 | 14:30 |  | Tootie | Gilbert
76 | 2002-04-13 | 12:55 | 2002-04-13 | 14:30 |  | Tootie | Gilbert
26 | 2002-04-13 | 13:50 | 2002-04-13 | 14:40 |  | Tootie | Gilbert
1 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
2 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
3 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
4 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
5 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
7 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
8 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
9 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
13 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
14 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
15 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
17 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
18 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
19 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
20 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
21 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
22 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
23 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
25 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
26 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
27 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
28 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
29 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
3 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
31 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
32 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
33 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
35 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
36 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
37 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
38 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
39 | 2002-04-14 | 21:30 | 2002-04-15 | 23:15 |  | Bryan | Art
40 | 2002-04-14 | 21:30 | 2002-04-15 | 23:15 |  | Bryan | Art
60 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
61 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
63 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
64 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
65 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
66 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
68 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
78 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
79 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
80 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
81 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
82 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
83 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
84 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
85 | 2002-04-13 | 18:30 | 2002-04-13 | 20:45 |  | Bryan | Doyle
120 | 2002-04-14 | 21:30 | 2002-04-14 | 23:15 |  | Bryan | Art
109 | 2002-04-14 | 21:30 | 2002-04-14 | 23:15 |  | Bryan | Art
105 | 2002-04-14 | 21:30 | 2002-04-14 | 23:15 |  | Bryan | Art
104 | 2002-04-14 | 21:30 | 2002-04-14 | 23:15 |  | Bryan | Art
103 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
102 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
87 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
86 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
85 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
84 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
76 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
75 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
74 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
73 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
72 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
68 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
66 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
65 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
64 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
63 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
61 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
60 | 2002-04-14 | 21:30 | 2002-04-15 | 0:30 |  | Bryan | Art
1 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
2 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
3 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
4 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
5 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
7 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
8 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
9 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
13 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
14 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
15 | 2002-04-15 | 1:45 | 2002-04-15 | 4:00 |  | Bryan | Art
17 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
18 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
19 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
20 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
21 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
22 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
23 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
24 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
25 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
26 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
27 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
28 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
29 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
30 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
31 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
32 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
33 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
60 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
61 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
63 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
64 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
65 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
66 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
68 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
69 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
71 | 2002-04-15 | 1:45 | 2002-04-15 | 3:45 |  | Bryan | Art
14 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
15 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
17 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
18 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
19 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
20 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
21 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
22 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
23 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
25 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
26 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
27 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
28 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
29 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
30 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
31 | 2002-04-15 | 8:30 | 2002-04-15 | 12:30 |  | Matt | Gilbert
32 | 2002-04-15 | 8:30 | 2002-04-15 | 12:30 |  | Matt | Gilbert
33 | 2002-04-15 | 8:30 | 2002-04-15 | 12:30 |  | Matt | Gilbert
35 | 2002-04-15 | 8:30 | 2002-04-15 | 12:30 |  | Matt | Gilbert
36 | 2002-04-15 | 8:30 | 2002-04-15 | 12:30 |  | Matt | Gilbert
37 | 2002-04-15 | 8:30 | 2002-04-15 | 12:30 |  | Matt | Gilbert
38 | 2002-04-15 | 8:30 | 2002-04-15 | 12:20 |  | Matt | Gilbert
39 | 2002-04-15 | 8:30 | 2002-04-15 | 12:20 |  | Matt | Gilbert
40 | 2002-04-15 | 8:30 | 2002-04-16 | 0:15 |  | Matt | Gilbert
42 | 2002-04-15 | 8:30 | 2002-04-15 | 12:20 |  | Matt | Gilbert
52 | 2002-04-15 | 10:15 | 2002-04-15 | 12:20 |  | Matt | Johnny
51 | 2002-04-15 | 10:15 | 2002-04-15 | 11:00 |  | Matt | Johnny
50 | 2002-04-15 | 10:15 | 2002-04-15 | 11:00 |  | Matt | Johnny
24 | 2002-04-15 | 10:15 | 2002-04-16 | 0:15 |  | Matt | Johnny
49 | 2002-04-15 | 10:15 | 2002-04-15 | 11:00 |  | Matt | Johnny
78 | 2002-04-15 | 10:15 | 2002-04-16 | 0:15 |  | Matt | Johnny
83 | 2002-04-15 | 10:15 | 2002-04-15 | 12:20 |  | Matt | Johnny
79 | 2002-04-15 | 10:15 | 2002-04-15 | 12:25 |  | Matt | Johnny
65 | 2002-04-15 | 10:15 | 2002-04-15 | 12:25 |  | Matt | Johnny
31 | 2002-04-15 | 12:50 | 2002-04-16 | 0:15 |  | Matt | Johnny
32 | 2002-04-15 | 14:10 | 2002-04-16 | 0:15 |  | Matt | Johnny
33 | 2002-04-15 | 14:10 | 2002-04-16 | 0:15 |  | Matt | Johnny
63 | 2002-04-15 | 7:40 | 2002-04-15 | 12:30 |  | Matt | Gilbert
64 | 2002-04-15 | 7:40 | 2002-04-15 | 12:30 |  | Matt | Gilbert
65 | 2002-04-15 | 7:40 | 2002-04-15 | 12:30 |  | Matt | Gilbert
68 | 2002-04-15 | 7:40 | 2002-04-15 | 12:30 |  | Matt | Gilbert
69 | 2002-04-15 | 7:40 | 2002-04-15 | 12:30 |  | Matt | Gilbert
71 | 2002-04-15 | 7:40 | 2002-04-15 | 12:30 |  | Matt | Gilbert
72 | 2002-04-15 | 7:40 | 2002-04-15 | 12:40 |  | Matt | Gilbert
73 | 2002-04-15 | 7:40 | 2002-04-15 | 12:40 |  | Matt | Gilbert
74 | 2002-04-15 | 7:40 | 2002-04-15 | 12:40 |  | Matt | Gilbert
75 | 2002-04-15 | 7:40 | 2002-04-15 | 12:40 |  | Matt | Gilbert
76 | 2002-04-15 | 7:40 | 2002-04-15 | 12:40 |  | Matt | Gilbert
84 | 2002-04-15 | 7:40 | 2002-04-15 | 12:30 |  | Matt | Gilbert
85 | 2002-04-15 | 7:40 | 2002-04-15 | 22:10 |  | Matt | Gilbert
86 | 2002-04-15 | 7:40 | 2002-04-15 | 22:10 |  | Matt | Gilbert
87 | 2002-04-15 | 7:40 | 2002-04-15 | 22:10 |  | Matt | Gilbert
88 | 2002-04-15 | 7:40 | 2002-04-15 | 22:10 |  | Matt | Gilbert
103 | 2002-04-15 | 7:40 | 2002-04-15 | 12:40 |  | Matt | Gilbert
104 | 2002-04-15 | 7:40 | 2002-04-15 | 12:40 |  | Matt | Gilbert
109 | 2002-04-15 | 7:40 | 2002-04-15 | 12:40 |  | Matt | Gilbert
120 | 2002-04-15 | 7:40 | 2002-04-15 | 12:10 |  | Matt | Gilbert
113 | 2002-04-15 | 7:40 | 2002-04-15 | 12:10 |  | Matt | Gilbert
117 | 2002-04-15 | 7:40 | 2002-04-15 | 12:10 |  | Matt | Gilbert
118 | 2002-04-15 | 7:40 | 2002-04-15 | 12:10 |  | Matt | Gilbert
121 | 2002-04-15 | 7:40 | 2002-04-15 | 12:10 |  | Matt | Gilbert
89 | 2002-04-15 | 8:20 | 2002-04-16 | 0:10 |  | Matt | Gilbert
90 | 2002-04-15 | 8:20 | 2002-04-15 | 12:10 |  | Matt | Gilbert
115 | 2002-04-15 | 8:20 | 2002-04-16 | 0:10 |  | Matt | Gilbert
116 | 2002-04-15 | 8:20 | 2002-04-15 | 10:40 |  | Matt | Gilbert
1 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
2 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
3 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
4 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
5 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
7 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
8 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
9 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
13 | 2002-04-15 | 8:20 | 2002-04-15 | 21:30 |  | Matt | Gilbert
61 | 2002-04-15 | 16:00 | 2002-04-15 | 21:50 |  | Charlie | Ben
109 | 2002-04-15 | 16:00 | 2002-04-16 | 0:30 |  | Charlie | Ben
108 | 2002-04-15 | 16:00 | 2002-04-16 | 0:30 |  | Charlie | Ben
102 | 2002-04-15 | 16:00 | 2002-04-16 | 0:30 |  | Charlie | Ben
103 | 2002-04-15 | 16:00 | 2002-04-16 | 0:30 |  | Charlie | Ben
104 | 2002-04-15 | 16:00 | 2002-04-16 | 1:50 |  | Charlie | Ben
86 | 2002-04-15 | 16:00 | 2002-04-15 | 22:10 |  | Charlie | Ben
78 | 2002-04-15 | 16:20 | 2002-04-15 | 22:10 |  | Charlie | Ben
79 | 2002-04-15 | 16:20 | 2002-04-15 | 22:10 |  | Charlie | Ben
80 | 2002-04-15 | 16:20 | 2002-04-15 | 22:10 |  | Charlie | Ben
81 | 2002-04-15 | 16:20 | 2002-04-15 | 22:10 |  | Charlie | Ben
82 | 2002-04-15 | 16:20 | 2002-04-15 | 22:10 |  | Charlie | Ben
83 | 2002-04-15 | 16:20 | 2002-04-15 | 22:10 |  | Charlie | Ben
108 | 2002-04-15 | 16:20 | 2002-04-16 | 0:30 |  | Charlie | Ben
42 | 2002-04-15 | 19:35 | 2002-04-16 | 0:30 |  | Charlie | Ben
41 | 2002-04-15 | 20:00 | 2002-04-16 | 1:05 |  | Charlie | Ben
43 | 2002-04-15 | 20:00 | 2002-04-16 | 1:05 |  | Charlie | Ben
96 | 2002-04-15 | 22:45 | 2002-04-16 | 0:30 |  | Charlie | Ben
1 | 2002-04-15 | 22:40 | 2002-04-16 | 0:30 |  | Charlie | Ben
2 | 2002-04-15 | 22:40 | 2002-04-16 | 0:30 |  | Charlie | Ben
3 | 2002-04-15 | 22:40 | 2002-04-16 | 0:30 |  | Charlie | Ben
4 | 2002-04-15 | 22:40 | 2002-04-16 | 0:30 |  | Charlie | Ben
5 | 2002-04-15 | 22:40 | 2002-04-16 | 0:30 |  | Charlie | Ben
7 | 2002-04-15 | 22:40 | 2002-04-16 | 0:30 |  | Charlie | Ben
120 | 2002-04-15 | 22:45 | 2002-04-16 | 0:40 |  | Charlie | Ben
100 | 2002-04-15 | 22:45 | 2002-04-16 | 0:35 |  | Charlie | Ben
84 | 2002-04-15 | 22:55 | 2002-04-16 | 0:35 |  | Charlie | Ben
85 | 2002-04-15 | 22:55 | 2002-04-16 | 0:35 |  | Charlie | Ben
86 | 2002-04-15 | 22:55 | 2002-04-16 | 0:35 |  | Charlie | Ben
87 | 2002-04-15 | 22:55 | 2002-04-16 | 0:35 |  | Charlie | Ben
88 | 2002-04-15 | 22:55 | 2002-04-16 | 0:35 |  | Charlie | Ben
114 | 2002-04-15 | 23:00 | 2002-04-16 | 0:35 |  | Charlie | Ben
83 | 2002-04-15 | 23:00 | 2002-04-16 | 0:35 |  | Charlie | Ben
82 | 2002-04-15 | 23:00 | 2002-04-16 | 0:35 |  | Charlie | Ben
81 | 2002-04-15 | 23:00 | 2002-04-16 | 0:35 |  | Charlie | Ben
78 | 2002-04-15 | 23:00 | 2002-04-16 | 0:35 |  | Charlie | Ben
79 | 2002-04-15 | 23:20 | 2002-04-16 | 0:35 |  | Charlie | Ben
80 | 2002-04-15 | 23:20 | 2002-04-16 | 0:35 |  | Charlie | Ben
1 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
2 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
3 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
4 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
5 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
7 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
8 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
9 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
13 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
14 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
15 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
17 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
18 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
19 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
20 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
21 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
22 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
23 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
24 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
25 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
26 | 2002-04-16 | 2:15 | 2002-04-16 | 3:10 |  | Charlie | Ben
60 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
61 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
62 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
63 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
64 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
65 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
66 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
68 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
69 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
71 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
72 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
73 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
74 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
75 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
76 | 2002-04-16 | 2:20 | 2002-04-16 | 3:15 |  | Charlie | Ben
35 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
63 | 2002-04-15 | 14:10 | 2002-04-15 | 21:50 |  | Matt | Johnny
64 | 2002-04-15 | 14:10 | 2002-04-15 | 21:50 |  | Matt | Johnny
65 | 2002-04-15 | 14:10 | 2002-04-15 | 21:50 |  | Matt | Johnny
36 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
37 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
38 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
66 | 2002-04-15 | 14:10 | 2002-04-15 | 21:50 |  | Matt | Johnny
68 | 2002-04-15 | 14:10 | 2002-04-15 | 21:50 |  | Matt | Johnny
72 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
73 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
74 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
75 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
76 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
78 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
79 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
84 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
85 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
87 | 2002-04-15 | 14:10 | 2002-04-15 | 22:30 |  | Matt | Johnny
91 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
92 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
93 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
116 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
114 | 2002-04-15 | 14:10 | 2002-04-15 | 21:30 |  | Matt | Johnny
39 | 2002-04-15 | 14:10 | 2002-04-16 | 0:20 |  | Matt | Johnny
107 | 2002-04-15 | 15:40 | 2002-04-16 | 0:20 |  | Matt | Johnny
113 | 2002-04-15 | 15:40 | 2002-04-16 | 0:20 |  | Matt | Johnny
117 | 2002-04-15 | 15:40 | 2002-04-16 | 1:20 |  | Matt | Johnny
122 | 2002-04-15 | 15:40 | 2002-04-16 | 1:20 |  | Matt | Johnny
119 | 2002-04-15 | 15:40 | 2002-04-16 | 1:20 |  | Matt | Johnny
118 | 2002-04-15 | 15:40 | 2002-04-16 | 0:20 |  | Matt | Johnny
40 | 2002-04-15 | 15:55 | 2002-04-16 | 0:20 |  | Matt | Johnny
55 | 2002-04-15 | 15:55 | 2002-04-16 | 0:20 |  | Matt | Johnny
107 | 2002-04-15 | 15:55 | 2002-04-16 | 0:20 |  | Matt | Johnny
34 | 2002-04-15 | 15:55 | 2002-04-16 | 0:20 |  | Matt | Johnny
45 | 2002-04-15 | 15:55 | 2002-04-16 | 0:20 |  | Matt | Johnny
60 | 2002-04-15 | 15:55 | 2002-04-15 | 21:50 |  | Tootie | Johnny
27 | 2002-04-16 | 2:30 | 2002-04-16 | 3:10 |  | Tootie | Johnny
28 | 2002-04-16 | 2:30 | 2002-04-16 | 3:10 |  | Tootie | Johnny
29 | 2002-04-16 | 2:30 | 2002-04-16 | 3:10 |  | Tootie | Johnny
30 | 2002-04-16 | 2:30 | 2002-04-16 | 3:10 |  | Tootie | Johnny
1 | 2002-04-16 | 6:20 | 2002-04-16 | 9:27 |  | Tootie | Johnny
2 | 2002-04-16 | 6:20 | 2002-04-16 | 9:27 |  | Tootie | Johnny
3 | 2002-04-16 | 6:20 | 2002-04-16 | 9:27 |  | Tootie | Johnny
4 | 2002-04-16 | 6:20 | 2002-04-16 | 9:27 |  | Tootie | Johnny
5 | 2002-04-16 | 6:20 | 2002-04-16 | 9:27 |  | Tootie | Johnny
7 | 2002-04-16 | 6:20 | 2002-04-16 | 9:27 |  | Tootie | Johnny
8 | 2002-04-16 | 6:20 | 2002-04-16 | 9:27 |  | Tootie | Johnny
9 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
13 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
14 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
15 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
17 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
18 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
19 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
20 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
21 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
22 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
23 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
24 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
25 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
26 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
27 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
28 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
29 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
30 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
31 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
32 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Tootie | Johnny
33 | 2002-04-16 | 6:20 | 2002-04-16 | 9:45 |  | Tootie | Johnny
34 | 2002-04-16 | 6:20 | 2002-04-16 | 9:45 |  | Tootie | Johnny
35 | 2002-04-16 | 6:20 | 2002-04-16 | 9:45 |  | Tootie | Johnny
36 | 2002-04-16 | 6:20 | 2002-04-16 | 9:45 |  | Tootie | Johnny
37 | 2002-04-16 | 6:20 | 2002-04-16 | 9:45 |  | Tootie | Johnny
38 | 2002-04-16 | 6:20 | 2002-04-16 | 9:45 |  | Tootie | Johnny
39 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
40 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
50 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
51 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
52 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
53 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
54 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
55 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
56 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
57 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
58 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
59 | 2002-04-16 | 6:20 | 2002-04-16 | 9:50 |  | Matt | Buckley
60 | 2002-04-16 | 6:20 | 2002-04-16 | 10:00 |  | Matt | Buckley
61 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
63 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
64 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
65 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
66 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
68 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
69 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
71 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
72 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
73 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
74 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
75 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
76 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
77 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
78 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
79 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
80 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
81 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
82 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
83 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
84 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
85 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
86 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
87 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
88 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
100 | 2002-04-16 | 6:20 | 2002-04-16 | 9:35 |  | Matt | Buckley
102 | 2002-04-16 | 6:30 | 2002-04-16 | 9:35 |  | Matt | Buckley
103 | 2002-04-16 | 6:30 | 2002-04-16 | 9:35 |  | Matt | Buckley
108 | 2002-04-16 | 6:30 | 2002-04-16 | 7:37 |  | Matt | Buckley
109 | 2002-04-16 | 6:30 | 2002-04-16 | 8:45 |  | Matt | Buckley
115 | 2002-04-16 | 6:30 | 2002-04-16 | 8:30 |  | Matt | Buckley
116 | 2002-04-16 | 6:30 | 2002-04-16 | 9:37 |  | Matt | Buckley
106 | 2002-04-16 | 6:30 | 2002-04-16 | 9:37 |  | Matt | Buckley
107 | 2002-04-16 | 6:30 | 2002-04-16 | 7:37 |  | Matt | Buckley
113 | 2002-04-16 | 6:30 | 2002-04-16 | 9:50 |  | Matt | Buckley
50 | 2002-04-16 | 6:30 | 2002-04-16 | 9:50 |  | Matt | Buckley
60 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
61 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
62 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
63 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
64 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
65 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
66 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
68 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
69 | 2002-04-17 | 1:50 | 2002-04-17 | 1:55 |  | Charlie | Buckley
71 | 2002-04-17 | 1:50 | 2002-04-17 | 3:15 |  | Charlie | Buckley
72 | 2002-04-17 | 1:50 | 2002-04-17 | 3:15 |  | Charlie | Buckley
74 | 2002-04-17 | 1:50 | 2002-04-17 | 3:15 |  | Charlie | Buckley
75 | 2002-04-17 | 1:50 | 2002-04-17 | 3:15 |  | Charlie | Buckley
76 | 2002-04-17 | 1:50 | 2002-04-17 | 3:15 |  | Charlie | Buckley
1 | 2002-04-17 | 2:25 | 2002-04-17 | 3:40 |  | Charlie | Buckley
2 | 2002-04-17 | 2:25 | 2002-04-17 | 3:40 |  | Charlie | Buckley
4 | 2002-04-17 | 2:25 | 2002-04-17 | 3:40 |  | Charlie | Buckley
5 | 2002-04-17 | 2:25 | 2002-04-17 | 3:40 |  | Charlie | Buckley
7 | 2002-04-17 | 2:25 | 2002-04-17 | 3:40 |  | Charlie | Buckley
9 | 2002-04-17 | 2:25 | 2002-04-17 | 8:18 |  | Charlie | Buckley
13 | 2002-04-17 | 2:25 | 2002-04-17 | 8:18 |  | Charlie | Buckley
14 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
15 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
17 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
18 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
19 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
20 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
21 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
22 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
23 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
25 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
26 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
27 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
28 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
29 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
30 | 2002-04-17 | 2:25 | 2002-04-17 | 8:25 |  | Charlie | Buckley
31 | 2002-04-17 | 2:25 | 2002-04-17 | 8:30 |  | Charlie | Buckley
32 | 2002-04-17 | 2:25 | 2002-04-17 | 8:30 |  | Charlie | Buckley
33 | 2002-04-17 | 2:25 | 2002-04-17 | 8:15 |  | Charlie | Buckley
34 | 2002-04-17 | 2:25 | 2002-04-17 | 8:15 |  | Charlie | Buckley
35 | 2002-04-17 | 2:25 | 2002-04-17 | 8:15 |  | Charlie | Buckley
36 | 2002-04-17 | 2:25 | 2002-04-17 | 8:15 |  | Charlie | Buckley
37 | 2002-04-17 | 2:25 | 2002-04-17 | 8:15 |  | Charlie | Buckley
90 | 2002-04-17 | 2:25 | 2002-04-17 | 8:15 |  | Charlie | Buckley
91 | 2002-04-17 | 2:25 | 2002-04-17 | 8:10 |  | Charlie | Buckley
92 | 2002-04-17 | 2:25 | 2002-04-17 | 8:10 |  | Charlie | Buckley
93 | 2002-04-17 | 2:25 | 2002-04-17 | 8:10 |  | Charlie | Buckley
102 | 2002-04-17 | 2:25 | 2002-04-17 | 8:10 |  | Charlie | Buckley
103 | 2002-04-17 | 2:25 | 2002-04-17 | 8:10 |  | Charlie | Buckley
104 | 2002-04-17 | 2:25 | 2002-04-17 | 8:10 |  | Charlie | Buckley
105 | 2002-04-17 | 2:25 | 2002-04-17 | 8:10 |  | Charlie | Buckley
106 | 2002-04-17 | 2:25 | 2002-04-17 | 8:10 |  | Charlie | Buckley
38 | 2002-04-17 | 2:25 | 2002-04-17 | 8:20 |  | Charlie | Buckley
39 | 2002-04-17 | 2:25 | 2002-04-17 | 8:20 |  | Charlie | Buckley
89 | 2002-04-17 | 2:25 | 2002-04-17 | 8:20 |  | Charlie | Buckley
1 | 2002-04-17 | 6:00 | 2002-04-17 | 8:20 |  | Charlie | Buckley
2 | 2002-04-17 | 6:00 | 2002-04-17 | 8:20 |  | Charlie | Buckley
3 | 2002-04-17 | 6:00 | 2002-04-17 | 8:20 |  | Charlie | Buckley
4 | 2002-04-17 | 6:00 | 2002-04-17 | 8:20 |  | Charlie | Buckley
5 | 2002-04-17 | 6:00 | 2002-04-17 | 8:20 |  | Charlie | Buckley
7 | 2002-04-17 | 6:00 | 2002-04-17 | 8:20 |  | Charlie | Buckley
8 | 2002-04-17 | 6:00 | 2002-04-17 | 8:20 |  | Charlie | Buckley
40 | 2002-04-17 | 6:00 | 2002-04-17 | 8:10 |  | Charlie | Buckley
41 | 2002-04-17 | 6:00 | 2002-04-17 | 8:10 |  | Charlie | Buckley
42 | 2002-04-17 | 6:00 | 2002-04-17 | 8:10 |  | Charlie | Buckley
43 | 2002-04-17 | 6:00 | 2002-04-17 | 8:05 |  | Charlie | Buckley
44 | 2002-04-17 | 6:00 | 2002-04-17 | 8:05 |  | Charlie | Buckley
45 | 2002-04-17 | 6:00 | 2002-04-17 | 8:05 |  | Charlie | Buckley
46 | 2002-04-17 | 6:00 | 2002-04-17 | 8:05 |  | Charlie | Buckley
47 | 2002-04-17 | 6:00 | 2002-04-17 | 8:05 |  | Charlie | Buckley
48 | 2002-04-17 | 6:00 | 2002-04-17 | 8:05 |  | Charlie | Buckley
49 | 2002-04-17 | 6:00 | 2002-04-17 | 8:05 |  | Charlie | Buckley
60 | 2002-04-17 | 6:10 | 2002-04-17 | 9:45 |  | Tootie | Art
61 | 2002-04-17 | 6:10 | 2002-04-17 | 9:45 |  | Tootie | Art
62 | 2002-04-17 | 6:10 | 2002-04-17 | 12:30 |  | Tootie | Art
63 | 2002-04-17 | 6:10 | 2002-04-17 | 12:30 |  | Tootie | Art
64 | 2002-04-17 | 6:10 | 2002-04-17 | 12:30 |  | Tootie | Art
65 | 2002-04-17 | 6:10 | 2002-04-17 | 12:30 |  | Tootie | Art
66 | 2002-04-17 | 6:10 | 2002-04-17 | 12:30 |  | Tootie | Art
68 | 2002-04-17 | 6:10 | 2002-04-17 | 8:15 |  | Tootie | Art
69 | 2002-04-17 | 6:10 | 2002-04-17 | 8:15 |  | Tootie | Art
84 | 2002-04-17 | 6:10 | 2002-04-17 | 8:15 |  | Tootie | Art
85 | 2002-04-17 | 6:10 | 2002-04-17 | 8:15 |  | Tootie | Art
86 | 2002-04-17 | 6:10 | 2002-04-17 | 8:15 |  | Tootie | Art
87 | 2002-04-17 | 6:10 | 2002-04-17 | 8:15 |  | Tootie | Art
88 | 2002-04-17 | 6:10 | 2002-04-17 | 8:15 |  | Tootie | Art
107 | 2002-04-17 | 6:10 | 2002-04-17 | 8:00 |  | Tootie | Art
118 | 2002-04-17 | 6:10 | 2002-04-17 | 8:00 |  | Tootie | Art
109 | 2002-04-17 | 6:10 | 2002-04-17 | 8:00 |  | Tootie | Art
120 | 2002-04-17 | 6:10 | 2002-04-17 | 8:00 |  | Tootie | Art
113 | 2002-04-17 | 6:10 | 2002-04-17 | 8:00 |  | Tootie | Art
114 | 2002-04-17 | 6:10 | 2002-04-17 | 8:00 |  | Tootie | Art
50 | 2002-04-17 | 7:23 | 2002-04-17 | 8:00 |  | Tootie | Art
122 | 2002-04-17 | 8:35 | 2002-04-17 | 8:48 |  | Tootie | Art
121 | 2002-04-17 | 8:35 | 2002-04-17 | 8:48 |  | Tootie | Art
118 | 2002-04-17 | 8:35 | 2002-04-17 | 8:53 |  | Tootie | Art
117 | 2002-04-17 | 8:35 | 2002-04-17 | 8:53 |  | Tootie | Art
113 | 2002-04-17 | 8:35 | 2002-04-17 | 11:40 |  | Tootie | Art
120 | 2002-04-17 | 8:35 | 2002-04-17 | 8:48 |  | Tootie | Art
109 | 2002-04-17 | 8:35 | 2002-04-17 | 11:40 |  | Tootie | Art
108 | 2002-04-17 | 8:35 | 2002-04-17 | 12:45 |  | Tootie | Art
107 | 2002-04-17 | 8:35 | 2002-04-17 | 12:45 |  | Tootie | Art
106 | 2002-04-17 | 8:35 | 2002-04-17 | 12:45 |  | Tootie | Art
105 | 2002-04-17 | 8:35 | 2002-04-17 | 12:45 |  | Tootie | Art
96 | 2002-04-17 | 8:45 | 2002-04-17 | 19:10 |  | Tootie | Art
93 | 2002-04-17 | 8:45 | 2002-04-17 | 19:10 |  | Tootie | Art
92 | 2002-04-17 | 8:45 | 2002-04-17 | 19:10
91 | 2002-04-17 | 8:45 | 2002-04-17 | 19:10 |  | Tootie | Art
37 | 2002-04-17 | 8:45 | 2002-04-17 | 9:25 |  | Tootie | Art
38 | 2002-04-17 | 8:45 | 2002-04-17 | 9:25 |  | Tootie | Art
39 | 2002-04-17 | 8:45 | 2002-04-17 | 11:45 |  | Tootie | Art
40 | 2002-04-17 | 8:45 | 2002-04-17 | 11:45 |  | Tootie | Art
41 | 2002-04-17 | 8:45 | 2002-04-17 | 11:46 |  | Tootie | Art
42 | 2002-04-17 | 8:45 | 2002-04-17 | 11:49 |  | Tootie | Art
43 | 2002-04-17 | 8:45 | 2002-04-17 | 11:57 |  | Tootie | Art
44 | 2002-04-17 | 8:45 | 2002-04-17 | 11:57 |  | Tootie | Art
45 | 2002-04-17 | 8:45 | 2002-04-17 | 11:57 |  | Tootie | Art
46 | 2002-04-17 | 8:45 | 2002-04-17 | 11:57 |  | Tootie | Art
89 | 2002-04-17 | 9:15 | 2002-04-17 | 18:10 |  | Tootie | Art
90 | 2002-04-17 | 9:15 | 2002-04-17 | 18:10 |  | Tootie | Art
4 | 2002-04-17 | 9:40 | 2002-04-17 | 18:10 |  | Tootie | Art
13 | 2002-04-17 | 9:40 | 2002-04-17 | 18:10 |  | Tootie | Art
14 | 2002-04-17 | 9:40 | 2002-04-17 | 18:10 |  | Tootie | Art
15 | 2002-04-17 | 9:40 | 2002-04-17 | 18:10 |  | Tootie | Art
25 | 2002-04-17 | 9:50 | 2002-04-17 | 18:10 |  | Tootie | Art
26 | 2002-04-17 | 9:50 | 2002-04-17 | 18:10 |  | Tootie | Art
88 | 2002-04-17 | 10:05 | 2002-04-17 | 18:10 |  | Tootie | Art
87 | 2002-04-17 | 10:05 | 2002-04-17 | 18:10 |  | Tootie | Art
83 | 2002-04-17 | 10:05 | 2002-04-17 | 18:10 |  | Tootie | Art
84 | 2002-04-17 | 10:05 | 2002-04-17 | 18:10 |  | Tootie | Art
85 | 2002-04-17 | 10:05 | 2002-04-17 | 18:20 |  | Tootie | Art
86 | 2002-04-17 | 10:05 | 2002-04-17 | 18:20 |  | Tootie | Art
17 | 2002-04-17 | 10:25 | 2002-04-17 | 18:20 |  | Tootie | Art
18 | 2002-04-17 | 10:25 | 2002-04-17 | 18:20 |  | Tootie | Art
19 | 2002-04-17 | 10:25 | 2002-04-17 | 18:20 |  | Tootie | Art
20 | 2002-04-17 | 10:25 | 2002-04-17 | 18:20 |  | Tootie | Art
21 | 2002-04-17 | 10:25 | 2002-04-17 | 18:20 |  | Tootie | Art
22 | 2002-04-17 | 10:25 | 2002-04-17 | 18:20 |  | Tootie | Art
5 | 2002-04-17 | 10:25 | 2002-04-17 | 18:20 |  | Tootie | Art
7 | 2002-04-17 | 10:25 | 2002-04-17 | 18:20 |  | Tootie | Art
8 | 2002-04-17 | 10:35 | 2002-04-17 | 18:20 |  | Tootie | Art
9 | 2002-04-17 | 10:35 | 2002-04-17 | 18:20 |  | Tootie | Art
23 | 2002-04-17 | 10:35 | 2002-04-17 | 18:20 |  | Tootie | Art
24 | 2002-04-17 | 10:35 | 2002-04-17 | 18:20 |  | Tootie | Art
27 | 2002-04-17 | 12:30 | 2002-04-17 | 19:00 |  | Tootie | Art
28 | 2002-04-17 | 12:30 | 2002-04-17 | 19:00 |  | Tootie | Art
29 | 2002-04-17 | 12:30 | 2002-04-17 | 19:00 |  | Tootie | Art
30 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
31 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
32 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
33 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
34 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
35 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
36 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
37 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
38 | 2002-04-17 | 13:00 | 2002-04-17 | 19:00 |  | Tootie | Art
100 | 2002-04-17 | 13:10 | 2002-04-17 | 18:25 |  | Tootie | Art
102 | 2002-04-17 | 13:10 | 2002-04-17 | 18:25 |  | Tootie | Art
103 | 2002-04-17 | 13:10 | 2002-04-17 | 18:25 |  | Tootie | Art
104 | 2002-04-17 | 13:10 | 2002-04-17 | 18:25 |  | Tootie | Art
105 | 2002-04-17 | 13:10 | 2002-04-17 | 18:25 |  | Tootie | Art
39 | 2002-04-17 | 13:11 | 2002-04-17 | 18:25 |  | Tootie | Art
107 | 2002-04-17 | 13:16 | 2002-04-17 | 18:25 |  | Tootie | Art
108 | 2002-04-17 | 13:16 | 2002-04-17 | 18:25 |  | Tootie | Art
109 | 2002-04-17 | 13:18 | 2002-04-17 | 18:25 |  | Tootie | Art
120 | 2002-04-17 | 13:18 | 2002-04-17 | 18:25 |  | Tootie | Art
113 | 2002-04-17 | 13:18 | 2002-04-17 | 18:25 |  | Tootie | Art
1 | 2002-04-17 | 18:35 | 2002-04-17 | 22:10 |  | Charlie | Ben
2 | 2002-04-17 | 18:35 | 2002-04-17 | 22:10 |  | Charlie | Ben
3 | 2002-04-17 | 18:35 | 2002-04-17 | 22:10 |  | Charlie | Ben
4 | 2002-04-17 | 18:35 | 2002-04-17 | 22:10 |  | Charlie | Ben
5 | 2002-04-17 | 18:35 | 2002-04-17 | 22:10 |  | Charlie | Ben
7 | 2002-04-17 | 18:35 | 2002-04-17 | 22:15 |  | Charlie | Ben
8 | 2002-04-17 | 18:35 | 2002-04-17 | 22:15 |  | Charlie | Ben
9 | 2002-04-17 | 18:35 | 2002-04-17 | 22:15 |  | Charlie | Ben
13 | 2002-04-17 | 18:35 | 2002-04-17 | 22:15 |  | Charlie | Ben
14 | 2002-04-17 | 18:35 | 2002-04-17 | 22:15 |  | Charlie | Ben
15 | 2002-04-17 | 18:35 | 2002-04-17 | 22:30 |  | Charlie | Ben
17 | 2002-04-17 | 18:35 | 2002-04-17 | 22:30 |  | Charlie | Ben
18 | 2002-04-17 | 18:35 | 2002-04-17 | 22:30 |  | Charlie | Ben
19 | 2002-04-17 | 18:35 | 2002-04-17 | 22:30 |  | Charlie | Ben
20 | 2002-04-17 | 18:35 | 2002-04-17 | 22:30 |  | Charlie | Ben
21 | 2002-04-17 | 18:35 | 2002-04-17 | 22:40 |  | Charlie | Ben
22 | 2002-04-17 | 18:35 | 2002-04-17 | 22:40 |  | Charlie | Ben
23 | 2002-04-17 | 18:35 | 2002-04-17 | 22:40 |  | Charlie | Ben
24 | 2002-04-17 | 18:35 | 2002-04-17 | 22:40 |  | Charlie | Ben
25 | 2002-04-17 | 18:35 | 2002-04-17 | 22:40 |  | Charlie | Ben
26 | 2002-04-17 | 18:35 | 2002-04-17 | 22:00 |  | Charlie | Ben
60 | 2002-04-17 | 18:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
61 | 2002-04-17 | 18:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
62 | 2002-04-17 | 18:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
63 | 2002-04-17 | 18:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
66 | 2002-04-17 | 18:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
68 | 2002-04-17 | 18:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
69 | 2002-04-17 | 18:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
71 | 2002-04-17 | 18:40 | 2002-04-17 | 22:05 |  | Charlie | Ben
72 | 2002-04-17 | 18:40 | 2002-04-17 | 22:05 |  | Charlie | Ben
73 | 2002-04-17 | 18:40 | 2002-04-17 | 22:05 |  | Charlie | Ben
74 | 2002-04-17 | 18:40 | 2002-04-17 | 22:05 |  | Charlie | Ben
83 | 2002-04-17 | 18:40 | 2002-04-17 | 22:10 |  | Charlie | Ben
84 | 2002-04-17 | 18:40 | 2002-04-17 | 22:10 |  | Charlie | Ben
85 | 2002-04-17 | 18:40 | 2002-04-17 | 22:10 |  | Charlie | Ben
86 | 2002-04-17 | 18:40 | 2002-04-17 | 22:10 |  | Charlie | Ben
87 | 2002-04-17 | 18:40 | 2002-04-17 | 22:10 |  | Charlie | Ben
82 | 2002-04-17 | 13:20 | 2002-04-17 | 19:05 |  | Tootie | Art
41 | 2002-04-17 | 14:20 | 2002-04-17 | 19:05 |  | Tootie | Art
42 | 2002-04-17 | 14:20 | 2002-04-17 | 19:05 |  | Tootie | Art
43 | 2002-04-17 | 14:20 | 2002-04-17 | 21:40 |  | Tootie | Art
81 | 2002-04-17 | 14:36 | 2002-04-17 | 19:05 |  | Tootie | Art
80 | 2002-04-17 | 14:50 | 2002-04-17 | 19:05 |  | Tootie | Art
79 | 2002-04-17 | 15:00 | 2002-04-17 | 19:05 |  | Tootie | Art
78 | 2002-04-17 | 15:00 | 2002-04-17 | 19:05 |  | Tootie | Art
77 | 2002-04-17 | 15:00 | 2002-04-17 | 19:05 |  | Tootie | Art
76 | 2002-04-17 | 15:00 | 2002-04-17 | 19:05 |  | Tootie | Art
75 | 2002-04-17 | 15:16 | 2002-04-17 | 19:05 |  | Tootie | Art
44 | 2002-04-17 | 15:18 | 2002-04-17 | 21:40 |  | Tootie | Art
45 | 2002-04-17 | 15:18 | 2002-04-17 | 21:40 |  | Tootie | Art
114 | 2002-04-17 | 15:30 | 2002-04-17 | 21:40 |  | Tootie | Art
46 | 2002-04-17 | 16:35 | 2002-04-17 | 21:40 |  | Charlie | Art
47 | 2002-04-17 | 16:35 | 2002-04-17 | 21:40 |  | Charlie | Art
49 | 2002-04-17 | 16:35 | 2002-04-17 | 21:50 |  | Charlie | Ben
50 | 2002-04-17 | 16:35 | 2002-04-17 | 21:50 |  | Charlie | Ben
51 | 2002-04-17 | 16:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
52 | 2002-04-17 | 16:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
53 | 2002-04-17 | 16:40 | 2002-04-17 | 22:00 |  | Charlie | Ben
118 | 2002-04-17 | 16:40 | 2002-04-17 | 18:30 |  | Charlie | Ben
119 | 2002-04-17 | 16:40 | 2002-04-17 | 18:30 |  | Charlie | Ben
121 | 2002-04-17 | 16:40 | 2002-04-17 | 18:30 |  | Charlie | Ben
122 | 2002-04-17 | 16:40 | 2002-04-17 | 18:30 |  | Charlie | Ben
74 | 2002-04-17 | 16:40 | 2002-04-17 | 18:30 |  | Charlie | Ben
73 | 2002-04-17 | 16:40 | 2002-04-17 | 18:30 |  | Charlie | Ben
72 | 2002-04-17 | 16:40 | 2002-04-17 | 18:30 |  | Charlie | Ben
80 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
81 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
82 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
83 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
84 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
85 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
86 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
87 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
88 | 2002-04-17 | 22:55 | 2002-04-18 | 4:40 |  | Charlie | Ben
26 | 2002-04-17 | 1:15 | 2002-04-18 | 9:00 |  | Charlie | Ben
27 | 2002-04-17 | 1:15 | 2002-04-18 | 11:20 |  | Charlie | Ben
28 | 2002-04-17 | 1:15 | 2002-04-18 | 11:20 |  | Charlie | Ben
29 | 2002-04-17 | 1:15 | 2002-04-18 | 11:20 |  | Charlie | Ben
30 | 2002-04-17 | 1:50 | 2002-04-18 | 11:20 |  | Charlie | Ben
31 | 2002-04-17 | 1:50 | 2002-04-18 | 8:10 |  | Charlie | Ben
32 | 2002-04-17 | 1:50 | 2002-04-18 | 11:20 |  | Charlie | Ben
33 | 2002-04-17 | 1:50 | 2002-04-18 | 11:20 |  | Charlie | Ben
34 | 2002-04-17 | 1:50 | 2002-04-18 | 11:20 |  | Charlie | Ben
92 | 2002-04-17 | 1:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
93 | 2002-04-17 | 1:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
35 | 2002-04-17 | 1:50 | 2002-04-18 | 11:30 |  | Charlie | Ben
96 | 2002-04-17 | 1:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
100 | 2002-04-17 | 1:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
102 | 2002-04-17 | 1:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
36 | 2002-04-17 | 1:50 | 2002-04-18 | 11:30 |  | Charlie | Ben
37 | 2002-04-18 | 5:50 | 2002-04-18 | 11:30 |  | Charlie | Ben
38 | 2002-04-18 | 5:50 | 2002-04-18 | 11:30 |  | Charlie | Ben
39 | 2002-04-18 | 5:50 | 2002-04-18 | 11:30 |  | Charlie | Ben
40 | 2002-04-18 | 5:50 | 2002-04-18 | 11:30 |  | Charlie | Ben
41 | 2002-04-18 | 5:50 | 2002-04-18 | 11:30 |  | Charlie | Ben
42 | 2002-04-18 | 5:50 | 2002-04-18 | 11:30 |  | Charlie | Ben
43 | 2002-04-18 | 5:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
44 | 2002-04-18 | 5:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
45 | 2002-04-18 | 5:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
46 | 2002-04-18 | 5:50 | 2002-04-18 | 15:30 |  | Charlie | Ben
60 | 2002-04-18 | 5:55 | 2002-04-18 | 8:15 |  | Charlie | Ben
61 | 2002-04-18 | 5:55 | 2002-04-18 | 8:15 |  | Charlie | Ben
62 | 2002-04-18 | 5:55 | 2002-04-18 | 8:15 |  | Charlie | Ben
63 | 2002-04-18 | 5:55 | 2002-04-18 | 9:00 |  | Charlie | Ben
66 | 2002-04-18 | 5:55 | 2002-04-18 | 9:00 |  | Charlie | Ben
69 | 2002-04-18 | 5:55 | 2002-04-18 | 9:50 |  | Charlie | Ben
71 | 2002-04-18 | 5:55 | 2002-04-18 | 9:50 |  | Charlie | Ben
72 | 2002-04-18 | 5:55 | 2002-04-18 | 10:20 |  | Charlie | Ben
73 | 2002-04-18 | 5:55 | 2002-04-18 | 10:20 |  | Charlie | Ben
74 | 2002-04-18 | 5:55 | 2002-04-18 | 10:35 |  | Charlie | Ben
75 | 2002-04-18 | 5:55 | 2002-04-18 | 10:35 |  | Charlie | Ben
76 | 2002-04-18 | 5:55 | 2002-04-18 | 10:40 |  | Matt | Art
77 | 2002-04-18 | 5:55 | 2002-04-18 | 11:20 |  | Matt | Art
47 | 2002-04-18 | 6:05 | 2002-04-18 | 13:30 |  | Matt | Art
80 | 2002-04-18 | 6:05 | 2002-04-18 | 11:20 |  | Matt | Art
82 | 2002-04-18 | 6:05 | 2002-04-18 | 11:20 |  | Matt | Art
65 | 2002-04-18 | 7:35 | 2002-04-18 | 9:00 |  | Matt | Art
23 | 2002-04-18 | 8:10 | 2002-04-18 | 15:30 |  | Matt | Art
49 | 2002-04-18 | 8:10 | 2002-04-18 | 9:00 |  | Matt | Art
50 | 2002-04-18 | 8:10 | 2002-04-18 | 9:00 |  | Matt | Art
83 | 2002-04-18 | 8:10 | 2002-04-18 | 11:30 |  | Matt | Art
84 | 2002-04-18 | 8:10 | 2002-04-18 | 12:00 |  | Matt | Art
85 | 2002-04-18 | 8:10 | 2002-04-18 | 12:00 |  | Matt | Art
51 | 2002-04-18 | 8:10 | 2002-04-18 | 9:00 |  | Matt | Art
52 | 2002-04-18 | 8:10 | 2002-04-18 | 9:00 |  | Matt | Art
88 | 2002-04-18 | 8:50 | 2002-04-18 | 12:00 |  | Matt | Art
87 | 2002-04-18 | 8:50 | 2002-04-18 | 12:00 |  | Matt | Art
68 | 2002-04-18 | 5:55 | 2002-04-18 | 9:00 |  | Matt | Art
1 | 2002-04-18 | 9:50 | 2002-04-18 | 11:20 |  | Matt | Art
2 | 2002-04-18 | 9:50 | 2002-04-18 | 11:20 |  | Matt | Art
3 | 2002-04-18 | 9:50 | 2002-04-18 | 11:20 |  | Matt | Art
5 | 2002-04-18 | 9:50 | 2002-04-18 | 10:40 |  | Matt | Art
7 | 2002-04-18 | 9:50 | 2002-04-18 | 10:40 |  | Matt | Art
9 | 2002-04-18 | 10:20 | 2002-04-18 | 12:00 |  | Matt | Art
69 | 2002-04-18 | 10:45 | 2002-04-18 | 11:20 |  | Matt | Art
78 | 2002-04-18 | 8:05 | 2002-04-18 | 11:20 |  | Matt | Art
79 | 2002-04-18 | 8:05 | 2002-04-18 | 11:20 |  | Matt | Art
41 | 2002-04-18 | 11:30 | 2002-04-18 | 12:00 |  | Matt | Art
42 | 2002-04-18 | 11:30 | 2002-04-18 | 13:30 |  | Matt | Art
88 | 2002-04-18 | 12:15 | 2002-04-18 | 12:30 |  | Matt | Art
87 | 2002-04-18 | 12:15 | 2002-04-18 | 12:30 |  | Matt | Art
1 | 2002-04-18 | 12:30 | 2002-04-18 | 15:30 |  | Matt | Art
2 | 2002-04-18 | 12:30 | 2002-04-18 | 15:30 |  | Matt | Art
3 | 2002-04-18 | 12:30 | 2002-04-18 | 15:30 |  | Matt | Art
4 | 2002-04-18 | 12:30 | 2002-04-18 | 15:30 |  | Matt | Art
5 | 2002-04-18 | 12:30 | 2002-04-18 | 15:30 |  | Matt | Art
7 | 2002-04-18 | 12:30 | 2002-04-18 | 15:30 |  | Matt | Art
88 | 2002-04-17 | 18:40 | 2002-04-17 | 21:50 |  | Charlie | Ben
89 | 2002-04-17 | 18:40 | 2002-04-17 | 21:50 |  | Charlie | Ben
90 | 2002-04-17 | 18:40 | 2002-04-17 | 21:50 |  | Charlie | Ben
100 | 2002-04-17 | 18:45 | 2002-04-17 | 21:50 |  | Charlie | Ben
102 | 2002-04-17 | 18:45 | 2002-04-17 | 21:50 |  | Charlie | Ben
103 | 2002-04-17 | 18:45 | 2002-04-17 | 21:50 |  | Charlie | Ben
104 | 2002-04-17 | 18:45 | 2002-04-17 | 21:50 |  | Charlie | Ben
105 | 2002-04-17 | 18:45 | 2002-04-17 | 21:50 |  | Charlie | Ben
106 | 2002-04-17 | 18:45 | 2002-04-17 | 21:50 |  | Charlie | Ben
89 | 2002-04-17 | 23:00 | 2002-04-18 | 15:50 |  | Charlie | Ben
90 | 2002-04-17 | 23:00 | 2002-04-18 | 16:15 |  | Charlie | Ben
91 | 2002-04-17 | 23:00 | 2002-04-18 | 15:50 |  | Charlie | Ben
1 | 2002-04-17 | 0:40 | 2002-04-18 | 4:40 |  | Charlie | Ben
2 | 2002-04-17 | 0:40 | 2002-04-18 | 4:40 |  | Charlie | Ben
3 | 2002-04-17 | 0:40 | 2002-04-18 | 4:40 |  | Charlie | Ben
4 | 2002-04-17 | 0:40 | 2002-04-18 | 5:55 |  | Charlie | Ben
5 | 2002-04-17 | 0:40 | 2002-04-18 | 5:55 |  | Charlie | Ben
7 | 2002-04-17 | 0:40 | 2002-04-18 | 7:30 |  | Charlie | Ben
8 | 2002-04-17 | 0:40 | 2002-04-18 | 7:30 |  | Charlie | Ben
9 | 2002-04-17 | 0:40 | 2002-04-18 | 7:30 |  | Charlie | Ben
13 | 2002-04-17 | 0:40 | 2002-04-18 | 7:50 |  | Charlie | Ben
14 | 2002-04-17 | 0:40 | 2002-04-18 | 8:50 |  | Charlie | Ben
15 | 2002-04-17 | 0:40 | 2002-04-18 | 7:50 |  | Charlie | Ben
17 | 2002-04-17 | 0:40 | 2002-04-18 | 7:50 |  | Charlie | Ben
18 | 2002-04-17 | 0:40 | 2002-04-18 | 7:50 |  | Charlie | Ben
19 | 2002-04-17 | 0:40 | 2002-04-18 | 7:50 |  | Charlie | Ben
20 | 2002-04-17 | 0:40 | 2002-04-18 | 7:50 |  | Charlie | Ben
21 | 2002-04-17 | 0:40 | 2002-04-18 | 7:50 |  | Charlie | Ben
22 | 2002-04-17 | 0:40 | 2002-04-18 | 7:50 |  | Charlie | Ben
118 | 2002-04-17 | 0:45 | 2002-04-18 | 15:45 |  | Charlie | Ben
119 | 2002-04-17 | 0:45 | 2002-04-18 | 15:45 |  | Charlie | Ben
121 | 2002-04-17 | 0:45 | 2002-04-18 | 12:30 |  | Charlie | Ben
122 | 2002-04-17 | 0:45 | 2002-04-18 | 12:30 |  | Charlie | Ben
117 | 2002-04-17 | 0:45 | 2002-04-18 | 15:45 |  | Charlie | Ben
23 | 2002-04-17 | 0:45 | 2002-04-18 | 8:00 |  | Charlie | Ben
24 | 2002-04-17 | 0:45 | 2002-04-18 | 8:50 |  | Charlie | Ben
25 | 2002-04-17 | 0:45 | 2002-04-18 | 9:00 |  | Charlie | Ben
113 | 2002-04-18 | 12:30 | 2002-04-18 | 15:15 |  | Matt | Johnny
103 | 2002-04-18 | 12:30 | 2002-04-18 | 15:50 |  | Matt | Johnny
104 | 2002-04-18 | 12:30 | 2002-04-18 | 15:50 |  | Matt | Johnny
105 | 2002-04-18 | 12:30 | 2002-04-18 | 15:50 |  | Matt | Johnny
41 | 2002-04-18 | 12:30 | 2002-04-18 | 14:40 |  | Matt | Johnny
8 | 2002-04-18 | 12:50 | 2002-04-18 | 14:07 |  | Matt | Johnny
9 | 2002-04-18 | 12:50 | 2002-04-18 | 18:15 |  | Matt | Johnny
13 | 2002-04-18 | 12:50 | 2002-04-18 | 18:15 |  | Matt | Johnny
14 | 2002-04-18 | 12:50 | 2002-04-18 | 18:15 |  | Matt | Johnny
17 | 2002-04-18 | 12:50 | 2002-04-18 | 18:15 |  | Matt | Johnny
69 | 2002-04-18 | 12:50 | 2002-04-18 | 15:45 |  | Matt | Johnny
65 | 2002-04-18 | 12:50 | 2002-04-18 | 14:55 |  | Matt | Johnny
18 | 2002-04-18 | 12:50 | 2002-04-18 | 14:55 |  | Matt | Johnny
19 | 2002-04-18 | 12:50 | 2002-04-18 | 15:15 |  | Matt | Johnny
66 | 2002-04-18 | 12:50 | 2002-04-18 | 15:45 |  | Matt | Johnny
68 | 2002-04-18 | 12:50 | 2002-04-18 | 18:15 |  | Matt | Johnny
20 | 2002-04-18 | 13:00 | 2002-04-18 | 13:20 |  | Matt | Johnny
21 | 2002-04-18 | 13:00 | 2002-04-18 | 13:35 |  | Matt | Johnny
22 | 2002-04-18 | 13:00 | 2002-04-18 | 13:35 |  | Matt | Johnny
23 | 2002-04-18 | 13:00 | 2002-04-18 | 20:25 |  | Matt | Johnny
24 | 2002-04-18 | 13:00 | 2002-04-18 | 20:25 |  | Matt | Johnny
25 | 2002-04-18 | 13:00 | 2002-04-18 | 20:25 |  | Matt | Johnny
69 | 2002-04-18 | 13:00 | 2002-04-18 | 18:15 |  | Matt | Johnny
71 | 2002-04-18 | 13:00 | 2002-04-18 | 20:20 |  | Matt | Johnny
63 | 2002-04-18 | 13:00 | 2002-04-18 | 15:45 |  | Matt | Johnny
26 | 2002-04-18 | 13:00 | 2002-04-18 | 15:05 |  | Matt | Johnny
15 | 2002-04-18 | 13:15 | 2002-04-18 | 20:25 |  | Matt | Johnny
27 | 2002-04-18 | 13:15 | 2002-04-18 | 15:30 |  | Matt | Johnny
28 | 2002-04-18 | 13:15 | 2002-04-18 | 15:45 |  | Matt | Johnny
29 | 2002-04-18 | 13:15 | 2002-04-18 | 20:25 |  | Matt | Johnny
30 | 2002-04-18 | 13:15 | 2002-04-18 | 20:25 |  | Matt | Johnny
31 | 2002-04-18 | 13:15 | 2002-04-18 | 14:07 |  | Matt | Johnny
32 | 2002-04-18 | 13:15 | 2002-04-18 | 20:35 |  | Matt | Johnny
33 | 2002-04-18 | 13:15 | 2002-04-18 | 20:35 |  | Matt | Johnny
34 | 2002-04-18 | 13:15 | 2002-04-18 | 20:35 |  | Matt | Johnny
35 | 2002-04-18 | 13:15 | 2002-04-18 | 20:35 |  | Matt | Johnny
72 | 2002-04-18 | 13:15 | 2002-04-18 | 15:50 |  | Matt | Duvall
73 | 2002-04-18 | 13:15 | 2002-04-18 | 15:50 |  | Matt | Duvall
74 | 2002-04-18 | 13:15 | 2002-04-18 | 15:50 |  | Matt | Duvall
75 | 2002-04-18 | 13:15 | 2002-04-18 | 14:15 |  | Matt | Duvall
76 | 2002-04-18 | 13:15 | 2002-04-18 | 14:15 |  | Matt | Duvall
77 | 2002-04-18 | 13:15 | 2002-04-18 | 15:50 |  | Matt | Duvall
78 | 2002-04-18 | 13:15 | 2002-04-18 | 15:50 |  | Matt | Duvall
36 | 2002-04-18 | 13:15 | 2002-04-18 | 15:50 |  | Matt | Duvall
79 | 2002-04-18 | 13:15 | 2002-04-18 | 14:15 |  | Matt | Duvall
80 | 2002-04-18 | 13:15 | 2002-04-18 | 14:15 |  | Matt | Duvall
81 | 2002-04-18 | 13:30 | 2002-04-18 | 14:15 |  | Matt | Duvall
18 | 2002-04-18 | 13:30 | 2002-04-18 | 20:35 |  | Matt | Duvall
37 | 2002-04-18 | 13:30 | 2002-04-18 | 20:35 |  | Matt | Duvall
38 | 2002-04-18 | 13:30 | 2002-04-18 | 20:35 |  | Matt | Duvall
39 | 2002-04-18 | 13:30 | 2002-04-18 | 20:35 |  | Matt | Duvall
40 | 2002-04-18 | 13:30 | 2002-04-18 | 20:35 |  | Matt | Duvall
49 | 2002-04-18 | 13:30 | 2002-04-18 | 20:35 |  | Matt | Duvall
82 | 2002-04-18 | 13:30 | 2002-04-18 | 14:15 |  | Matt | Duvall
114 | 2002-04-18 | 15:50 | 2002-04-18 | 20:40 |  | Matt | Duvall
115 | 2002-04-18 | 15:50 | 2002-04-18 | 20:40 |  | Matt | Duvall
50 | 2002-04-18 | 15:50 | 2002-04-18 | 20:40 |  | Matt | Duvall
51 | 2002-04-18 | 15:50 | 2002-04-18 | 20:40 |  | Matt | Duvall
52 | 2002-04-18 | 15:50 | 2002-04-18 | 20:40 |  | Matt | Duvall
23 | 2002-04-18 | 16:00 | 2002-04-18 | 20:40 |  | Matt | Duvall
24 | 2002-04-18 | 16:00 | 2002-04-18 | 20:40 |  | Matt | Duvall
25 | 2002-04-18 | 16:00 | 2002-04-18 | 20:40 |  | Matt | Duvall
72 | 2002-04-18 | 16:15 | 2002-04-18 | 18:30 |  | Matt | Duvall
73 | 2002-04-18 | 16:15 | 2002-04-18 | 18:30 |  | Matt | Duvall
74 | 2002-04-18 | 16:15 | 2002-04-18 | 20:20 |  | Matt | Duvall
75 | 2002-04-18 | 16:15 | 2002-04-18 | 20:40 |  | Matt | Duvall
76 | 2002-04-18 | 16:15 | 2002-04-18 | 20:40 |  | Matt | Duvall
1 | 2002-04-18 | 17:20 | 2002-04-18 | 20:50 |  | Matt | Duvall
2 | 2002-04-18 | 17:20 | 2002-04-18 | 20:50 |  | Matt | Duvall
3 | 2002-04-18 | 17:20 | 2002-04-18 | 20:50 |  | Matt | Duvall
4 | 2002-04-18 | 17:20 | 2002-04-18 | 20:50 |  | Matt | Duvall
90 | 2002-04-18 | 21:50 | 2002-04-18 | 22:50 |  | Charlie | Art
91 | 2002-04-18 | 21:50 | 2002-04-18 | 22:50 |  | Charlie | Art
92 | 2002-04-18 | 21:50 | 2002-04-18 | 22:50 |  | Charlie | Art
40 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
41 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
42 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
43 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
44 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
45 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
46 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
47 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
48 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
49 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
50 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
51 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
52 | 2002-04-18 | 21:55 | 2002-04-18 | 22:55 |  | Charlie | Art
55 | 2002-04-18 | 21:55 | 2002-04-18 | 22:35 |  | Charlie | Art
56 | 2002-04-18 | 21:55 | 2002-04-18 | 22:35 |  | Charlie | Art
93 | 2002-04-18 | 22:00 | 2002-04-18 | 22:50 |  | Charlie | Art
96 | 2002-04-18 | 22:00 | 2002-04-18 | 22:50 |  | Charlie | Art
100 | 2002-04-18 | 22:00 | 2002-04-18 | 22:50 |  | Charlie | Art
57 | 2002-04-18 | 22:00 | 2002-04-18 | 22:35 |  | Charlie | Art
58 | 2002-04-18 | 22:00 | 2002-04-18 | 22:35 |  | Charlie | Art
59 | 2002-04-18 | 22:00 | 2002-04-18 | 22:35 |  | Charlie | Art
102 | 2002-04-18 | 22:00 | 2002-04-18 | 22:50 |  | Charlie | Art
103 | 2002-04-18 | 22:00 | 2002-04-18 | 22:50 |  | Charlie | Art
1 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
2 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
3 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
4 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
5 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
7 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
8 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
9 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
13 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
14 | 2002-04-18 | 22:10 | 2002-04-18 | 22:55 |  | Charlie | Art
15 | 2002-04-18 | 22:15 | 2002-04-18 | 22:55 |  | Charlie | Art
17 | 2002-04-18 | 22:15 | 2002-04-18 | 22:55 |  | Charlie | Art
1 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
2 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
3 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
4 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
5 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
7 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
8 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
9 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
13 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
14 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
15 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
17 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
18 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
20 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
21 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
22 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
23 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
24 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
25 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
26 | 2002-04-18 | 23:50 | 2002-04-19 | 3:25 |  | Charlie | Art
63 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
64 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
65 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
66 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
68 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
69 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
71 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
72 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
73 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
74 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
75 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
76 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
77 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
78 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
79 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
80 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
81 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
82 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
83 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
84 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
27 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
28 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
29 | 2002-04-19 | 0:01 | 2002-04-19 | 3:30 |  | Charlie | Art
30 | 2002-04-19 | 0:10 | 2002-04-19 | 3:30 |  | Charlie | Art
32 | 2002-04-19 | 0:10 | 2002-04-19 | 3:30 |  | Charlie | Art
33 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
34 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
35 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
36 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
37 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
85 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
86 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
87 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
88 | 2002-04-19 | 1:00 | 2002-04-19 | 3:30 |  | Charlie | Art
38 | 2002-04-19 | 1:35 | 2002-04-19 | 3:30 |  | Charlie | Art
5 | 2002-04-18 | 17:20 | 2002-04-18 | 20:50 |  | Charlie | Ben
7 | 2002-04-18 | 17:35 | 2002-04-18 | 20:50 |  | Charlie | Ben
8 | 2002-04-18 | 17:35 | 2002-04-18 | 20:50 |  | Charlie | Ben
120 | 2002-04-18 | 16:10 | 2002-04-18 | 20:45 |  | Charlie | Ben
20 | 2002-04-18 | 17:40 | 2002-04-18 | 21:00 |  | Charlie | Ben
21 | 2002-04-18 | 17:40 | 2002-04-18 | 21:00 |  | Charlie | Ben
22 | 2002-04-18 | 17:40 | 2002-04-18 | 21:00 |  | Charlie | Ben
26 | 2002-04-18 | 17:40 | 2002-04-18 | 20:50 |  | Charlie | Ben
63 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
64 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
65 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
66 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
77 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
78 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
79 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
80 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
81 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
82 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
83 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
84 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
85 | 2002-04-18 | 17:45 | 2002-04-18 | 20:30 |  | Charlie | Ben
27 | 2002-04-18 | 17:45 | 2002-04-18 | 20:50 |  | Charlie | Ben
28 | 2002-04-18 | 17:55 | 2002-04-18 | 20:50 |  | Charlie | Ben
36 | 2002-04-18 | 18:05 | 2002-04-18 | 21:05 |  | Charlie | Ben
39 | 2002-04-18 | 18:05 | 2002-04-18 | 20:45 |  | Charlie | Ben
86 | 2002-04-18 | 18:05 | 2002-04-18 | 20:45 |  | Charlie | Ben
87 | 2002-04-18 | 18:05 | 2002-04-18 | 21:05 |  | Charlie | Ben
42 | 2002-04-18 | 18:15 | 2002-04-18 | 21:05 |  | Charlie | Ben
88 | 2002-04-18 | 18:15 | 2002-04-18 | 20:45 |  | Charlie | Ben
89 | 2002-04-18 | 18:20 | 2002-04-18 | 20:45 |  | Charlie | Ben
43 | 2002-04-18 | 19:50 | 2002-04-18 | 20:45 |  | Charlie | Ben
44 | 2002-04-18 | 19:50 | 2002-04-18 | 20:45 |  | Charlie | Ben
118 | 2002-04-18 | 19:50 | 2002-04-18 | 20:45 |  | Charlie | Ben
119 | 2002-04-18 | 19:50 | 2002-04-18 | 20:45 |  | Charlie | Ben
122 | 2002-04-18 | 19:50 | 2002-04-18 | 20:45 |  | Charlie | Ben
113 | 2002-04-18 | 20:00 | 2002-04-18 | 20:45 |  | Charlie | Ben
108 | 2002-04-18 | 20:00 | 2002-04-18 | 20:45 |  | Charlie | Ben
109 | 2002-04-18 | 20:00 | 2002-04-18 | 20:45 |  | Charlie | Duvall
55 | 2002-04-18 | 20:00 | 2002-04-18 | 21:10 |  | Charlie | Duvall
45 | 2002-04-18 | 20:00 | 2002-04-18 | 21:10 |  | Charlie | Duvall
72 | 2002-04-18 | 20:00 | 2002-04-18 | 20:45 |  | Charlie | Duvall
73 | 2002-04-18 | 20:00 | 2002-04-18 | 20:45 |  | Charlie | Duvall
63 | 2002-04-18 | 21:10 | 2002-04-18 | 22:30 |  | Charlie | Duvall
64 | 2002-04-18 | 21:10 | 2002-04-18 | 22:30 |  | Charlie | Duvall
65 | 2002-04-18 | 21:10 | 2002-04-18 | 22:30 |  | Charlie | Duvall
66 | 2002-04-18 | 21:15 | 2002-04-18 | 22:30 |  | Charlie | Duvall
68 | 2002-04-18 | 21:15 | 2002-04-18 | 22:30 |  | Charlie | Duvall
69 | 2002-04-18 | 21:15 | 2002-04-18 | 22:30 |  | Charlie | Duvall
71 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
72 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
73 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
74 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
75 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
76 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
77 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
78 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
79 | 2002-04-18 | 21:20 | 2002-04-18 | 22:40 |  | Charlie | Duvall
81 | 2002-04-18 | 21:20 | 2002-04-18 | 22:45 |  | Charlie | Duvall
82 | 2002-04-18 | 21:20 | 2002-04-18 | 22:45 |  | Charlie | Duvall
83 | 2002-04-18 | 21:20 | 2002-04-18 | 22:45 |  | Charlie | Duvall
84 | 2002-04-18 | 21:25 | 2002-04-18 | 22:45 |  | Charlie | Duvall
85 | 2002-04-18 | 21:25 | 2002-04-18 | 22:45 |  | Charlie | Duvall
86 | 2002-04-18 | 21:40 | 2002-04-18 | 22:45 |  | Charlie | Duvall
87 | 2002-04-18 | 21:40 | 2002-04-18 | 22:45 |  | Charlie | Duvall
88 | 2002-04-18 | 21:40 | 2002-04-18 | 22:45 |  | Charlie | Duvall
89 | 2002-04-18 | 21:40 | 2002-04-18 | 22:45 |  | Charlie | Duvall
32 | 2002-04-18 | 21:45 | 2002-04-18 | 22:30 |  | Charlie | Duvall
33 | 2002-04-18 | 21:45 | 2002-04-18 | 22:30 |  | Charlie | Duvall
34 | 2002-04-18 | 21:45 | 2002-04-18 | 22:30 |  | Charlie | Duvall
35 | 2002-04-18 | 21:45 | 2002-04-18 | 22:30 |  | Charlie | Duvall
36 | 2002-04-18 | 21:45 | 2002-04-18 | 22:30 |  | Charlie | Duvall
37 | 2002-04-18 | 21:45 | 2002-04-18 | 22:30 |  | Charlie | Duvall
38 | 2002-04-18 | 21:45 | 2002-04-18 | 22:30 |  | Charlie | Duvall
39 | 2002-04-18 | 21:45 | 2002-04-18 | 22:30 |  | Charlie | Duvall
41 | 2002-04-19 | 3:50 | 2002-04-19 | 4:50 |  | Kenny | Ben
40 | 2002-04-19 | 3:50 | 2002-04-19 | 4:50 |  | Kenny | Ben
39 | 2002-04-19 | 3:50 | 2002-04-19 | 4:50 |  | Kenny | Ben
38 | 2002-04-19 | 3:50 | 2002-04-19 | 4:50 |  | Kenny | Ben
37 | 2002-04-19 | 3:50 | 2002-04-20 | 18:30 |  | Kenny | Ben
36 | 2002-04-19 | 3:50 | 2002-04-20 | 18:30 |  | Kenny | Ben
35 | 2002-04-19 | 3:50 | 2002-04-20 | 13:00 |  | Kenny | Ben
34 | 2002-04-19 | 3:50 | 2002-04-20 | 18:30 |  | Kenny | Ben
33 | 2002-04-19 | 3:50 | 2002-04-20 | 18:30 |  | Kenny | Ben
32 | 2002-04-19 | 3:50 | 2002-04-20 | 18:30 |  | Kenny | Ben
30 | 2002-04-19 | 3:55 | 2002-04-20 | 18:30 |  | Kenny | Ben
29 | 2002-04-19 | 3:55 | 2002-04-20 | 18:30 |  | Kenny | Ben
28 | 2002-04-19 | 3:55 | 2002-04-20 | 13:00 |  | Kenny | Ben
27 | 2002-04-19 | 3:55 | 2002-04-20 | 13:00 |  | Kenny | Ben
38 | 2002-04-19 | 5:20 | 2002-04-20 | 18:30 |  | Kenny | Ben
39 | 2002-04-19 | 5:20 | 2002-04-20 | 18:30 |  | Kenny | Ben
40 | 2002-04-19 | 5:20 | 2002-04-20 | 18:30 |  | Kenny | Ben
41 | 2002-04-19 | 5:20 | 2002-04-20 | 19:30 |  | Kenny | Ben
84 | 2002-04-19 | 5:30 | 2002-04-20 | 16:45 |  | Kenny | Ben
85 | 2002-04-19 | 5:30 | 2002-04-20 | 16:45 |  | Kenny | Ben
86 | 2002-04-19 | 5:30 | 2002-04-20 | 16:45 |  | Kenny | Ben
23 | 2002-04-19 | 5:30 | 2002-04-20 | 13:00 |  | Kenny | Ben
24 | 2002-04-19 | 5:30 | 2002-04-20 | 13:00 |  | Kenny | Ben
25 | 2002-04-19 | 5:30 | 2002-04-20 | 13:00 |  | Kenny | Ben
26 | 2002-04-19 | 5:30 | 2002-04-20 | 13:00 |  | Kenny | Ben
22 | 2002-04-19 | 7:30 | 2002-04-20 | 19:30 |  | Kenny | Ben
21 | 2002-04-19 | 7:30 | 2002-04-20 | 19:30 |  | Kenny | Ben
20 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
19 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
18 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
17 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
15 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
14 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
13 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
9 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
8 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
7 | 2002-04-19 | 7:30 | 2002-04-20 | 9:45 |  | Kenny | Ben
5 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
4 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
3 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
2 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
1 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
122 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
119 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
109 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
108 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
116 | 2002-04-19 | 7:30 | 2002-04-19 | 20:30 |  | Kenny | Art
18 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
21 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
42 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
43 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
44 | 2002-04-19 | 9:00 | 2002-04-19 | 22:30 |  | Kenny | Art
45 | 2002-04-19 | 9:00 | 2002-04-19 | 22:30 |  | Kenny | Art
83 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
82 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
81 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
80 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
79 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
78 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
77 | 2002-04-19 | 9:00 | 2002-04-19 | 20:30 |  | Kenny | Art
46 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
47 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
49 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
75 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
76 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
74 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
73 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
72 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
115 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
71 | 2002-04-19 | 10:00 | 2002-04-19 | 22:30 |  | Kenny | Art
68 | 2002-04-19 | 13:00 | 2002-04-19 | 22:30 |  | Kenny | Art
69 | 2002-04-19 | 13:00 | 2002-04-19 | 22:30 |  | Kenny | Art
50 | 2002-04-19 | 13:00 | 2002-04-19 | 22:30 |  | Kenny | Art
51 | 2002-04-19 | 13:00 | 2002-04-19 | 22:30 |  | Kenny | Art
52 | 2002-04-19 | 15:30 | 2002-04-19 | 20:30 |  | Kenny | Art
65 | 2002-04-19 | 15:30 | 2002-04-19 | 20:30 |  | Kenny | Art
114 | 2002-04-19 | 15:30 | 2002-04-19 | 20:30 |  | Kenny | Art
66 | 2002-04-19 | 15:30 | 2002-04-19 | 20:30 |  | Kenny | Art
122 | 2002-04-19 | 3:45 | 2002-04-19 | 4:45 |  | Kenny | Ben
119 | 2002-04-19 | 3:45 | 2002-04-19 | 4:45 |  | Kenny | Ben
118 | 2002-04-19 | 3:45 | 2002-04-19 | 4:45 |  | Kenny | Ben
117 | 2002-04-19 | 3:45 | 2002-04-19 | 4:45 |  | Kenny | Ben
113 | 2002-04-19 | 3:45 | 2002-04-19 | 4:50 |  | Kenny | Ben
120 | 2002-04-19 | 3:45 | 2002-04-19 | 5:00 |  | Kenny | Ben
109 | 2002-04-19 | 3:45 | 2002-04-19 | 5:00 |  | Kenny | Ben
108 | 2002-04-19 | 3:45 | 2002-04-19 | 5:00 |  | Kenny | Ben
107 | 2002-04-19 | 3:45 | 2002-04-20 | 8:45 |  | Kenny | Ben
106 | 2002-04-19 | 3:45 | 2002-04-20 | 8:45 |  | Kenny | Ben
105 | 2002-04-19 | 3:45 | 2002-04-20 | 8:45 |  | Kenny | Ben
104 | 2002-04-19 | 3:45 | 2002-04-20 | 8:45 |  | Kenny | Ben
103 | 2002-04-19 | 3:45 | 2002-04-20 | 13:00 |  | Kenny | Ben
102 | 2002-04-19 | 3:45 | 2002-04-20 | 13:00 |  | Kenny | Ben
100 | 2002-04-19 | 3:45 | 2002-04-20 | 20:30 |  | Kenny | Ben
96 | 2002-04-19 | 3:45 | 2002-04-20 | 20:30 |  | Kenny | Ben
93 | 2002-04-19 | 3:45 | 2002-04-20 | 20:30 |  | Kenny | Ben
92 | 2002-04-19 | 3:45 | 2002-04-20 | 20:30 |  | Kenny | Ben
91 | 2002-04-19 | 3:45 | 2002-04-20 | 20:30 |  | Kenny | Ben
90 | 2002-04-19 | 3:45 | 2002-04-20 | 20:00 |  | Kenny | Ben
89 | 2002-04-19 | 3:45 | 2002-04-20 | 20:00 |  | Kenny | Ben
88 | 2002-04-19 | 3:45 | 2002-04-20 | 19:30 |  | Kenny | Ben
87 | 2002-04-19 | 3:45 | 2002-04-20 | 19:30 |  | Kenny | Ben
59 | 2002-04-19 | 3:50 | 2002-04-19 | 4:30 |  | Kenny | Ben
58 | 2002-04-19 | 3:50 | 2002-04-19 | 4:30 |  | Kenny | Ben
57 | 2002-04-19 | 3:50 | 2002-04-19 | 4:30 |  | Kenny | Ben
56 | 2002-04-19 | 3:50 | 2002-04-19 | 4:30 |  | Kenny | Ben
55 | 2002-04-19 | 3:50 | 2002-04-19 | 4:35 |  | Kenny | Ben
52 | 2002-04-19 | 3:50 | 2002-04-19 | 4:35 |  | Kenny | Ben
50 | 2002-04-19 | 3:50 | 2002-04-19 | 4:35 |  | Kenny | Ben
49 | 2002-04-19 | 3:50 | 2002-04-19 | 4:40 |  | Kenny | Ben
47 | 2002-04-19 | 3:50 | 2002-04-19 | 4:40 |  | Kenny | Ben
46 | 2002-04-19 | 3:50 | 2002-04-19 | 4:40 |  | Kenny | Ben
45 | 2002-04-19 | 3:50 | 2002-04-19 | 4:40 |  | Kenny | Ben
44 | 2002-04-19 | 3:50 | 2002-04-19 | 4:40 |  | Kenny | Ben
43 | 2002-04-19 | 3:50 | 2002-04-19 | 4:40 |  | Kenny | Ben
42 | 2002-04-19 | 3:50 | 2002-04-19 | 4:40 |  | Kenny | Ben
42 | 2002-04-19 | 23:30 | 2002-04-20 | 20:00 |  | Kenny | Ben
43 | 2002-04-19 | 23:30 | 2002-04-20 | 20:00 |  | Kenny | Ben
63 | 2002-04-19 | 23:30 | 2002-04-20 | 12:45 |  | Kenny | Ben
64 | 2002-04-19 | 23:30 | 2002-04-20 | 12:45 |  | Kenny | Ben
65 | 2002-04-19 | 23:30 | 2002-04-20 | 18:30 |  | Kenny | Ben
5 | 2002-04-19 | 23:30 | 2002-04-20 | 20:45 |  | Kenny | Ben
66 | 2002-04-19 | 23:30 | 2002-04-20 | 18:30 |  | Kenny | Ben
68 | 2002-04-19 | 23:30 | 2002-04-20 | 19:30 |  | Kenny | Ben
69 | 2002-04-19 | 23:30 | 2002-04-20 | 19:30 |  | Kenny | Ben
35 | 2002-04-20 | 14:00 | 2002-04-20 | 20:00 |  | Kenny | Ben
29 | 2002-04-20 | 14:00 | 2002-04-20 | 20:00 |  | Kenny | Ben
31 | 2002-04-20 | 14:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
32 | 2002-04-20 | 14:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
33 | 2002-04-20 | 14:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
28 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
27 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
26 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
25 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
24 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
23 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
22 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
21 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
20 | 2002-04-20 | 15:00 | 2002-04-20 | 21:00 |  | Kenny | Ben
122 | 2002-04-20 | 15:00 | 2002-04-20 | 19:30 |  | Kenny | Ben
119 | 2002-04-20 | 15:00 | 2002-04-20 | 21:30 |  | Kenny | Ben
118 | 2002-04-20 | 15:00 | 2002-04-20 | 21:30 |  | Kenny | Ben
120 | 2002-04-20 | 15:00 | 2002-04-20 | 21:30 |  | Kenny | Ben
109 | 2002-04-20 | 15:00 | 2002-04-20 | 21:30 |  | Kenny | Ben
108 | 2002-04-20 | 15:00 | 2002-04-20 | 21:30 |  | Kenny | Ben
49 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
50 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
51 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
52 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
55 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
56 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
57 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
58 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
59 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
14 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
15 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
17 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
18 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
19 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
20 | 2002-04-20 | 22:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
64 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
65 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
66 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
68 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
69 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
70 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
71 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
72 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
73 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
75 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
76 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
77 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
78 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
79 | 2002-04-20 | 20:00 | 2002-04-20 | 23:00 |  | Bryan | Johnny
59 | 2002-04-22 | 12:05 | 2002-04-22 | 14:35 |  | Tootie | Ben
58 | 2002-04-22 | 12:05 | 2002-04-22 | 14:35 |  | Tootie | Ben
57 | 2002-04-22 | 12:05 | 2002-04-22 | 14:35 |  | Tootie | Ben
55 | 2002-04-22 | 12:05 | 2002-04-22 | 15:20 |  | Tootie | Ben
52 | 2002-04-22 | 12:05 | 2002-04-22 | 15:20 |  | Tootie | Ben
64 | 2002-04-22 | 12:05 | 2002-04-22 | 13:20 |  | Tootie | Ben
65 | 2002-04-22 | 12:05 | 2002-04-22 | 13:20 |  | Tootie | Ben
66 | 2002-04-22 | 12:05 | 2002-04-22 | 13:20 |  | Tootie | Ben
68 | 2002-04-22 | 12:05 | 2002-04-22 | 14:35 |  | Tootie | Ben
69 | 2002-04-22 | 12:05 | 2002-04-22 | 14:35 |  | Tootie | Ben
50 | 2002-04-22 | 12:05 | 2002-04-22 | 14:35 |  | Tootie | Ben
47 | 2002-04-22 | 12:25 | 2002-04-22 | 15:30 |  | Tootie | Ben
46 | 2002-04-22 | 12:25 | 2002-04-22 | 15:30 |  | Tootie | Ben
45 | 2002-04-22 | 12:25 | 2002-04-22 | 15:30 |  | Tootie | Ben
44 | 2002-04-22 | 12:25 | 2002-04-22 | 16:03 |  | Tootie | Ben
43 | 2002-04-22 | 12:25 | 2002-04-22 | 16:03 |  | Tootie | Ben
42 | 2002-04-22 | 12:25 | 2002-04-22 | 16:03 |  | Tootie | Ben
41 | 2002-04-22 | 12:25 | 2002-04-22 | 16:03 |  | Tootie | Ben
40 | 2002-04-22 | 12:25 | 2002-04-22 | 16:30 |  | Tootie | Ben
39 | 2002-04-22 | 12:25 | 2002-04-22 | 16:30 |  | Tootie | Ben
83 | 2002-04-22 | 12:55 | 2002-04-22 | 16:28 |  | Tootie | Ben
84 | 2002-04-22 | 12:55 | 2002-04-22 | 16:28 |  | Tootie | Ben
85 | 2002-04-22 | 12:55 | 2002-04-22 | 16:28 |  | Tootie | Ben
86 | 2002-04-22 | 12:55 | 2002-04-22 | 16:28 |  | Tootie | Ben
87 | 2002-04-22 | 12:55 | 2002-04-22 | 16:28 |  | Tootie | Ben
88 | 2002-04-22 | 12:55 | 2002-04-22 | 16:36 |  | Tootie | Ben
9 | 2002-04-22 | 12:55 | 2002-04-22 | 21:25 |  | Tootie | Ben
8 | 2002-04-22 | 12:55 | 2002-04-22 | 21:25 |  | Tootie | Ben
7 | 2002-04-22 | 12:55 | 2002-04-22 | 21:25 |  | Tootie | Ben
5 | 2002-04-22 | 12:55 | 2002-04-22 | 21:25 |  | Tootie | Ben
89 | 2002-04-22 | 12:55 | 2002-04-22 | 16:36 |  | Tootie | Ben
90 | 2002-04-22 | 12:55 | 2002-04-22 | 16:36 |  | Tootie | Ben
91 | 2002-04-22 | 12:55 | 2002-04-22 | 16:36 |  | Tootie | Ben
92 | 2002-04-22 | 12:55 | 2002-04-22 | 16:45 |  | Tootie | Ben
93 | 2002-04-22 | 12:55 | 2002-04-22 | 16:45 |  | Tootie | Ben
96 | 2002-04-22 | 12:55 | 2002-04-22 | 16:45 |  | Tootie | Ben
100 | 2002-04-22 | 12:55 | 2002-04-22 | 20:40 |  | Tootie | Ben
102 | 2002-04-22 | 13:10 | 2002-04-22 | 20:40 |  | Tootie | Ben
103 | 2002-04-22 | 13:10 | 2002-04-22 | 20:40 |  | Tootie | Ben
104 | 2002-04-22 | 13:10 | 2002-04-22 | 21:05 |  | Tootie | Ben
105 | 2002-04-22 | 13:10 | 2002-04-22 | 21:05 |  | Tootie | Ben
106 | 2002-04-22 | 13:10 | 2002-04-22 | 21:05 |  | Tootie | Ben
107 | 2002-04-22 | 13:10 | 2002-04-22 | 21:05 |  | Tootie | Ben
108 | 2002-04-22 | 13:10 | 2002-04-22 | 21:05 |  | Tootie | Ben
109 | 2002-04-22 | 13:22 | 2002-04-22 | 21:05 |  | Tootie | Ben
113 | 2002-04-22 | 13:25 | 2002-04-22 | 21:05 |  | Tootie | Ben
117 | 2002-04-22 | 13:55 | 2002-04-22 | 21:05 |  | Tootie | Ben
118 | 2002-04-22 | 13:55 | 2002-04-22 | 21:05 |  | Tootie | Ben
115 | 2002-04-22 | 14:00 | 2002-04-22 | 21:05 |  | Tootie | Ben
116 | 2002-04-22 | 14:00 | 2002-04-22 | 21:05 |  | Tootie | Ben
114 | 2002-04-22 | 14:00 | 2002-04-22 | 21:05 |  | Tootie | Ben
38 | 2002-04-22 | 12:30 | 2002-04-22 | 16:35 |  | Tootie | Ben
37 | 2002-04-22 | 12:30 | 2002-04-22 | 16:35 |  | Tootie | Ben
36 | 2002-04-22 | 12:30 | 2002-04-22 | 16:35 |  | Tootie | Ben
35 | 2002-04-22 | 12:30 | 2002-04-22 | 16:35 |  | Tootie | Ben
34 | 2002-04-22 | 12:30 | 2002-04-22 | 16:35 |  | Tootie | Ben
33 | 2002-04-22 | 12:30 | 2002-04-22 | 16:35 |  | Tootie | Ben
32 | 2002-04-22 | 12:30 | 2002-04-22 | 16:35 |  | Tootie | Ben
30 | 2002-04-22 | 12:30 | 2002-04-22 | 16:45 |  | Tootie | Ben
29 | 2002-04-22 | 12:30 | 2002-04-22 | 16:45 |  | Tootie | Ben
28 | 2002-04-22 | 12:30 | 2002-04-22 | 16:45 |  | Tootie | Ben
27 | 2002-04-22 | 12:30 | 2002-04-22 | 20:40 |  | Tootie | Ben
26 | 2002-04-22 | 12:30 | 2002-04-22 | 20:40 |  | Tootie | Ben
25 | 2002-04-22 | 12:30 | 2002-04-22 | 20:40 |  | Tootie | Ben
24 | 2002-04-22 | 12:30 | 2002-04-22 | 20:45 |  | Tootie | Ben
23 | 2002-04-22 | 12:30 | 2002-04-22 | 20:45 |  | Tootie | Ben
22 | 2002-04-22 | 12:30 | 2002-04-22 | 20:45 |  | Tootie | Ben
71 | 2002-04-22 | 12:45 | 2002-04-22 | 14:35 |  | Tootie | Ben
72 | 2002-04-22 | 12:45 | 2002-04-22 | 15:25 |  | Tootie | Ben
73 | 2002-04-22 | 12:45 | 2002-04-22 | 15:25 |  | Tootie | Ben
74 | 2002-04-22 | 12:45 | 2002-04-22 | 15:25 |  | Tootie | Ben
75 | 2002-04-22 | 12:45 | 2002-04-22 | 16:00 |  | Tootie | Ben
76 | 2002-04-22 | 12:45 | 2002-04-22 | 16:00 |  | Tootie | Ben
77 | 2002-04-22 | 12:45 | 2002-04-22 | 16:00 |  | Tootie | Ben
78 | 2002-04-22 | 12:45 | 2002-04-22 | 16:00 |  | Tootie | Ben
79 | 2002-04-22 | 12:45 | 2002-04-22 | 16:00 |  | Tootie | Ben
80 | 2002-04-22 | 12:45 | 2002-04-22 | 16:30 |  | Tootie | Ben
81 | 2002-04-22 | 12:45 | 2002-04-22 | 16:30 |  | Tootie | Ben
82 | 2002-04-22 | 12:45 | 2002-04-22 | 16:30 |  | Tootie | Ben
21 | 2002-04-22 | 12:45 | 2002-04-22 | 20:50 |  | Tootie | Ben
20 | 2002-04-22 | 12:45 | 2002-04-22 | 20:50 |  | Tootie | Ben
19 | 2002-04-22 | 12:45 | 2002-04-22 | 21:00 |  | Tootie | Ben
18 | 2002-04-22 | 12:45 | 2002-04-22 | 21:00 |  | Tootie | Ben
17 | 2002-04-22 | 12:45 | 2002-04-22 | 21:00 |  | Tootie | Ben
15 | 2002-04-22 | 12:45 | 2002-04-22 | 21:00 |  | Tootie | Ben
14 | 2002-04-22 | 12:45 | 2002-04-22 | 21:00 |  | Tootie | Ben
13 | 2002-04-22 | 12:45 | 2002-04-22 | 21:00 |  | Tootie | Ben
1 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
2 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
3 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
28 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
29 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
30 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
31 | 2002-04-22 | 16:55 | 2002-04-22 | 17:50 |  | Charlie | Pete
32 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
33 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
34 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
35 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
36 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
119 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
121 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
122 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
91 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
92 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
93 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
96 | 2002-04-22 | 16:55 | 2002-04-22 | 21:10 |  | Charlie | Pete
83 | 2002-04-22 | 17:10 | 2002-04-22 | 21:15 |  | Charlie | Pete
84 | 2002-04-22 | 17:10 | 2002-04-22 | 21:15 |  | Charlie | Pete
85 | 2002-04-22 | 17:10 | 2002-04-22 | 21:15 |  | Charlie | Pete
86 | 2002-04-22 | 17:10 | 2002-04-22 | 21:15 |  | Charlie | Pete
87 | 2002-04-22 | 17:10 | 2002-04-22 | 21:15 |  | Charlie | Pete
88 | 2002-04-22 | 17:10 | 2002-04-22 | 21:15 |  | Charlie | Pete
89 | 2002-04-22 | 17:10 | 2002-04-22 | 21:15 |  | Charlie | Pete
90 | 2002-04-22 | 17:10 | 2002-04-22 | 21:15 |  | Charlie | Pete
37 | 2002-04-22 | 17:15 | 2002-04-22 | 21:20 |  | Charlie | Pete
38 | 2002-04-22 | 17:15 | 2002-04-22 | 21:20 |  | Charlie | Pete
39 | 2002-04-22 | 17:15 | 2002-04-22 | 21:20 |  | Charlie | Pete
40 | 2002-04-22 | 17:15 | 2002-04-22 | 21:20 |  | Charlie | Pete
41 | 2002-04-22 | 17:25 | 2002-04-22 | 21:20 |  | Charlie | Pete
42 | 2002-04-22 | 17:25 | 2002-04-22 | 21:20 |  | Charlie | Pete
43 | 2002-04-22 | 17:25 | 2002-04-22 | 21:20 |  | Charlie | Pete
120 | 2002-04-22 | 17:25 | 2002-04-22 | 21:10 |  | Charlie | Pete
80 | 2002-04-22 | 17:25 | 2002-04-22 | 21:10 |  | Charlie | Pete
81 | 2002-04-22 | 17:25 | 2002-04-22 | 21:10 |  | Charlie | Pete
82 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
75 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
76 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
77 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
78 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
79 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
44 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
45 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
46 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
47 | 2002-04-22 | 17:35 | 2002-04-22 | 21:20 |  | Charlie | Pete
71 | 2002-04-22 | 17:35 | 2002-04-22 | 21:25 |  | Charlie | Pete
72 | 2002-04-22 | 17:35 | 2002-04-22 | 21:25 |  | Charlie | Pete
73 | 2002-04-22 | 17:35 | 2002-04-22 | 21:25 |  | Charlie | Pete
74 | 2002-04-22 | 17:35 | 2002-04-22 | 21:25 |  | Charlie | Pete
49 | 2002-04-22 | 17:45 | 2002-04-22 | 21:25 |  | Charlie | Pete
50 | 2002-04-22 | 17:45 | 2002-04-22 | 21:25 |  | Charlie | Pete
68 | 2002-04-22 | 17:45 | 2002-04-22 | 21:25 |  | Charlie | Pete
51 | 2002-04-22 | 17:45 | 2002-04-22 | 21:25 |  | Charlie | Pete
69 | 2002-04-22 | 17:45 | 2002-04-22 | 21:25 |  | Charlie | Pete
52 | 2002-04-22 | 17:45 | 2002-04-22 | 21:25 |  | Charlie | Pete
55 | 2002-04-22 | 17:55 | 2002-04-22 | 21:25 |  | Charlie | Pete
56 | 2002-04-22 | 18:00 | 2002-04-22 | 21:25 |  | Charlie | Pete
57 | 2002-04-22 | 18:10 | 2002-04-22 | 21:25 |  | Charlie | Pete
65 | 2002-04-22 | 21:30 | 2002-04-23 | 2:25 |  | Charlie | Pete
66 | 2002-04-22 | 21:30 | 2002-04-23 | 2:25 |  | Charlie | Pete
68 | 2002-04-22 | 21:30 | 2002-04-23 | 2:25 |  | Charlie | Pete
69 | 2002-04-22 | 21:30 | 2002-04-23 | 2:25 |  | Charlie | Pete
71 | 2002-04-22 | 21:30 | 2002-04-23 | 2:25 |  | Charlie | Pete
72 | 2002-04-22 | 21:30 | 2002-04-23 | 2:30 |  | Charlie | Pete
73 | 2002-04-22 | 21:30 | 2002-04-23 | 2:30 |  | Charlie | Pete
74 | 2002-04-22 | 21:30 | 2002-04-23 | 2:30 |  | Charlie | Pete
75 | 2002-04-22 | 21:30 | 2002-04-23 | 2:50 |  | Charlie | Pete
76 | 2002-04-22 | 21:30 | 2002-04-23 | 2:50 |  | Charlie | Pete
77 | 2002-04-22 | 21:30 | 2002-04-23 | 2:50 |  | Charlie | Pete
78 | 2002-04-22 | 21:30 | 2002-04-23 | 2:50 |  | Charlie | Pete
79 | 2002-04-22 | 21:30 | 2002-04-23 | 2:50 |  | Charlie | Pete
80 | 2002-04-22 | 21:30 | 2002-04-23 | 2:55 |  | Charlie | Pete
81 | 2002-04-22 | 21:30 | 2002-04-23 | 2:55 |  | Charlie | Pete
82 | 2002-04-22 | 21:30 | 2002-04-23 | 2:55 |  | Charlie | Pete
83 | 2002-04-22 | 21:30 | 2002-04-23 | 2:55 |  | Charlie | Pete
84 | 2002-04-22 | 21:30 | 2002-04-23 | 2:55 |  | Charlie | Pete
85 | 2002-04-22 | 21:30 | 2002-04-23 | 2:55 |  | Charlie | Pete
86 | 2002-04-22 | 21:30 | 2002-04-23 | 3:05 |  | Charlie | Pete
87 | 2002-04-22 | 21:30 | 2002-04-23 | 3:05 |  | Charlie | Pete
88 | 2002-04-22 | 21:30 | 2002-04-23 | 3:05 |  | Charlie | Pete
89 | 2002-04-22 | 21:30 | 2002-04-23 | 3:05 |  | Charlie | Pete
90 | 2002-04-22 | 21:35 | 2002-04-23 | 3:20 |  | Charlie | Pete
91 | 2002-04-22 | 21:35 | 2002-04-23 | 3:20 |  | Charlie | Pete
92 | 2002-04-22 | 21:35 | 2002-04-23 | 3:20 |  | Charlie | Pete
93 | 2002-04-22 | 21:35 | 2002-04-23 | 3:20 |  | Charlie | Pete
96 | 2002-04-22 | 21:35 | 2002-04-23 | 3:35 |  | Charlie | Pete
100 | 2002-04-22 | 21:35 | 2002-04-23 | 3:35 |  | Charlie | Pete
102 | 2002-04-22 | 21:35 | 2002-04-23 | 4:00 |  | Charlie | Pete
103 | 2002-04-22 | 21:35 | 2002-04-23 | 4:00 |  | Charlie | Pete
1 | 2002-04-22 | 21:35 | 2002-04-23 | 2:25 |  | Charlie | Pete
2 | 2002-04-22 | 21:35 | 2002-04-23 | 2:25 |  | Charlie | Pete
3 | 2002-04-22 | 21:35 | 2002-04-23 | 2:25 |  | Charlie | Pete
4 | 2002-04-22 | 21:35 | 2002-04-23 | 2:25 |  | Charlie | Pete
5 | 2002-04-22 | 21:35 | 2002-04-23 | 2:25 |  | Charlie | Pete
7 | 2002-04-22 | 21:35 | 2002-04-23 | 2:25 |  | Charlie | Pete
8 | 2002-04-22 | 21:35 | 2002-04-23 | 2:25 |  | Charlie | Pete
9 | 2002-04-22 | 21:35 | 2002-04-23 | 2:25 |  | Charlie | Pete
13 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
14 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
15 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
17 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
18 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
19 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
20 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
21 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
22 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
23 | 2002-04-22 | 21:35 | 2002-04-23 | 2:55 |  | Charlie | Pete
24 | 2002-04-22 | 21:35 | 2002-04-23 | 3:10 |  | Charlie | Pete
25 | 2002-04-22 | 21:35 | 2002-04-23 | 3:10 |  | Charlie | Pete
26 | 2002-04-22 | 21:35 | 2002-04-23 | 3:10 |  | Charlie | Pete
27 | 2002-04-22 | 21:35 | 2002-04-23 | 3:10 |  | Charlie | Pete
28 | 2002-04-22 | 21:35 | 2002-04-23 | 3:10 |  | Charlie | Pete
29 | 2002-04-22 | 21:35 | 2002-04-23 | 3:10 |  | Charlie | Pete
30 | 2002-04-22 | 21:35 | 2002-04-23 | 4:30 |  | Charlie | Pete
32 | 2002-04-22 | 21:35 | 2002-04-23 | 4:30 |  | Charlie | Pete
33 | 2002-04-22 | 21:35 | 2002-04-23 | 7:56 |  | Charlie | Pete
34 | 2002-04-22 | 21:35 | 2002-04-23 | 7:56 |  | Charlie | Pete
35 | 2002-04-22 | 21:35 | 2002-04-23 | 7:56 |  | Charlie | Pete
36 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
37 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
38 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
39 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
40 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
41 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
42 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
43 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
44 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
45 | 2002-04-22 | 21:40 | 2002-04-23 | 7:56 |  | Charlie | Pete
104 | 2002-04-22 | 23:10 | 2002-04-23 | 7:36 |  | Charlie | Pete
105 | 2002-04-22 | 23:10 | 2002-04-23 | 7:36 |  | Charlie | Pete
46 | 2002-04-22 | 23:10 | 2002-04-23 | 7:56 |  | Charlie | Pete
47 | 2002-04-22 | 23:10 | 2002-04-23 | 7:56 |  | Charlie | Pete
106 | 2002-04-22 | 23:25 | 2002-04-23 | 7:36 |  | Charlie | Pete
107 | 2002-04-22 | 23:25 | 2002-04-23 | 7:36 |  | Charlie | Pete
108 | 2002-04-22 | 22:30 | 2002-04-23 | 7:36 |  | Charlie | Pete
109 | 2002-04-22 | 22:30 | 2002-04-23 | 7:36 |  | Charlie | Pete
49 | 2002-04-22 | 23:45 | 2002-04-23 | 7:56 |  | Charlie | Pete
50 | 2002-04-23 | 1:20 | 2002-04-23 | 7:56 |  | Charlie | Pete
51 | 2002-04-23 | 1:20 | 2002-04-23 | 7:56 |  | Charlie | Pete
52 | 2002-04-23 | 1:20 | 2002-04-23 | 7:56 |  | Charlie | Pete
55 | 2002-04-23 | 1:20 | 2002-04-23 | 7:56 |  | Charlie | Pete
56 | 2002-04-23 | 1:20 | 2002-04-23 | 7:56 |  | Charlie | Pete
57 | 2002-04-23 | 1:20 | 2002-04-23 | 7:56 |  | Charlie | Pete
58 | 2002-04-23 | 1:20 | 2002-04-23 | 7:56 |  | Charlie | Pete
59 | 2002-04-23 | 1:20 | 2002-04-23 | 7:56 |  | Charlie | Pete
114 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
115 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
63 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
64 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
70 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
120 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
113 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
117 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
118 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
119 | 2002-04-23 | 1:20 | 2002-04-23 | 7:40 |  | Charlie | Pete
65 | 2002-04-23 | 4:45 | 2002-04-23 | 7:40 |  | Charlie | Pete
66 | 2002-04-23 | 4:45 | 2002-04-23 | 7:40 |  | Charlie | Pete
1 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
2 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
3 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
4 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
5 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
7 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
8 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
9 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
68 | 2002-04-23 | 4:55 | 2002-04-23 | 7:40 |  | Charlie | Pete
69 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
71 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
72 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
73 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
74 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
75 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
76 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
77 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
13 | 2002-04-23 | 4:55 | 2002-04-23 | 7:47 |  | Charlie | Pete
78 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
79 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
80 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
81 | 2002-04-23 | 4:55 | 2002-04-23 | 7:45 |  | Charlie | Pete
82 | 2002-04-23 | 5:45 | 2002-04-23 | 7:45 |  | Charlie | Pete
32 | 2002-04-23 | 5:55 | 2002-04-23 | 7:56 |  | Charlie | Pete
14 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
15 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
17 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
18 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
19 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
20 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
21 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
22 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
23 | 2002-04-23 | 6:10 | 2002-04-23 | 7:47 |  | Charlie | Pete
83 | 2002-04-23 | 6:10 | 2002-04-23 | 7:45 |  | Charlie | Pete
84 | 2002-04-23 | 6:10 | 2002-04-23 | 7:45 |  | Charlie | Pete
85 | 2002-04-23 | 6:10 | 2002-04-23 | 7:45 |  | Charlie | Pete
86 | 2002-04-23 | 6:10 | 2002-04-23 | 7:45 |  | Charlie | Pete
87 | 2002-04-23 | 6:10 | 2002-04-23 | 7:45 |  | Charlie | Pete
88 | 2002-04-23 | 6:10 | 2002-04-23 | 7:45 |  | Charlie | Pete
89 | 2002-04-23 | 6:10 | 2002-04-23 | 7:45 |  | Charlie | Pete
1 | 2002-04-23 | 12:02 | 2002-04-23 | 12:35 |  | Tootie | Ben
2 | 2002-04-23 | 12:02 | 2002-04-23 | 12:35 |  | Tootie | Ben
3 | 2002-04-23 | 12:02 | 2002-04-23 | 12:35 |  | Tootie | Ben
4 | 2002-04-23 | 12:02 | 2002-04-23 | 12:35 |  | Tootie | Ben
5 | 2002-04-23 | 12:02 | 2002-04-23 | 12:35 |  | Tootie | Ben
7 | 2002-04-23 | 12:02 | 2002-04-23 | 13:51 |  | Tootie | Ben
8 | 2002-04-23 | 12:07 | 2002-04-23 | 13:51 |  | Tootie | Ben
9 | 2002-04-23 | 12:07 | 2002-04-23 | 13:51 |  | Tootie | Ben
13 | 2002-04-23 | 12:07 | 2002-04-23 | 13:51 |  | Tootie | Ben
14 | 2002-04-23 | 12:07 | 2002-04-23 | 13:51 |  | Tootie | Ben
15 | 2002-04-23 | 12:07 | 2002-04-23 | 13:51 |  | Tootie | Ben
17 | 2002-04-23 | 12:07 | 2002-04-23 | 13:51 |  | Tootie | Ben
18 | 2002-04-23 | 12:07 | 2002-04-23 | 13:51 |  | Tootie | Ben
1 | 2002-04-23 | 17:00 | 2002-04-23 | 18:05 |  | Tootie | Ben
2 | 2002-04-23 | 17:00 | 2002-04-23 | 18:05 |  | Tootie | Ben
3 | 2002-04-23 | 17:00 | 2002-04-23 | 18:05 |  | Tootie | Ben
4 | 2002-04-23 | 17:00 | 2002-04-23 | 18:20 |  | Tootie | Ben
5 | 2002-04-23 | 17:00 | 2002-04-23 | 18:20 |  | Tootie | Ben
7 | 2002-04-23 | 17:00 | 2002-04-23 | 18:20 |  | Tootie | Ben
8 | 2002-04-23 | 17:00 | 2002-04-23 | 18:20 |  | Tootie | Ben
9 | 2002-04-23 | 17:00 | 2002-04-23 | 18:20 |  | Tootie | Ben
13 | 2002-04-23 | 17:00 | 2002-04-23 | 18:20 |  | Tootie | Ben
14 | 2002-04-23 | 17:00 | 2002-04-23 | 18:20 |  | Tootie | Ben
15 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
17 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
18 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
19 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
20 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
21 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
22 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
63 | 2002-04-23 | 17:00 | 2002-04-23 | 18:10 |  | Tootie | Ben
64 | 2002-04-23 | 17:00 | 2002-04-23 | 18:10 |  | Tootie | Ben
65 | 2002-04-23 | 17:00 | 2002-04-23 | 18:10 |  | Tootie | Ben
66 | 2002-04-23 | 17:00 | 2002-04-23 | 18:10 |  | Tootie | Ben
68 | 2002-04-23 | 17:00 | 2002-04-23 | 18:15 |  | Tootie | Ben
23 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
24 | 2002-04-23 | 17:00 | 2002-04-23 | 18:25 |  | Tootie | Ben
26 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
27 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
28 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
29 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
3041 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
32 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
33 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
34 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
35 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
36 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
37 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
38 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
39 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
69 | 2002-04-23 | 17:10 | 2002-04-23 | 18:15 |  | Charlie | Ben
70 | 2002-04-23 | 17:10 | 2002-04-23 | 18:15 |  | Charlie | Ben
71 | 2002-04-23 | 17:10 | 2002-04-23 | 18:15 |  | Charlie | Ben
72 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
73 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
74 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
75 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
76 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
77 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
78 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
80 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
82 | 2002-04-23 | 17:10 | 2002-04-23 | 18:20 |  | Charlie | Ben
84 | 2002-04-23 | 17:10 | 2002-04-23 | 18:25 |  | Charlie | Ben
85 | 2002-04-23 | 17:10 | 2002-04-23 | 18:25 |  | Charlie | Ben
86 | 2002-04-23 | 17:10 | 2002-04-23 | 18:25 |  | Charlie | Ben
87 | 2002-04-23 | 17:10 | 2002-04-23 | 18:25 |  | Charlie | Ben
88 | 2002-04-23 | 17:10 | 2002-04-23 | 18:25 |  | Charlie | Ben
89 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
90 | 2002-04-23 | 17:10 | 2002-04-23 | 18:30 |  | Charlie | Ben
40 | 2002-04-23 | 17:20 | 2002-04-23 | 18:30 |  | Charlie | Ben
108 | 2002-04-23 | 17:20 | 2002-04-23 | 18:30 |  | Charlie | Ben
109 | 2002-04-23 | 17:20 | 2002-04-23 | 18:30 |  | Charlie | Ben
91 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
92 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
41 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
42 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
43 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
44 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
45 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
46 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
93 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
96 | 2002-04-23 | 17:25 | 2002-04-23 | 18:30 |  | Charlie | Ben
100 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
102 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
103 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
104 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
105 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
47 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
49 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
50 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
51 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
52 | 2002-04-23 | 17:30 | 2002-04-23 | 18:30 |  | Charlie | Ben
63 | 2002-04-23 | 18:40 | 2002-04-23 | 19:30 |  | Charlie | Ben
64 | 2002-04-23 | 18:40 | 2002-04-23 | 19:30 |  | Charlie | Ben
65 | 2002-04-23 | 18:40 | 2002-04-23 | 19:30 |  | Charlie | Ben
66 | 2002-04-23 | 18:40 | 2002-04-23 | 19:30 |  | Charlie | Ben
68 | 2002-04-23 | 18:40 | 2002-04-23 | 19:35 |  | Charlie | Ben
69 | 2002-04-23 | 18:40 | 2002-04-23 | 19:35 |  | Charlie | Ben
70 | 2002-04-23 | 18:40 | 2002-04-23 | 19:35 |  | Charlie | Ben
71 | 2002-04-23 | 18:40 | 2002-04-23 | 19:35 |  | Charlie | Ben
72 | 2002-04-23 | 18:55 | 2002-04-23 | 19:40 |  | Charlie | Ben
73 | 2002-04-23 | 18:55 | 2002-04-23 | 19:40 |  | Charlie | Ben
74 | 2002-04-23 | 18:55 | 2002-04-23 | 19:40 |  | Charlie | Ben
75 | 2002-04-23 | 19:00 | 2002-04-23 | 19:40 |  | Charlie | Ben
76 | 2002-04-23 | 19:00 | 2002-04-23 | 19:45 |  | Charlie | Ben
77 | 2002-04-23 | 19:00 | 2002-04-23 | 19:45 |  | Charlie | Ben
78 | 2002-04-23 | 19:25 | 2002-04-23 | 19:45 |  | Charlie | Ben
79 | 2002-04-23 | 19:25 | 2002-04-23 | 19:45 |  | Charlie | Ben
1 | 2002-04-23 | 18:55 | 2002-04-23 | 19:15 |  | Charlie | Art
2 | 2002-04-23 | 18:55 | 2002-04-23 | 19:15 |  | Charlie | Art
3 | 2002-04-23 | 18:55 | 2002-04-23 | 19:15 |  | Charlie | Art
4 | 2002-04-23 | 18:55 | 2002-04-23 | 19:15 |  | Charlie | Art
5 | 2002-04-23 | 18:55 | 2002-04-23 | 19:15 |  | Charlie | Art
7 | 2002-04-23 | 18:55 | 2002-04-23 | 19:15 |  | Charlie | Art
8 | 2002-04-23 | 18:55 | 2002-04-23 | 19:20 |  | Charlie | Art
9 | 2002-04-23 | 18:55 | 2002-04-23 | 19:20 |  | Charlie | Art
13 | 2002-04-23 | 18:55 | 2002-04-23 | 19:20 |  | Charlie | Art
14 | 2002-04-23 | 19:00 | 2002-04-23 | 19:20 |  | Charlie | Art
15 | 2002-04-23 | 19:00 | 2002-04-23 | 19:20 |  | Charlie | Art
17 | 2002-04-23 | 19:00 | 2002-04-23 | 19:20 |  | Charlie | Art
18 | 2002-04-23 | 19:35 | 2002-04-23 | 19:45 |  | Charlie | Art
19 | 2002-04-23 | 19:35 | 2002-04-23 | 19:45 |  | Charlie | Art
20 | 2002-04-23 | 19:35 | 2002-04-23 | 19:45 |  | Charlie | Art
21 | 2002-04-23 | 19:35 | 2002-04-23 | 19:45 |  | Charlie | Art
22 | 2002-04-23 | 19:40 | 2002-04-23 | 19:45 |  | Charlie | Art
23 | 2002-04-23 | 19:40 | 2002-04-23 | 19:45 |  | Charlie | Art
24 | 2002-04-23 | 19:40 | 2002-04-23 | 19:45 |  | Charlie | Art
25 | 2002-04-23 | 19:40 | 2002-04-23 | 19:45 |  | Charlie | Art
26 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
27 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
28 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
29 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
30 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
31 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
32 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
33 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
34 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
35 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
36 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
37 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
38 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
39 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
40 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
41 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
42 | 2002-04-23 | 21:10 | 2002-04-24 | 1:25 |  | Charlie | Art
43 | 2002-04-23 | 21:15 | 2002-04-24 | 1:25 |  | Charlie | Art
80 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
81 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
82 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
83 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
84 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
85 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
86 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
87 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
88 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
89 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
90 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
91 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
92 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
93 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
96 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
100 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
102 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
103 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
104 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
105 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
106 | 2002-04-23 | 21:15 | 2002-04-24 | 1:30 |  | Charlie | Art
44 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
45 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
46 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
47 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
48 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
49 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
50 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
51 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
52 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
55 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
56 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
57 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
58 | 2002-04-23 | 21:20 | 2002-04-24 | 1:30 |  | Charlie | Art
107 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
108 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
109 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
113 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
120 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
118 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
119 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
121 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
122 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
59 | 2002-04-23 | 21:25 | 2002-04-24 | 1:35 |  | Charlie | Art
1 | 2002-04-23 | 21:30 | 2002-04-24 | 1:35 |  | Charlie | Art
2 | 2002-04-23 | 21:30 | 2002-04-24 | 1:35 |  | Charlie | Art
3 | 2002-04-23 | 21:30 | 2002-04-24 | 1:35 |  | Charlie | Art
4 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
5 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
7 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
8 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
9 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
63 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
64 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
65 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
66 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
68 | 2002-04-23 | 21:50 | 2002-04-24 | 1:35 |  | Charlie | Art
13 | 2002-04-23 | 21:50 | 2002-04-24 | 1:40 |  | Charlie | Art
14 | 2002-04-23 | 21:50 | 2002-04-24 | 1:40 |  | Charlie | Art
15 | 2002-04-23 | 22:00 | 2002-04-24 | 1:40 |  | Charlie | Art
17 | 2002-04-23 | 22:00 | 2002-04-24 | 1:40 |  | Charlie | Art
18 | 2002-04-23 | 20:05 | 2002-04-24 | 1:40 |  | Charlie | Art
63 | 2002-04-24 | 1:45 | 2002-04-24 | 3:30 |  | Charlie | Art
64 | 2002-04-24 | 1:45 | 2002-04-24 | 3:30 |  | Charlie | Art
65 | 2002-04-24 | 1:45 | 2002-04-24 | 3:55 |  | Charlie | Art
66 | 2002-04-24 | 1:45 | 2002-04-24 | 3:55 |  | Charlie | Art
68 | 2002-04-24 | 1:45 | 2002-04-24 | 3:55 |  | Charlie | Art
69 | 2002-04-24 | 1:45 | 2002-04-24 | 3:55 |  | Charlie | Art
70 | 2002-04-24 | 1:45 | 2002-04-24 | 3:55 |  | Charlie | Art
71 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
72 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
73 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
74 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
75 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
76 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
77 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
78 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
79 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
80 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
81 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
82 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
83 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
84 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
85 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
86 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
87 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
88 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
89 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
90 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
93 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
96 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
100 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
102 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
103 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
104 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
105 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
106 | 2002-04-24 | 1:45 | 2002-04-24 | 4:40 |  | Charlie | Art
1 | 2002-04-24 | 1:50 | 2002-04-24 | 3:55 |  | Charlie | Art
2 | 2002-04-24 | 1:50 | 2002-04-24 | 3:55 |  | Charlie | Art
3 | 2002-04-24 | 1:50 | 2002-04-24 | 3:55 |  | Charlie | Art
4 | 2002-04-24 | 1:50 | 2002-04-24 | 3:55 |  | Charlie | Art
5 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
7 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
8 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
9 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
13 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
14 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
15 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
17 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
18 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
19 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
20 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
21 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
22 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
23 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
24 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
25 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
26 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
27 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
28 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
29 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
30 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
31 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
32 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
33 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
34 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
35 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
36 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
37 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
38 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
39 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
40 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
41 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
42 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
43 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
44 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
45 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
46 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
47 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
48 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
49 | 2002-04-24 | 1:50 | 2002-04-24 | 4:40 |  | Charlie | Art
1 | 2002-04-24 | 5:10 | 2002-04-24 | 8:32 |  | Charlie | Art
2 | 2002-04-24 | 5:10 | 2002-04-24 | 8:32 |  | Charlie | Art
3 | 2002-04-24 | 5:10 | 2002-04-24 | 8:32 |  | Charlie | Art
4 | 2002-04-24 | 5:10 | 2002-04-24 | 8:32 |  | Charlie | Art
5 | 2002-04-24 | 5:10 | 2002-04-24 | 8:32 |  | Charlie | Art
7 | 2002-04-24 | 5:10 | 2002-04-24 | 8:32 |  | Charlie | Art
8 | 2002-04-24 | 5:10 | 2002-04-24 | 8:32 |  | Charlie | Art
9 | 2002-04-24 | 5:10 | 2002-04-24 | 8:36 |  | Charlie | Art
13 | 2002-04-24 | 5:10 | 2002-04-24 | 8:37 |  | Charlie | Art
14 | 2002-04-24 | 5:10 | 2002-04-24 | 8:39 |  | Charlie | Art
15 | 2002-04-24 | 5:10 | 2002-04-24 | 8:41 |  | Charlie | Art
17 | 2002-04-24 | 5:10 | 2002-04-24 | 8:42 |  | Charlie | Art
18 | 2002-04-24 | 5:10 | 2002-04-24 | 8:47 |  | Charlie | Art
19 | 2002-04-24 | 5:10 | 2002-04-24 | 8:48 |  | Charlie | Art
20 | 2002-04-24 | 5:10 | 2002-04-24 | 8:54 |  | Charlie | Art
21 | 2002-04-24 | 5:10 | 2002-04-24 | 8:59 |  | Charlie | Art
22 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
23 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
24 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
25 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
26 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
27 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
28 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
29 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
30 | 2002-04-24 | 5:10 | 2002-04-24 | 9:03 |  | Charlie | Art
31 | 2002-04-24 | 5:15 | 2002-04-24 | 9:03 |  | Charlie | Art
32 | 2002-04-24 | 5:15 | 2002-04-24 | 9:07 |  | Charlie | Art
33 | 2002-04-24 | 5:15 | 2002-04-24 | 9:07 |  | Charlie | Art
34 | 2002-04-24 | 5:15 | 2002-04-24 | 9:07 |  | Charlie | Art
35 | 2002-04-24 | 5:15 | 2002-04-24 | 9:07 |  | Charlie | Art
36 | 2002-04-24 | 5:15 | 2002-04-24 | 9:07 |  | Charlie | Art
37 | 2002-04-24 | 5:15 | 2002-04-24 | 7:55 |  | Charlie | Art
38 | 2002-04-24 | 5:15 | 2002-04-24 | 7:53 |  | Charlie | Art
39 | 2002-04-24 | 5:15 | 2002-04-24 | 7:53 |  | Charlie | Art
40 | 2002-04-24 | 5:15 | 2002-04-24 | 7:25 |  | Charlie | Art
41 | 2002-04-24 | 5:15 | 2002-04-24 | 7:20 |  | Charlie | Art
42 | 2002-04-24 | 5:15 | 2002-04-24 | 7:20 |  | Charlie | Art
43 | 2002-04-24 | 5:15 | 2002-04-24 | 7:15 |  | Charlie | Art
44 | 2002-04-24 | 5:15 | 2002-04-24 | 7:15 |  | Charlie | Art
45 | 2002-04-24 | 5:15 | 2002-04-24 | 5:35 |  | Charlie | Art
63 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
64 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
65 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
66 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
68 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
69 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
70 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
71 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
72 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
73 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
74 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
75 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
76 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
77 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
78 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
79 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
80 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
81 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
82 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
83 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
84 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
85 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
86 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
87 | 2002-04-24 | 5:10 | 2002-04-24 | 9:39 |  | Charlie | Art
88 | 2002-04-24 | 5:10 | 2002-04-24 | 9:33 |  | Charlie | Art
89 | 2002-04-24 | 5:10 | 2002-04-24 | 9:33 |  | Charlie | Art
90 | 2002-04-24 | 5:10 | 2002-04-24 | 9:33 |  | Charlie | Art
91 | 2002-04-24 | 5:10 | 2002-04-24 | 9:33 |  | Charlie | Art
92 | 2002-04-24 | 5:10 | 2002-04-24 | 9:33 |  | Charlie | Art
93 | 2002-04-24 | 5:10 | 2002-04-24 | 9:33 |  | Charlie | Art
88 | 2002-04-24 | 12:49 | 2002-04-24 | 15:18 |  | Tootie | Johnny
89 | 2002-04-24 | 12:49 | 2002-04-24 | 15:18 |  | Tootie | Johnny
90 | 2002-04-24 | 12:49 | 2002-04-24 | 15:18 |  | Tootie | Johnny
91 | 2002-04-24 | 12:49 | 2002-04-24 | 15:18 |  | Tootie | Johnny
92 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
93 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
96 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
100 | 2002-04-24 | 12:49 | 2002-04-24 | 16:35 |  | Tootie | Johnny
102 | 2002-04-24 | 12:49 | 2002-04-24 | 16:35 |  | Tootie | Johnny
103 | 2002-04-24 | 12:49 | 2002-04-24 | 16:35 |  | Tootie | Johnny
104 | 2002-04-24 | 12:49 | 2002-04-24 | 16:35 |  | Tootie | Johnny
105 | 2002-04-24 | 12:49 | 2002-04-24 | 16:50 |  | Tootie | Johnny
106 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
107 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
108 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
109 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
113 | 2002-04-24 | 12:49 | 2002-04-24 | 16:35 |  | Tootie | Johnny
117 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
118 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
119 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
120 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
122 | 2002-04-24 | 12:49 | 2002-04-24 | 15:32 |  | Tootie | Johnny
60 | 2002-04-24 | 12:49 | 2002-04-24 | 15:06 |  | Tootie | Johnny
61 | 2002-04-24 | 12:49 | 2002-04-24 | 15:06 |  | Tootie | Johnny
62 | 2002-04-24 | 5:15 | 2002-04-24 | 15:06 |  | Tootie | Johnny
96 | 2002-04-24 | 5:15 | 2002-04-24 | 9:27 |  | Tootie | Johnny
100 | 2002-04-24 | 5:15 | 2002-04-24 | 9:27 |  | Tootie | Johnny
102 | 2002-04-24 | 5:15 | 2002-04-24 | 9:27 |  | Tootie | Johnny
103 | 2002-04-24 | 7:05 | 2002-04-24 | 9:27 |  | Tootie | Johnny
104 | 2002-04-24 | 7:05 | 2002-04-24 | 9:17 |  | Tootie | Johnny
105 | 2002-04-24 | 7:05 | 2002-04-24 | 9:17 |  | Tootie | Johnny
106 | 2002-04-24 | 7:05 | 2002-04-24 | 9:17 |  | Tootie | Johnny
107 | 2002-04-24 | 7:05 | 2002-04-24 | 9:17 |  | Tootie | Johnny
108 | 2002-04-24 | 7:05 | 2002-04-24 | 9:12 |  | Tootie | Johnny
109 | 2002-04-24 | 7:05 | 2002-04-24 | 9:09 |  | Tootie | Johnny
113 | 2002-04-24 | 7:05 | 2002-04-24 | 9:04 |  | Tootie | Johnny
120 | 2002-04-24 | 7:05 | 2002-04-24 | 9:04 |  | Tootie | Johnny
117 | 2002-04-24 | 7:10 | 2002-04-24 | 8:33 |  | Tootie | Johnny
114 | 2002-04-24 | 7:25 | 2002-04-24 | 8:05 |  | Tootie | Johnny
63 | 2002-04-24 | 12:25 | 2002-04-24 | 15:06 |  | Tootie | Johnny
64 | 2002-04-24 | 12:25 | 2002-04-24 | 15:06 |  | Tootie | Johnny
65 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
66 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
68 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
69 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
70 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
71 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
73 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
74 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
75 | 2002-04-24 | 12:25 | 2002-04-24 | 15:11 |  | Tootie | Johnny
76 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
77 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
78 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
79 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
80 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
81 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
82 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
83 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
84 | 2002-04-24 | 12:45 | 2002-04-24 | 15:18 |  | Tootie | Johnny
85 | 2002-04-24 | 12:49 | 2002-04-24 | 15:18 |  | Tootie | Johnny
86 | 2002-04-24 | 12:49 | 2002-04-24 | 15:18 |  | Tootie | Johnny
87 | 2002-04-24 | 12:49 | 2002-04-24 | 15:18 |  | Tootie | Johnny
1 | 2002-04-24 | 21:10 | 2002-04-24 | 23:55 |  | Charlie | Ben
2 | 2002-04-24 | 21:10 | 2002-04-24 | 23:55 |  | Charlie | Ben
3 | 2002-04-24 | 21:10 | 2002-04-24 | 23:55 |  | Charlie | Ben
4 | 2002-04-24 | 21:10 | 2002-04-24 | 23:55 |  | Charlie | Ben
5 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
7 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
8 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
9 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
13 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
14 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
15 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
17 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
18 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
19 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
20 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
21 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
22 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
23 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
24 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
25 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
26 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
27 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
28 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
29 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
30 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
31 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
32 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
33 | 2002-04-24 | 21:10 | 2002-04-25 | 0:10 |  | Charlie | Ben
34 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
35 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
36 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
37 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
38 | 2002-04-24 | 21:25 | 2002-04-25 | 0:15 |  | Charlie | Ben
39 | 2002-04-24 | 21:25 | 2002-04-25 | 0:15 |  | Charlie | Ben
40 | 2002-04-24 | 22:30 | 2002-04-25 | 0:15 |  | Charlie | Ben
41 | 2002-04-24 | 23:30 | 2002-04-25 | 0:15 |  | Charlie | Ben
42 | 2002-04-24 | 23:30 | 2002-04-25 | 0:15 |  | Charlie | Ben
63 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
64 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
65 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
66 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
68 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
69 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
70 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
71 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
72 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
73 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
74 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
75 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
76 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
77 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
83 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
85 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
86 | 2002-04-24 | 21:20 | 2002-04-25 | 0:10 |  | Charlie | Ben
87 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
88 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
89 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
90 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
91 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
92 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
93 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
100 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
102 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
103 | 2002-04-24 | 21:20 | 2002-04-25 | 0:15 |  | Charlie | Ben
104 | 2002-04-24 | 23:30 | 2002-04-25 | 0:15 |  | Charlie | Ben
105 | 2002-04-24 | 23:30 | 2002-04-25 | 0:15 |  | Charlie | Ben
106 | 2002-04-24 | 23:30 | 2002-04-25 | 0:15 |  | Charlie | Ben
107 | 2002-04-24 | 23:30 | 2002-04-25 | 0:15 |  | Charlie | Ben
109 | 2002-04-24 | 23:30 | 2002-04-25 | 0:15 |  | Charlie | Ben
43 | 2002-04-24 | 23:30 | 2002-04-25 | 0:10 |  | Charlie | Ben
44 | 2002-04-24 | 23:30 | 2002-04-25 | 0:10 |  | Charlie | Ben
104 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
105 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
106 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
107 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
108 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
109 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
113 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
117 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
118 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
119 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
120 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
121 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
122 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Ben
114 | 2002-04-25 | 7:25 | 2002-04-25 | 15:45 |  | Charlie | Ben
115 | 2002-04-25 | 7:25 | 2002-04-25 | 15:45 |  | Charlie | Ben
116 | 2002-04-25 | 7:25 | 2002-04-25 | 15:45 |  | Charlie | Ben
49 | 2002-04-25 | 7:25 | 2002-04-25 | 8:12 |  | Charlie | Ben
50 | 2002-04-25 | 7:27 | 2002-04-25 | 8:12 |  | Charlie | Ben
51 | 2002-04-25 | 7:27 | 2002-04-25 | 8:12 |  | Charlie | Ben
52 | 2002-04-25 | 7:27 | 2002-04-25 | 8:12 |  | Charlie | Ben
58 | 2002-04-25 | 7:27 | 2002-04-25 | 8:12 |  | Charlie | Ben
59 | 2002-04-25 | 7:30 | 2002-04-25 | 8:12 |  | Charlie | Ben
55 | 2002-04-25 | 7:30 | 2002-04-25 | 8:12 |  | Charlie | Ben
56 | 2002-04-25 | 7:30 | 2002-04-25 | 8:12 |  | Charlie | Ben
57 | 2002-04-25 | 7:30 | 2002-04-25 | 8:12 |  | Charlie | Ben
47 | 2002-04-25 | 7:33 | 2002-04-25 | 8:12 |  | Charlie | Ben
46 | 2002-04-25 | 7:33 | 2002-04-25 | 8:12 |  | Charlie | Ben
45 | 2002-04-25 | 7:33 | 2002-04-25 | 8:12 |  | Charlie | Ben
44 | 2002-04-25 | 7:33 | 2002-04-25 | 8:12 |  | Charlie | Ben
43 | 2002-04-25 | 7:33 | 2002-04-25 | 8:20 |  | Charlie | Ben
42 | 2002-04-25 | 7:33 | 2002-04-25 | 8:20 |  | Charlie | Ben
41 | 2002-04-25 | 7:33 | 2002-04-25 | 8:20 |  | Charlie | Ben
40 | 2002-04-25 | 7:36 | 2002-04-25 | 8:20 |  | Charlie | Ben
39 | 2002-04-25 | 7:36 | 2002-04-25 | 8:20 |  | Charlie | Ben
38 | 2002-04-25 | 7:36 | 2002-04-25 | 8:20 |  | Charlie | Ben
37 | 2002-04-25 | 7:36 | 2002-04-25 | 8:20 |  | Charlie | Ben
36 | 2002-04-25 | 7:36 | 2002-04-25 | 8:20 |  | Charlie | Ben
60 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
61 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
62 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
63 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
64 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
65 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
66 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
68 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
69 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
70 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
71 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
72 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
73 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
74 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
75 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
76 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
77 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
78 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
79 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
80 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
81 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
82 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
83 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
84 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
85 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
86 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
87 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
88 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
89 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
90 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
91 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
92 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
93 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
96 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
100 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
102 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
103 | 2002-04-25 | 6:35 | 2002-04-25 | 15:45 |  | Charlie | Johnny
30 | 2002-04-25 | 8:28 | 2002-04-25 | 9:57 |  | Tootie | Johnny
14 | 2002-04-25 | 8:28 | 2002-04-25 | 9:57 |  | Tootie | Johnny
23 | 2002-04-25 | 8:28 | 2002-04-25 | 9:57 |  | Tootie | Johnny
1 | 2002-04-25 | 8:30 | 2002-04-25 | 8:41 |  | Tootie | Johnny
2 | 2002-04-25 | 8:30 | 2002-04-25 | 8:41 |  | Tootie | Johnny
13 | 2002-04-25 | 8:30 | 2002-04-25 | 8:46 |  | Tootie | Johnny
37 | 2002-04-25 | 8:36 | 2002-04-25 | 9:57 |  | Tootie | Johnny
47 | 2002-04-25 | 9:06 | 2002-04-25 | 9:52 |  | Tootie | Johnny
13 | 2002-04-25 | 9:06 | 2002-04-25 | 10:13 |  | Tootie | Johnny
15 | 2002-04-25 | 9:06 | 2002-04-25 | 10:13 |  | Tootie | Johnny
29 | 2002-04-25 | 9:11 | 2002-04-25 | 10:13 |  | Tootie | Johnny
9 | 2002-04-25 | 9:11 | 2002-04-25 | 10:13 |  | Tootie | Johnny
8 | 2002-04-25 | 9:11 | 2002-04-25 | 10:13 |  | Tootie | Johnny
45 | 2002-04-25 | 9:21 | 2002-04-25 | 9:57 |  | Tootie | Johnny
46 | 2002-04-25 | 9:21 | 2002-04-25 | 9:57 |  | Tootie | Johnny
49 | 2002-04-25 | 9:27 | 2002-04-25 | 9:52 |  | Tootie | Johnny
50 | 2002-04-25 | 9:27 | 2002-04-25 | 9:52 |  | Tootie | Johnny
49 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
50 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
51 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
52 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
53 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
54 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
55 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
56 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
57 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
58 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
59 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
29 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
30 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
21 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
22 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
23 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
24 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
25 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
26 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
27 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
28 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
13 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
14 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
15 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
17 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
18 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
19 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
20 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
9 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
8 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
7 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
5 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
4 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
3 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
2 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
78 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
79 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
80 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
81 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
82 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
83 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
84 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
85 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
86 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
87 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
88 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
89 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
90 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
91 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
92 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
93 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
117 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
69 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
70 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
71 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
121 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
122 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
72 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
73 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
74 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
75 | 2002-04-26 | 0:05 | 2002-04-26 | 1:05 |  | Bryan | Doyle
1 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
2 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
3 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
4 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
5 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
7 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
8 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
9 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
13 | 2002-04-26 | 15:20 | 2002-04-26 | 22:30 |  | Matt | Johnny
14 | 2002-04-26 | 15:20 | 2002-04-27 | 0:30 |  | Matt | Johnny
15 | 2002-04-26 | 15:20 | 2002-04-27 | 0:30 |  | Matt | Johnny
17 | 2002-04-26 | 15:20 | 2002-04-27 | 0:30 |  | Matt | Johnny
18 | 2002-04-26 | 15:20 | 2002-04-27 | 0:30 |  | Matt | Johnny
19 | 2002-04-26 | 15:20 | 2002-04-27 | 0:30 |  | Matt | Johnny
20 | 2002-04-26 | 15:20 | 2002-04-27 | 4:00 |  | Matt | Johnny
21 | 2002-04-26 | 15:20 | 2002-04-27 | 4:00 |  | Matt | Johnny
22 | 2002-04-26 | 15:25 | 2002-04-27 | 4:00 |  | Matt | Johnny
23 | 2002-04-26 | 15:25 | 2002-04-27 | 4:00 |  | Matt | Johnny
24 | 2002-04-26 | 15:25 | 2002-04-27 | 4:00 |  | Matt | Johnny
25 | 2002-04-26 | 15:25 | 2002-04-27 | 4:00 |  | Matt | Johnny
26 | 2002-04-26 | 15:25 | 2002-04-27 | 4:00 |  | Matt | Johnny
27 | 2002-04-26 | 15:25 | 2002-04-27 | 4:00 |  | Matt | Johnny
28 | 2002-04-26 | 15:25 | 2002-04-27 | 4:00 |  | Matt | Johnny
29 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
30 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
31 | 2002-04-26 | 15:25 | 2002-04-26 | 16:35 |  | Matt | Johnny
32 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
33 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
34 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
35 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
36 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
37 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
38 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
39 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
40 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
60 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
61 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
62 | 2002-04-26 | 15:25 | 2002-04-27 | 6:15 |  | Matt | Johnny
63 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
64 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
65 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
66 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
68 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
69 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
70 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
71 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
72 | 2002-04-26 | 15:30 | 2002-04-26 | 22:30 |  | Matt | Johnny
73 | 2002-04-26 | 15:30 | 2002-04-27 | 0:30 |  | Matt | Johnny
74 | 2002-04-26 | 15:30 | 2002-04-27 | 0:30 |  | Matt | Johnny
75 | 2002-04-26 | 15:30 | 2002-04-27 | 0:30 |  | Matt | Johnny
76 | 2002-04-26 | 15:30 | 2002-04-27 | 0:30 |  | Matt | Johnny
77 | 2002-04-26 | 15:30 | 2002-04-27 | 4:00 |  | Matt | Johnny
41 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
42 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
43 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
44 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
45 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
46 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
47 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
78 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
79 | 2002-04-26 | 15:50 | 2002-04-26 | 16:30 |  | Matt | Johnny
80 | 2002-04-26 | 15:50 | 2002-04-26 | 16:30 |  | Matt | Johnny
81 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
82 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
114 | 2002-04-26 | 15:50 | 2002-04-26 | 16:15 |  | Matt | Johnny
115 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
116 | 2002-04-26 | 15:50 | 2002-04-26 | 16:15 |  | Matt | Johnny
119 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
113 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
120 | 2002-04-26 | 15:50 | 2002-04-27 | 6:15 |  | Matt | Johnny
108 | 2002-04-26 | 15:55 | 2002-04-27 | 6:15 |  | Matt | Johnny
109 | 2002-04-26 | 15:55 | 2002-04-27 | 6:15 |  | Matt | Johnny
106 | 2002-04-26 | 15:55 | 2002-04-27 | 6:15 |  | Matt | Johnny
107 | 2002-04-26 | 15:55 | 2002-04-27 | 6:15 |  | Matt | Johnny
83 | 2002-04-26 | 15:55 | 2002-04-27 | 6:15 |  | Matt | Johnny
121 | 2002-04-26 | 15:30 | 2002-04-27 | 4:00 |  | Matt | Johnny
122 | 2002-04-26 | 15:30 | 2002-04-27 | 4:00 |  | Matt | Johnny
118 | 2002-04-26 | 15:30 | 2002-04-27 | 6:15 |  | Matt | Johnny
117 | 2002-04-26 | 15:30 | 2002-04-27 | 6:00 |  | Matt | Johnny
105 | 2002-04-26 | 16:15 | 2002-04-27 | 6:15 |  | Matt | Johnny
104 | 2002-04-26 | 16:15 | 2002-04-27 | 6:15 |  | Matt | Johnny
103 | 2002-04-26 | 16:15 | 2002-04-27 | 6:15 |  | Matt | Johnny
102 | 2002-04-26 | 16:15 | 2002-04-27 | 6:15 |  | Matt | Johnny
100 | 2002-04-26 | 16:15 | 2002-04-27 | 6:15 |  | Matt | Johnny
84 | 2002-04-26 | 16:30 | 2002-04-27 | 6:15 |  | Matt | Johnny
86 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
87 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
43 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
44 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
45 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
46 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
47 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
49 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
50 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
51 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
64 | 2002-04-26 | 17:10 | 2002-04-27 | 6:15 |  | Matt | Johnny
96 | 2002-04-26 | 17:35 | 2002-04-27 | 6:15 |  | Matt | Johnny
93 | 2002-04-26 | 17:35 | 2002-04-27 | 6:15 |  | Matt | Johnny
92 | 2002-04-26 | 17:35 | 2002-04-27 | 6:15 |  | Matt | Johnny
91 | 2002-04-26 | 17:35 | 2002-04-27 | 6:15 |  | Matt | Johnny
90 | 2002-04-26 | 17:35 | 2002-04-27 | 6:15 |  | Matt | Johnny
85 | 2002-04-26 | 17:35 | 2002-04-27 | 6:15 |  | Matt | Johnny
52 | 2002-04-26 | 18:00 | 2002-04-27 | 6:15 |  | Matt | Johnny
55 | 2002-04-26 | 18:00 | 2002-04-27 | 6:15 |  | Matt | Johnny
56 | 2002-04-26 | 18:00 | 2002-04-27 | 6:15 |  | Matt | Johnny
57 | 2002-04-26 | 18:00 | 2002-04-27 | 6:15 |  | Matt | Johnny
58 | 2002-04-26 | 18:00 | 2002-04-27 | 6:15 |  | Matt | Johnny
1 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Doyle
2 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Doyle
3 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Doyle
4 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Doyle
5 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Doyle
7 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Doyle
8 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Doyle
9 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Doyle
13 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Doyle
14 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Doyle
15 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Doyle
17 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Doyle
18 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Doyle
19 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Doyle
20 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Doyle
21 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Doyle
22 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Doyle
23 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Doyle
24 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Doyle
25 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Doyle
26 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Doyle
27 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Doyle
28 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Doyle
29 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Doyle
30 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Doyle
31 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Doyle
32 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Doyle
33 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Doyle
34 | 2002-04-29 | 17:10 | 2002-04-29 | 20:20 |  | Charlie | Doyle
35 | 2002-04-29 | 17:10 | 2002-04-29 | 20:20 |  | Charlie | Doyle
36 | 2002-04-29 | 17:10 | 2002-04-29 | 20:20 |  | Charlie | Doyle
37 | 2002-04-29 | 17:10 | 2002-04-29 | 20:20 |  | Charlie | Doyle
38 | 2002-04-29 | 17:10 | 2002-04-29 | 20:20 |  | Charlie | Doyle
39 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Doyle
40 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Doyle
41 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Doyle
42 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Doyle
43 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Doyle
44 | 2002-04-29 | 17:10 | 2002-04-29 | 20:40 |  | Charlie | Doyle
45 | 2002-04-29 | 17:10 | 2002-04-29 | 20:40 |  | Charlie | Doyle
46 | 2002-04-29 | 17:10 | 2002-04-29 | 20:40 |  | Charlie | Doyle
47 | 2002-04-29 | 17:10 | 2002-04-29 | 20:40 |  | Charlie | Doyle
49 | 2002-04-29 | 17:10 | 2002-04-29 | 20:40 |  | Charlie | Doyle
50 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
51 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
52 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
54 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Doyle
55 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
56 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
57 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
58 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
114 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
115 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
116 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
53 | 2002-04-29 | 17:10 | 2002-04-29 | 21:20 |  | Charlie | Doyle
1 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
2 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
3 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
4 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
5 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
7 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
8 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
9 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
13 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
14 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
15 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
17 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
18 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
19 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
20 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
21 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
22 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
23 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
24 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
25 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
26 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
27 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
28 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
29 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
30 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
32 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
33 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
34 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
35 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
36 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
37 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
38 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
39 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
40 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
41 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
42 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
43 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
44 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
45 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
46 | 2002-04-30 | 2:15 | 2002-04-30 | 6:40 |  | Charlie | Doyle
60 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Art
61 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Art
62 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Art
63 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Art
64 | 2002-04-29 | 17:10 | 2002-04-29 | 19:40 |  | Charlie | Art
65 | 2002-04-29 | 17:10 | 2002-04-29 | 19:45 |  | Charlie | Art
66 | 2002-04-29 | 17:10 | 2002-04-29 | 19:45 |  | Charlie | Art
67 | 2002-04-29 | 17:10 | 2002-04-29 | 19:45 |  | Charlie | Art
68 | 2002-04-29 | 17:10 | 2002-04-29 | 19:45 |  | Charlie | Art
69 | 2002-04-29 | 17:10 | 2002-04-29 | 19:45 |  | Charlie | Art
70 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Art
71 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Art
72 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Art
73 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Art
74 | 2002-04-29 | 17:10 | 2002-04-29 | 19:50 |  | Charlie | Art
75 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Art
76 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Art
77 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Art
78 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Art
79 | 2002-04-29 | 17:10 | 2002-04-29 | 19:55 |  | Charlie | Art
80 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Art
81 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Art
82 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Art
83 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Art
84 | 2002-04-29 | 17:10 | 2002-04-29 | 20:00 |  | Charlie | Art
85 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Art
86 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Art
87 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Art
88 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Art
89 | 2002-04-29 | 17:10 | 2002-04-29 | 20:10 |  | Charlie | Art
90 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Art
91 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Art
92 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Art
93 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Art
96 | 2002-04-29 | 17:10 | 2002-04-29 | 20:15 |  | Charlie | Art
100 | 2002-04-29 | 17:10 | 2002-04-29 | 20:25 |  | Charlie | Art
102 | 2002-04-29 | 17:10 | 2002-04-29 | 20:25 |  | Charlie | Art
103 | 2002-04-29 | 17:10 | 2002-04-29 | 20:25 |  | Charlie | Art
104 | 2002-04-29 | 17:10 | 2002-04-29 | 20:25 |  | Charlie | Art
105 | 2002-04-29 | 17:10 | 2002-04-29 | 20:25 |  | Charlie | Art
106 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Art
107 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Art
108 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Art
109 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Art
113 | 2002-04-29 | 17:10 | 2002-04-29 | 20:30 |  | Charlie | Art
117 | 2002-04-29 | 17:10 | 2002-04-29 | 20:45 |  | Charlie | Art
118 | 2002-04-29 | 17:10 | 2002-04-29 | 20:45 |  | Charlie | Art
119 | 2002-04-29 | 17:10 | 2002-04-29 | 20:45 |  | Charlie | Art
120 | 2002-04-29 | 17:10 | 2002-04-29 | 20:45 |  | Charlie | Art
121 | 2002-04-29 | 17:10 | 2002-04-29 | 20:45 |  | Charlie | Art
122 | 2002-04-29 | 17:10 | 2002-04-29 | 20:45 |  | Charlie | Art
66 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
67 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
68 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
69 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
70 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
71 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
72 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
73 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
74 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
75 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
76 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
77 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
78 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
79 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
80 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
81 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
82 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
83 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
84 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
85 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
86 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
87 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
88 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
89 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
90 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
91 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
92 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
93 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
96 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
100 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
102 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
103 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
104 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
105 | 2002-04-30 | 2:20 | 2002-04-30 | 6:40 |  | Charlie | Johnny
1 | 2002-04-30 | 6:55 | 2002-04-30 | 8:38 |  | Tootie | Art
2 | 2002-04-30 | 6:55 | 2002-04-30 | 8:38 |  | Tootie | Art
3 | 2002-04-30 | 6:55 | 2002-04-30 | 8:38 |  | Tootie | Art
4 | 2002-04-30 | 6:55 | 2002-04-30 | 8:38 |  | Tootie | Art
5 | 2002-04-30 | 6:55 | 2002-04-30 | 8:38 |  | Tootie | Art
7 | 2002-04-30 | 6:55 | 2002-04-30 | 8:47 |  | Tootie | Art
8 | 2002-04-30 | 6:55 | 2002-04-30 | 8:47 |  | Tootie | Art
9 | 2002-04-30 | 6:55 | 2002-04-30 | 8:47 |  | Tootie | Art
13 | 2002-04-30 | 6:55 | 2002-04-30 | 8:47 |  | Tootie | Art
14 | 2002-04-30 | 6:55 | 2002-04-30 | 8:47 |  | Tootie | Art
15 | 2002-04-30 | 6:55 | 2002-04-30 | 8:47 |  | Tootie | Art
17 | 2002-04-30 | 6:55 | 2002-04-30 | 8:47 |  | Tootie | Art
18 | 2002-04-30 | 6:55 | 2002-04-30 | 8:53 |  | Tootie | Art
20 | 2002-04-30 | 6:55 | 2002-04-30 | 8:53 |  | Tootie | Art
21 | 2002-04-30 | 6:55 | 2002-04-30 | 8:56 |  | Tootie | Art
22 | 2002-04-30 | 6:55 | 2002-04-30 | 8:56 |  | Tootie | Art
23 | 2002-04-30 | 6:55 | 2002-04-30 | 10:02 |  | Tootie | Art
24 | 2002-04-30 | 6:55 | 2002-04-30 | 10:02 |  | Tootie | Art
25 | 2002-04-30 | 6:55 | 2002-04-30 | 10:02 |  | Tootie | Art
26 | 2002-04-30 | 6:55 | 2002-04-30 | 10:02 |  | Tootie | Art
27 | 2002-04-30 | 6:55 | 2002-04-30 | 10:02 |  | Tootie | Art
28 | 2002-04-30 | 6:55 | 2002-04-30 | 10:02 |  | Tootie | Art
29 | 2002-04-30 | 6:55 | 2002-04-30 | 10:05 |  | Tootie | Art
30 | 2002-04-30 | 6:55 | 2002-04-30 | 10:05 |  | Tootie | Art
32 | 2002-04-30 | 6:55 | 2002-04-30 | 10:05 |  | Tootie | Art
33 | 2002-04-30 | 6:55 | 2002-04-30 | 10:05 |  | Tootie | Art
34 | 2002-04-30 | 6:55 | 2002-04-30 | 10:05 |  | Tootie | Art
35 | 2002-04-30 | 6:55 | 2002-04-30 | 10:05 |  | Tootie | Art
36 | 2002-04-30 | 6:55 | 2002-04-30 | 10:05 |  | Tootie | Art
114 | 2002-04-30 | 8:44 | 2002-04-30 | 10:05 |  | Tootie | Art
66 | 2002-04-30 | 7:00 | 2002-04-30 | 8:40 |  | Tootie | Art
67 | 2002-04-30 | 7:00 | 2002-04-30 | 8:45 |  | Tootie | Art
68 | 2002-04-30 | 7:00 | 2002-04-30 | 8:45 |  | Tootie | Art
69 | 2002-04-30 | 7:00 | 2002-04-30 | 8:45 |  | Tootie | Art
70 | 2002-04-30 | 7:00 | 2002-04-30 | 8:45 |  | Tootie | Art
71 | 2002-04-30 | 7:00 | 2002-04-30 | 8:50 |  | Tootie | Art
72 | 2002-04-30 | 7:00 | 2002-04-30 | 8:50 |  | Tootie | Art
73 | 2002-04-30 | 7:00 | 2002-04-30 | 8:50 |  | Tootie | Art
74 | 2002-04-30 | 7:00 | 2002-04-30 | 8:50 |  | Tootie | Art
75 | 2002-04-30 | 7:00 | 2002-04-30 | 8:50 |  | Tootie | Art
76 | 2002-04-30 | 7:00 | 2002-04-30 | 8:50 |  | Tootie | Art
77 | 2002-04-30 | 7:00 | 2002-04-30 | 8:55 |  | Tootie | Art
78 | 2002-04-30 | 7:00 | 2002-04-30 | 8:55 |  | Tootie | Art
79 | 2002-04-30 | 7:00 | 2002-04-30 | 10:00 |  | Tootie | Art
80 | 2002-04-30 | 7:00 | 2002-04-30 | 10:00 |  | Tootie | Art
82 | 2002-04-30 | 7:00 | 2002-04-30 | 10:00 |  | Tootie | Art
83 | 2002-04-30 | 7:00 | 2002-04-30 | 10:00 |  | Tootie | Art
84 | 2002-04-30 | 7:00 | 2002-04-30 | 10:00 |  | Tootie | Art
85 | 2002-04-30 | 7:00 | 2002-04-30 | 10:00 |  | Tootie | Art
86 | 2002-04-30 | 7:00 | 2002-04-30 | 10:00 |  | Tootie | Art
87 | 2002-04-30 | 7:00 | 2002-04-30 | 10:05 |  | Tootie | Art
88 | 2002-04-30 | 7:00 | 2002-04-30 | 10:05 |  | Tootie | Art
89 | 2002-04-30 | 7:00 | 2002-04-30 | 10:05 |  | Tootie | Art
90 | 2002-04-30 | 7:00 | 2002-04-30 | 10:05 |  | Tootie | Art
91 | 2002-04-30 | 7:00 | 2002-04-30 | 10:05 |  | Tootie | Art
92 | 2002-04-30 | 7:00 | 2002-04-30 | 10:05 |  | Tootie | Art

## PROJECTS
Desert Sky
SPECIAL PROJECTS
Month: | April '02
1. Continued punch list
2. Completed installation of Hirschmann switches
3. Completed installation of UPS's.
4. Completed SCADA final ATP
5. Completed sitewide 100 hour reliability test
6. Replaced bad VEM generators on pads 70 and 77
7. Finished repair on pad #67